## Table 1
Short Circuit Fault Level of EHT Grids in Odisha, in MVA and kA
Sl. No. | Substation | 2026-27
|  | Three phase to ground fault |  | Single line to ground fault
|  | 3ph fault level (MVA) | 3ph fault current (kA) | SLG fault level (MVA) | SLG fault current (kA)
765kV
1 | Angul PGCIL (bus1) | 46995.5 | 35.5 | 34633.7 | 26.1
2 | Begunia | 24056.6 | 18.2 | 17788 | 13.4
3 | Jharsuguda PGCIL (bus1) | 46669.4 | 35.2 | 31200.3 | 23.5
4 | Jharsuguda PGCIL (bus2) | 41198.9 | 31.1 | 32317.5 | 24.4
5 | NTPC Darlipalli | 34369.6 | 25.9 | 28374.2 | 21.4
6 | OTPCL | 31981.2 | 24.1 | 21821.4 | 16.5
400kV
1 | Angul PGCIL (bus1) | 38237.2 | 55.2 | 30842.1 | 44.5
2 | Begunia | 23488.2 | 33.9 | 18847.2 | 27.2
3 | Bhadrak New | 12485.5 | 18 | 10093.2 | 14.6
4 | Bisra PGCIL | 27677.3 | 39.9 | 18846.6 | 27.2
5 | Bolangir PGCIL | 5083.2 | 7.3 | 4316.4 | 6.2
6 | Duburi | 14670.4 | 21.2 | 12163.8 | 17.6
7 | IBTPS-1 | 15903.5 | 23 | 13888.8 | 20
8 | IBTPS-2 | 13149.8 | 19 | 11316.8 | 16.3
9 | Indravati | 7305.5 | 10.5 | 6340.1 | 9.2
10 | Indravati PGCIL | 7379.7 | 10.7 | 6315.5 | 9.1
11 | Jayanagar PGCIL | 11867.3 | 17.1 | 10075.3 | 14.5
12 | Jharsuguda PGCIL (bus2) | 27837.9 | 40.2 | 21829.6 | 31.5
13 | Jharsuguda PGCIL (bus1) | 34914.5 | 50.4 | 24786.5 | 35.8
14 | Kaniha NTPC | 37396.1 | 54 | 37267 | 53.8
15 | Keonjhar PGCIL | 7723.5 | 11.1 | 5836.5 | 8.4
16 | Khuntuni | 24660.3 | 35.6 | 20111.9 | 29
17 | Kuchei PGCIL | 14789.7 | 21.3 | 11345.3 | 16.4
18 | Lapanga | 22997.5 | 33.2 | 20172.9 | 29.1
19 | Mendhasal | 21225 | 30.6 | 18105.8 | 26.1
20 | Meramundali | 17246 | 24.9 | 14663.2 | 21.2
21 | Meramundali-B | 22587.5 | 32.6 | 17767.9 | 25.6
22 | Narendrapur New | 9432.2 | 13.6 | 7790.2 | 11.2
23 | Pandiabil | 19407.1 | 28 | 16098 | 23.2
24 | Paradeep | 7410.2 | 10.7 | 6416.8 | 9.3
25 | Rengali PGCIL | 20205.4 | 29.2 | 15104.9 | 21.8
26 | Theruvali | 6817.1 | 9.8 | 4294.9 | 6.2
220kV
1 | Aska | 6372.8 | 16.7 | 5658.6 | 14.9
2 | Atri | 9698.2 | 25.5 | 8527.5 | 22.4
3 | Balasore | 3978.4 | 10.4 | 3690.8 | 9.7
4 | Balianta | 4831.4 | 12.7 | 3839.7 | 10.1
5 | Balichandrapur | 2891.1 | 7.6 | 2395 | 6.3
6 | Baliguda | 1276 | 3.3 | 1181.9 | 3.1
7 | Balimela | 7492.9 | 19.7 | 7917.3 | 20.8
8 | Bamra | 4601.8 | 12.1 | 3199.5 | 8.4
9 | Bargarh new | 3395.3 | 8.9 | 3113.6 | 8.2
10 | Barkote | 3587.7 | 9.4 | 3084.4 | 8.1
11 | Bhadrak | 8224.2 | 21.6 | 8140.7 | 21.4
12 | Bhadrak New | 8795.3 | 23.1 | 9071.8 | 23.8
13 | Bhanjanagar | 6439.2 | 16.9 | 5223 | 13.7
14 | Bidanasi | 10338.9 | 27.1 | 9153.1 | 24
15 | Bisra PGCIL | 11173.4 | 29.3 | 11241.7 | 29.5
16 | Bolangir new | 4421.5 | 11.6 | 4659.1 | 12.2
17 | Bolangir PGCIL | 4509.5 | 11.8 | 4805 | 12.6
18 | Bonai | 3238.7 | 8.5 | 2511.8 | 6.6
19 | Budhipadar | 17548 | 46.1 | 16379.3 | 43
20 | Chandaka | 9124.6 | 23.9 | 9561.6 | 25.1
21 | Chandaka-B | 9097.2 | 23.9 | 9438.2 | 24.8
22 | Chandiposh | 3885.3 | 10.2 | 2514.3 | 6.6
23 | Chendipada | 5240.8 | 13.8 | 3809.8 | 10
24 | Cuttack | 8433.1 | 22.1 | 7114.5 | 18.7
25 | Dasapalla | 2842.8 | 7.5 | 2110.1 | 5.5
26 | Deogarh | 3447.6 | 9 | 2487.6 | 6.5
27 | Dhamra | 2602.8 | 6.8 | 2156.2 | 5.7
28 | Dhenkanal (New) GIS | 9146 | 24 | 7392.7 | 19.4
29 | Duburi | 9951.6 | 26.1 | 9661.1 | 25.4
30 | Duburi new | 11198.1 | 29.4 | 12007 | 31.5
31 | Godachhack | 4745.9 | 12.5 | 3585.1 | 9.4
32 | Godisahi | 6129.9 | 16.1 | 5030.4 | 13.2
33 | Govindpalli | 1760.2 | 4.6 | 1565.6 | 4.1
34 | Gunupur | 2554.3 | 6.7 | 1967.8 | 5.2
35 | Indravati | 7287.4 | 19.1 | 8384.6 | 22
36 | Infocity II | 8659.6 | 22.7 | 7776.2 | 20.4
37 | ITPS | 10179.8 | 26.7 | 9189.7 | 24.1
38 | Jayanagar | 9896.5 | 26 | 10069.6 | 26.4
39 | Jayanagar PGCIL | 9868.6 | 25.9 | 10347.9 | 27.2
40 | Jayapatna | 2894.2 | 7.6 | 2328.8 | 6.1
41 | Joda | 4209.7 | 11 | 3536.6 | 9.3
42 | Kaikata | 2392.4 | 6.3 | 1851.2 | 4.9
43 | Kalimela | 1346.4 | 3.5 | 1208.8 | 3.2
44 | Kanas | 4369.5 | 11.5 | 3413.3 | 9
45 | Kantanada | 8481.6 | 22.3 | 7939.1 | 20.8
46 | Kasipur | 3280.2 | 8.6 | 2544.5 | 6.7
47 | Katapalli | 7195.7 | 18.9 | 6562.1 | 17.2
48 | Keonjhar | 5199.6 | 13.6 | 5221.7 | 13.7
49 | Keonjhar OPTCL | 5120.3 | 13.4 | 4922.4 | 12.9
50 | Kesinga | 2546.4 | 6.7 | 2548.2 | 6.7
51 | Khamar | 4531.7 | 11.9 | 3380.7 | 8.9
52 | Khandapada | 3806.8 | 10 | 2741.2 | 7.2
53 | Khuntuni | 11410.1 | 29.9 | 11515.8 | 30.2
54 | Kuakhia GIS | 3985.5 | 10.5 | 2910 | 7.6
55 | Kuanramunda | 5280.3 | 13.9 | 3976.3 | 10.4
56 | Kuchei | 6129.1 | 16.1 | 6656.9 | 17.5
57 | Lapanga | 13246.8 | 34.8 | 12672.7 | 33.3
58 | Laxmipur | 4834.6 | 12.7 | 3665.1 | 9.6
59 | Lephripada | 5474.7 | 14.4 | 3796.8 | 10
60 | M. Rampur | 1458 | 3.8 | 1353.7 | 3.6
61 | Malkangiri | 1253.6 | 3.3 | 1280.8 | 3.4
62 | Mendhasal | 11802.6 | 31 | 13159.8 | 34.5
63 | Meramundali (bus 1) | 17845.5 | 46.8 | 18412.3 | 48.3
64 | Meramundali (bus 2) | 17983.9 | 47.2 | 18562.4 | 48.7
65 | Meramundali-B | 8827.4 | 23.2 | 9090.9 | 23.9
66 | Nalco | 8319.9 | 21.8 | 9751.3 | 25.6
67 | Narasinghpur | 2661.5 | 7 | 2087.3 | 5.5
68 | Narendrapur | 6918.9 | 18.2 | 6781.5 | 17.8
69 | Narendrapur New | 7694.5 | 20.2 | 8011.8 | 21
70 | Nayagarh | 2797.9 | 7.3 | 2554.9 | 6.7
71 | Nuapada | 1473.1 | 3.9 | 1245.9 | 3.3
72 | Palhada | 2551.3 | 6.7 | 2066.1 | 5.4
73 | Pandiabil | 10292 | 27 | 10705.3 | 28.1
74 | Paradeep | 6321.1 | 16.6 | 6152.9 | 16.1
75 | Paradeep new | 6842.4 | 18 | 7076.1 | 18.6
76 | Pratapsasan | 7650.2 | 20.1 | 6450.9 | 16.9
77 | Rengali OS | 10527.9 | 27.6 | 10463.9 | 27.5
78 | Rengali PGCIL | 10399.4 | 27.3 | 10382.8 | 27.2
79 | Rengali PH | 10146.1 | 26.6 | 9823.5 | 25.8
80 | Samangara | 4013.9 | 10.5 | 3509.1 | 9.2
81 | STPS | 11878.2 | 31.2 | 11375.2 | 29.9
82 | Tarkera | 10157.8 | 26.7 | 9112.8 | 23.9
83 | Telkoi | 2420.9 | 6.4 | 1818.3 | 4.8
84 | Theruvalli | 6642.3 | 17.4 | 5270.7 | 13.8
85 | TTPS | 14596.7 | 38.3 | 13280.8 | 34.9
86 | Turumunga | 3598.5 | 9.4 | 3097.3 | 8.1
87 | Upper Kolab | 8511.1 | 22.3 | 8392.5 | 22

## Table 2
Short Circuit Fault Level of EHT Grids in Odisha, in MVA and kA
Sl. No. | Substation | 2026-27
|  | Three phase to ground fault |  | Single line to ground fault
|  | 3ph fault level (MVA) | 3ph fault current (kA) | SLG fault level (MVA) | SLG fault current (kA)
132kV
1 | Agarpada | 1705.2 | 7.5 | 1380.5 | 6
2 | Akhusingh | 1247.3 | 5.5 | 1078.4 | 4.7
3 | Anandpur | 2460.5 | 10.8 | 1996.6 | 8.7
4 | Angul | 3524.8 | 15.4 | 3126 | 13.7
5 | Argul | 2205.1 | 9.6 | 2177.8 | 9.5
6 | Aska | 3496.7 | 15.3 | 3536.6 | 15.5
7 | Aska (new) | 3709.9 | 16.2 | 3878 | 17
8 | Athamallik | 981.6 | 4.3 | 920.9 | 4
9 | Atri (Karadagadia) | 3565.8 | 15.6 | 3588.1 | 15.7
10 | Autonagar | 3240.1 | 14.2 | 3753.9 | 16.4
11 | Badagada | 5028 | 22 | 6129.3 | 26.8
12 | Bahugram | 1464.9 | 6.4 | 1451.5 | 6.3
13 | Balasore | 2640.4 | 11.5 | 2974.7 | 13
14 | Balianta | 3875 | 16.9 | 3841.1 | 16.8
15 | Balugaon | 1368.2 | 6 | 1484.6 | 6.5
16 | Bamra | 2817.3 | 12.3 | 2396.4 | 10.5
17 | Bangiriposi | 1543.4 | 6.8 | 1305.4 | 5.7
18 | Banki | 1514.1 | 6.6 | 1473.6 | 6.4
19 | Barbil | 1761 | 7.7 | 1579.2 | 6.9
20 | Bargarh | 1727.1 | 7.6 | 2068.3 | 9
21 | Bargarh (new) | 1758.4 | 7.7 | 2108.1 | 9.2
22 | Baripada | 2209.1 | 9.7 | 2389.5 | 10.5
23 | Barpali | 1480.2 | 6.5 | 1476.1 | 6.5
24 | Basta | 1120.9 | 4.9 | 1109.8 | 4.9
25 | Berhampur | 3251.8 | 14.2 | 3745.9 | 16.4
26 | Betanoti | 1017.3 | 4.4 | 959.1 | 4.2
27 | Bhadrak | 4153.9 | 18.2 | 4605.7 | 20.1
28 | Bhanjanagar | 2892 | 12.6 | 2910 | 12.7
29 | Bhatli | 1301.1 | 5.7 | 1295.6 | 5.7
30 | Bhawanipatna | 1225 | 5.4 | 1143.2 | 5
31 | Bhogarai | 837.9 | 3.7 | 899.7 | 3.9
32 | Bidanasi | 3580.2 | 15.7 | 3984.3 | 17.4
33 | Binika | 1141.9 | 5 | 864.9 | 3.8
34 | Birmaharajpur | 1094.6 | 4.8 | 1034.8 | 4.5
35 | Boinda | 1066 | 4.7 | 991.4 | 4.3
36 | Bolangir | 2601.2 | 11.4 | 2834.4 | 12.4
37 | Bolangir new | 2754.2 | 12 | 3055.1 | 13.4
38 | Bolani | 1589.6 | 7 | 1313.7 | 5.7
39 | Boriguma | 1405.1 | 6.1 | 1282.4 | 5.6
40 | Boudh | 1463.1 | 6.4 | 1430.2 | 6.3
41 | Brajrajnagar | 4029.8 | 17.6 | 3457.1 | 15.1
42 | Brundbahal | 1347.7 | 5.9 | 1066.7 | 4.7
43 | Budhipadar | 5866.3 | 25.7 | 5710.7 | 25
44 | Buguda | 1810.6 | 7.9 | 1479 | 6.5
45 | CDA | 3265.3 | 14.3 | 3192.3 | 14
46 | Chainpal | 6780.5 | 29.7 | 6863.2 | 30
47 | Chandaka | 6349 | 27.8 | 7792.3 | 34.1
48 | Chandaka-B | 6340.1 | 27.7 | 7785.6 | 34.1
49 | Chandbali | 1379.6 | 6 | 1499.7 | 6.6
50 | Chandikhole | 1687.2 | 7.4 | 1623.3 | 7.1
51 | Chandipur | 1737.1 | 7.6 | 1535.3 | 6.7
52 | Chandpur | 1223.8 | 5.4 | 1128.2 | 4.9
53 | Chendipada | 2245.5 | 9.8 | 2191.9 | 9.6
54 | Chhatrapur | 2867 | 12.5 | 2833.3 | 12.4
55 | Chhend | 4145.9 | 18.1 | 4098.4 | 17.9
56 | Chikiti | 1392.3 | 6.1 | 1398.1 | 6.1
57 | Chitalo | 1366.1 | 6 | 1053.5 | 4.6
58 | Choudwar | 3565.7 | 15.6 | 3568.7 | 15.6
59 | Cuttack | 3290.3 | 14.4 | 3424.3 | 15
60 | Dabugaon | 477.9 | 2.1 | 515.9 | 2.3
61 | Dhamra | 1484.2 | 6.5 | 1605.6 | 7
62 | Dhenkanal | 3422 | 15 | 3271 | 14.3
63 | Dhenkanal (New) GIS | 3597 | 15.7 | 3444.8 | 15.1
64 | Dhenkikote | 532.1 | 2.3 | 564.7 | 2.5
65 | Digapahandi | 2386.1 | 10.4 | 2256.1 | 9.9
66 | Duburi | 4597.4 | 20.1 | 4384.6 | 19.2
67 | G.Udaygiri | 1173.6 | 5.1 | 1023.8 | 4.5
68 | Ganjam | 1574.6 | 6.9 | 1363.6 | 6
69 | Ghens | 1018.1 | 4.5 | 1109.1 | 4.9
70 | Godachhak | 2642.6 | 11.6 | 2539.7 | 11.1
71 | Gondia | 1005.9 | 4.4 | 851.5 | 3.7
72 | Gunupur | 1719.3 | 7.5 | 1571.6 | 6.9
73 | Hinjlikut | 1959.3 | 8.6 | 1331.3 | 5.8
74 | Hirakud | 2971.5 | 13 | 2671.4 | 11.7
75 | Jagatsinghpur | 2473.6 | 10.8 | 2384.5 | 10.4
76 | Jajpur road | 4151.9 | 18.2 | 3798.4 | 16.6
77 | Jajpur town | 1851.6 | 8.1 | 1765.8 | 7.7
78 | Jaleswar | 1066.5 | 4.7 | 1162.2 | 5.1
79 | Jayanagar | 2993.9 | 13.1 | 3303.9 | 14.5
80 | Jayapatna | 1779.6 | 7.8 | 1753.1 | 7.7
81 | Jharsuguda | 4259 | 18.6 | 3481.5 | 15.2
82 | Joda | 2695.5 | 11.8 | 2705.6 | 11.8
83 | Junagarh | 1480.3 | 6.5 | 1444.2 | 6.3
84 | Kabisurjyanagar | 2176 | 9.5 | 1600.4 | 7
85 | Kalarangi | 2394.8 | 10.5 | 1958.3 | 8.6
86 | Kalunga | 2550.4 | 11.2 | 2394.3 | 10.5
87 | Kamakhyanagar | 1901.5 | 8.3 | 1650.6 | 7.2
88 | Kantabanji | 625.3 | 2.7 | 724.8 | 3.2
89 | Karanjia | 1087.2 | 4.8 | 1079.4 | 4.7
90 | Katapalli | 4617.5 | 20.2 | 4678 | 20.5
91 | Kendrapara | 3030.2 | 13.3 | 2909.7 | 12.7
92 | Kesinga | 2323.4 | 10.2 | 2491.5 | 10.9
93 | Kesura | 4754.9 | 20.8 | 5623.7 | 24.6
94 | Khajuriakata | 1591.2 | 7 | 1470.7 | 6.4
95 | Khariar | 1137.1 | 5 | 1227.1 | 5.4
96 | Khuntuni GIS | 2644.7 | 11.6 | 2421.5 | 10.6
97 | Khurda | 1338.7 | 5.9 | 1519.7 | 6.6
98 | Kodala | 1352.1 | 5.9 | 978.6 | 4.3
99 | Komna | 1077.7 | 4.7 | 876.9 | 3.8
100 | Konark | 1234.2 | 5.4 | 1064.8 | 4.7
101 | Kuakhia | 3075.2 | 13.5 | 2514.7 | 11
102 | Kuchei PGCIL | 2549.4 | 11.2 | 2822.6 | 12.3
103 | Kuchinda | 1346.5 | 5.9 | 1217.4 | 5.3
104 | Kumarmunda | 3167.7 | 13.9 | 2957.3 | 12.9
105 | Kutra | 1820.3 | 8 | 1131.4 | 4.9
106 | Lakhanpur (Belpahar) | 2051.8 | 9 | 1302.8 | 5.7
107 | Lamtaput | 870.7 | 3.8 | 619.9 | 2.7
108 | Lapanga | 6550 | 28.6 | 6450.3 | 28.2
109 | Mancheswar-A | 5965.9 | 26.1 | 7344.3 | 32.1
110 | Mancheswar-B | 5824.6 | 25.5 | 7281.1 | 31.8
111 | Maneswar | 1776.9 | 7.8 | 1535.3 | 6.7
112 | Mania (Tangi) | 1891.1 | 8.3 | 1633.9 | 7.1
113 | Marshaghai | 2171.6 | 9.5 | 1880.6 | 8.2
114 | Mendhasal | 3142.7 | 13.7 | 3013 | 13.2
115 | Meramundali | 6449.3 | 28.2 | 6099.9 | 26.7
116 | Mohana | 815.3 | 3.6 | 726.6 | 3.2
117 | Muniguda | 1290 | 5.6 | 1102.4 | 4.8
118 | Narendrapur | 3585.4 | 15.7 | 4155.6 | 18.2
119 | Navarangpur | 1011.8 | 4.4 | 767.4 | 3.4
120 | Nayapalli | 5608.3 | 24.5 | 6907.8 | 30.2
121 | Nimapara | 3076.4 | 13.5 | 2967.6 | 13
122 | Nuapada | 1223.2 | 5.4 | 1177.1 | 5.1
123 | Nuapara | 1223.2 | 5.4 | 1177.1 | 5.1
124 | Nuapatna | 1463.4 | 6.4 | 1497.7 | 6.6
125 | Olavar | 1348.2 | 5.9 | 1272.6 | 5.6
126 | Padampur | 962.4 | 4.2 | 1044.8 | 4.6
127 | Palasponga | 1114.8 | 4.9 | 1134.8 | 5
128 | Paradeep | 3809.3 | 16.7 | 3933.9 | 17.2
129 | Paralakhemundi | 1025.7 | 4.5 | 984.2 | 4.3
130 | Parjang | 2274.7 | 9.9 | 1524.9 | 6.7
131 | Parmanpur | 2547 | 11.1 | 1763.9 | 7.7
132 | Patnagarh | 1469.5 | 6.4 | 1465.5 | 6.4
133 | Pattamundai | 1643 | 7.2 | 1610.5 | 7
134 | Phulbani | 1104.2 | 4.8 | 1184.9 | 5.2
135 | Phulnakhara | 4151.5 | 18.2 | 3619.8 | 15.8
136 | Podagada | 882.5 | 3.9 | 761.4 | 3.3
137 | Pottangi | 976.5 | 4.3 | 900.1 | 3.9
138 | Pratapsasan | 5022 | 22 | 4854.7 | 21.2
139 | Puri | 2853.4 | 12.5 | 2994.7 | 13.1
140 | Purusottampur | 1967.1 | 8.6 | 1705.9 | 7.5
141 | R.Udayagiri | 1128.6 | 4.9 | 1070.3 | 4.7
142 | Raibania | 981.9 | 4.3 | 809.3 | 3.5
143 | Rairakhole | 902.8 | 3.9 | 828.2 | 3.6
144 | Rairangpur | 896.8 | 3.9 | 886.2 | 3.9
145 | Rajgangpur | 3023 | 13.2 | 2867.2 | 12.5
146 | Rajnagar | 1032.5 | 4.5 | 967.8 | 4.2
147 | Ranasinghpur | 3983.8 | 17.4 | 3976.4 | 17.4
148 | Rayagada | 1134.9 | 5 | 1036.4 | 4.5
149 | Rourkela | 4525.9 | 19.8 | 4598.7 | 20.1
150 | Saintala | 1183 | 5.2 | 1023.5 | 4.5
151 | Salipur | 1840.3 | 8 | 1758.4 | 7.7
152 | Samagara | 3185.8 | 13.9 | 3429.4 | 15
153 | Sambalpur | 2932.8 | 12.8 | 2924.5 | 12.8
154 | Satashanka | 2030.5 | 8.9 | 1766.5 | 7.7
155 | Satyanagar | 5683.7 | 24.9 | 7103.9 | 31.1
156 | Shamuka | 1701.5 | 7.4 | 1639.9 | 7.2
157 | Somnathpur | 1924.2 | 8.4 | 1802.8 | 7.9
158 | Sonepur | 1295.6 | 5.7 | 1398.2 | 6.1
159 | Soro | 1319 | 5.8 | 1358.6 | 5.9
160 | Sunabeda | 1758.7 | 7.7 | 1733.6 | 7.6
161 | Sundargarh | 2599.9 | 11.4 | 2215.9 | 9.7
162 | Tarabha | 1442.4 | 6.3 | 1059.9 | 4.6
163 | Tarkera | 4964.4 | 21.7 | 5256.9 | 23
164 | Tentulikhunti | 946.6 | 4.1 | 984.4 | 4.3
165 | Theruvalli | 2443.4 | 10.7 | 2382 | 10.4
166 | Thuapalli (Khuntulipalli) | 1071.2 | 4.7 | 796 | 3.5
167 | Thumula rampur | 1067.8 | 4.7 | 983.7 | 4.3
168 | Tirtol | 1654.9 | 7.2 | 1541.2 | 6.7
169 | Titlagarh | 1164.5 | 5.1 | 1010.7 | 4.4
170 | Turumunga | 2071.8 | 9.1 | 2026.2 | 8.9
171 | Tushra | 1126 | 4.9 | 1104.2 | 4.8
172 | Udala | 844.7 | 3.7 | 933 | 4.1
173 | Umerkote | 313 | 1.4 | 372.8 | 1.6
174 | Unit VIII | 5573.1 | 24.4 | 6924.8 | 30.3