## Sheet1
ODISHA POWER TRANSMISSION CORPORATION LIMITED
TRIPPING REPORT FOR THE MONTH OF APRIL-2023
Name of the Division: EHT(O&M), DIVISION LAPANGA
Sl. No. | Name of Grid S/S | Name of the feeder | Trip Time/ Date | Close time/Date | Duration | Relay Indication |  | Remarks
[6 empty] | Local end | Remote end
1 | 400/220/132/33KV GRID SS LAPANGA | 22OKV LAPANGA-KATAPALI CKT-I | 11:35/10.04.23 | 15:56/10.04.23 | 03HRS 21MINS | BPH-G, DIST-40.83KM,Z2,IL1-0.01KA,IL2-0.01KA,IL3-5.15KA | BPH-G, DIST-21.9KM,Z1,IL2-3.6KA | NIL
2 | 400/220/132/33KV GRID SS LAPANGA | 400KV LAPANGA-MERAMUNDALI CKT-II | 13:31/10.04.23 | 16:54/10.04.23 | 3HRS 23MINS | YPH-G, DIST-145.1KM,Z1,IL1-0.8KA,IL2-2.7KA,IL3-0.19KA | YPH-G, DIST-26.2KM,Z1,IL2-7.9KA | NIL
3 | 400/220/132/33KV GRID SS LAPANGA | 22OKV LAPANGA-KATAPALI CKT-I | 14:32/12.04.23 | 15:04/12.04.23 | 32MINS | BPH-G, DIST-36KM,Z2,IL1-0.04KA,IL2-0.05KA,IL3-3.214KA | BPH-G, DIST-35.055KM,Z1,IL1-0.41KA,IL2-0.59KA,IL3-2.837KA | NIL