## EVENT REPORT (hidden)
ODISHA POWER TRANSMISSION CORPORATION LIMITED | [10 empty] | INSTRUCTION
ENERGY ACCOUNTING AND BILLING SECTION, SLDC BHUBANESWAR
SUB-STATION CHANGE-IN EVENT REPORT
ZONE (CESU/NESCO/WESCO/SOUTHCO) | [8 empty] | YEAR: | 2019
SUBSTATION NAME : |  |  | 400/220/132/33KV GRID S/S,OPTCL,MENDHASAL
MONTH: |  |  | 2021-02-01
PHONE NO.- |  |  | 9438908147
NAME OF THE EVENT (S) | SL.NO. | (33kV/132kV)TYPE & (1ɸ/2ɸ/3ɸ) | DATE | TIME (in HRS) |  | TRF's on LOAD | TRF's under S/D | REMARKS |  |  | mention the PT voltage level & phase. During that period mention the transformers that were in loaded condition and those under shutdown.
PT / CT FAILURE or PT FUSE or PT LOOSE | 1 | NIL |  | START
STOP
CT RATIO CHANGE | SL.NO. | TRF/FDR NAME* | DATE | TIME (in HRS) |  | OLD RATIO | NEW RATIO | REMARKS |  |  | Mention the CT voltage level, old and new ratio, transformer or feeder name and phase.
| 1 | NIL |  | START
STOP
METER CHANGE | SL.NO. | TRF/FDR NAME | DATE | TIME (in HRS) |  | METER TYPE (MAIN/CHECK/ AUDIT) | OLD METER | NEW METER | S/D DURATION | REMARKS | Mention the Old meter Sl. No., new meter Sl. No., wether audit meter or billing meter, feeder name, MAIN/CHECK meter and duration of shutdown.
| 1 | 220kv Chandaka-3 |  | START |  | Apex-100, SECURE AUDIT METER | OPT00443 | OPT00541 | 0HRs:30MIN
STOP
TRANSFORMER CAPACITY UPGRADATION |  |  | MAKE & Sl. No. |  | TRF-I/II/III/IV/V | CAPACITY |  | DATE | TIME(HH:MM) | REMARKS | Mention the required details of the old and new transformer and if the respective meters have been changed or altered
|  | OLD TRANSFORMER | NEW 315MVA ICT-III |  |  |  | STOP DATE & TIME
|  | NEW TRANSFORMER |  |  |  |  | CHARGE DATE & TIME
TIME SYNCHRONISATION | SL.NO. | TRF/FDR NAME | METER TYPE (MAIN/CHECK) | MTR SL NO. |  |  |  | REMARKS |  |  | Mention the meters which have been time syncd by Secure Meters Ltd and Audit meters should not be mentioned.
| 1 | NIL
2
3
TRANSFORMER S/D PERIOD/DISCONNECTION TRANSFORMER FROM 33KV SIDE LOAD/ INCOMER FAILURE/ 132KV-220KV-400KV FEEDERS TRIPPINGS OR SHUTDOWNS | SL.NO. | TRF/FDR NAME | INTERRUPTION START |  | INTERRUPTION STOP |  | REASON | REMARKS |  |  | Mention interruption of Power Transformers, 220Kv/132 Kv Industrial feeders and Railway feeder due to any reason or interruption due to incomer failure
|  |  | DATE | TIME | DATE | TIME
| 1 | 400 kv mendhasal-meramundali ckt-I | 12.08.21 | 10:50 | 12.08.21 | 16:08 | L/c taken by line s/d mendhasal for tree branch cutting work at L.O.C-173
| 2 | 400 kv mendhasal-meramundali ckt-II | 2021-08-27 | 10:47 | 2021-08-27 | 13:19 | L/C taken by s/I meramundali for jumper tightening work.
| 3 | 220KV Msal-Bidanasi Ckt-II | 2021-08-09 | 9:09 | 2021-08-09 | 20:21 | L/c taken for Jumper tightening by line s/d m.sal
| 4 | 400KV Mnsal-Mrm Ckt-I | 2021-08-08 | 9:09 | 2021-08-08 | 17:20 | L/c taken for Jumper tightening by line s/d m.sal
| 5 | 220Kv Mndsal-bhanjanagar ckt | 2021-08-02 | 14:50 | 2021-08-04 | 18:18 | Ia=1.66ka,dis=95.6km,Snaping of Rph Conductor at LOC-40 B.nagar end
| 6 | 220Kv Mndsal-Atri-1 ckt | 2021-08-21 | 12:02 | 2021-08-21 | 16:59 | Replacement of N.I.T Switch at m.sal end.
| 7 | 220Kv Mndsal-Nayagarh ckt | 2021-08-11 | 15:08 | 2021-08-11 | 18:19 | L/C taken by s/I CDK
| 8 | 220Kv Mndsal-CDK-1 ckt | 2021-08-05 | 15:03 | 2021-08-05 | 16:55 | L/C tekan for jumper tightening at m.sal end.
| 9 | 220 kv mndsal-cdk-2 | 2021-08-11 | 7:57 | 2021-08-11 | 15:56 | Jumper tightening by line s/d m.sal
| 10 | 220 kv mndsal-cdk-3 | 2021-08-19 | 15:39 | 2021-08-19 | 18:26 | L/C taken by s/I cdk for mtc. Work at their end.
| 11 | 32Kv Mndsal-chandaka ckt | 2021-08-16 | 11:28 | 2021-08-16 | 11:39 | Il3=3.3ka,dis=23.7km,Il3-E
|  |  | 2021-08-23 | 8:06 | 2021-08-23 | 17:13 | L/C teken by S/I CDK for mtc. Work at their end.
| 12 | 100MVA AUTO-II | 2021-08-27 | 10:17 | 2021-08-27 | 17:59 | L/C taken for arresting of oil leakage by application of DEVCOM Compound by agency
|  |  | 2021-08-28 | 8:45 | 2021-08-28 | 17:17 | L/C taken for arresting of oil leakage by application of DEVCOM Compound by agency
| 5 | 400KV Mnsal-Mrm Ckt-II | 04.02.21 | 8:52 | 04.02.21 | 17:12 | L/C taken for maintenance work
| 6 |  | 13.02.21 | 14:08 | 13.02.21 | 15:09 | Tripped at their end,indication at our end.IL1-2.48ka,d-99.5km
| 7 |  | 24.02.21 | 13:17 | 24.02.21 | 19:09 | tripped by dp ,zone1 trip,IL1-5.49ka,dis-36.3km
| 8 | 220KV Mndsal-Atri Ckt.-I | 02.02.21 | 12:08 | 02.02.21 | 18:14 | L/C taken for line maintenance work
| 9 |  | 23.02.21 | 10:47 | 23.02.21 | 18:03 | L/C taken for maintenance work
| 10 | 220Kv Mndsal-Nayagarh ckt | 16.02.21 | 11:00 | 16.02.21 | 19:39 | L/C taken for maintenance work
| 11 | 220Kv Mndsal-Bhanjanagar ckt | 03.02.21 | 10:03 | 03.02.21 | 17:50 | L/C taken for line maintenance work
| 12 |  | 05.02.21 | 11:37 | 05.02.21 | 19:08 | L/C taken for R ph cvt replacement work
| 13 |  | 19.02.21 | 8:35 | 19.02.21 | 17:44 | L/C taken for line maintenance work
| 14 |  | 20.02.20 | 8:25 | 20.02.21 | 17:05 | L/C taken for line maintenance work
| 15 |  | 22.02.21 | 12:34 | 22.02.21 | 13:36 | L/C taken for maintenance work
| 16 |  | 24.02.21 | 12:48 | 24.02.21 | 13:13 | tripped by dp ,zone2 trip,IL1-1.14ka,dis-108km
| 17 | 132Kv Mndsal-khurda ckt | 10.02.21 | 7:01 | 10.02.21 | 18:44 | L/C taken for line maintenance work
| 18 | 100MVA AUTO-2 | 20.02.21 | 12:07 | 20.02.21 | 12:55 | L/C taken for maintenance work
| 17 | 132Kv Mndsal-khurda ckt | 10.02.21 | 7:01 | 10.02.21 | 18:44 | L/C taken for line maintenance work
| 18 | 100MVA AUTO-2 | 20.02.21 | 12:07 | 20.02.21 | 12:55 | L/C taken for maintenance work
DC supply fail to meters, Problem in download of meter data,any other issue related to Billing meter |  | TRF/FDR NAME | DATE |  |  | TIME (in HRS) |  | REMARKS |  |  | Mention DC supply related issues and any other issues that affects the billing meters
|  | NIL |  |  |  | START
STOP
SL.NO.
NEW ELEMENTS (TRF/FDR/STN.) ADDED |  | TRF/FDR NAME/STN TRF | DATE | TIME (in HRS) |  | MAIN METER | CHECK METER | STN. METER | REMARKS |  | Mention the elements added newly to the substation
|  | 315MVA ICT-III |  | START
STOP
SL.NO.
ANY OTHER ISSUES (like work done by E&MR on billing meters) |  | TRF/FDR NAME | DATE |  |  | TIME (in HRS) |  | REMARKS |  |  | Mention if any work has been done by E&MR on billing meters
START
STOP
SL.NO.
Load sharing pattern by all the Transformers |  | TRF-I | [8 empty] | Mention wether the transformers are always in parallel or the load is divided among them or if any TRF has been kept ideal/ unloaded.
TRF-II
TRF-III
*TRF=Transformer
FDR=Any 220/132/33 kv Feeder |  | N.B :- from 14.6.19 ,19:30Hrs Mendhasal grid availing station supply from CESU due to 33KV cable brusting.
Formulas:
TRF-I/II/III/IV/V = [DATE]
Note on A30: Mendhasala:

## Disturbance
ODISHA POWER TRANSMISSION CORPORATION LIMITED | [10 empty] | INSTRUCTION
ENERGY ACCOUNTING AND BILLING SECTION, SLDC BHUBANESWAR
SUB-STATION CHANGE-IN EVENT REPORT
ZONE (CESU/NESCO/WESCO/SOUTHCO) | [8 empty] | YEAR: | 2021
SUBSTATION NAME : |  |  | 400/220/132/33KV GRID S/S,OPTCL,MENDHASAL
MONTH: |  |  | 2023-04-01
PHONE NO.- |  |  | 9438908147
NAME OF THE EVENT (S) | SL.NO. | (33kV/132kV)TYPE & (1ɸ/2ɸ/3ɸ) | DATE | TIME (in HRS) |  | TRF's on LOAD | TRF's under S/D | REMARKS |  |  | mention the PT voltage level & phase. During that period mention the transformers that were in loaded condition and those under shutdown.
PT / CT FAILURE or PT FUSE or PT LOOSE | 1 | NIL |  | START
STOP
CT RATIO CHANGE | SL.NO. | 132KV MENDHASAL-KHORDA FDR | DATE | TIME (in HRS) |  | OLD RATIO | NEW RATIO | REMARKS |  |  | Mention the CT voltage level, old and new ratio, transformer or feeder name and phase.
| 1 | NIL | 09.03.23 | START |  | 400/1 | 800/1 | CT RATIO IN APEX METER HAS BEEN CHANGED TO 800/1 BY M/s SECURE METER
STOP
METER CHANGE | SL.NO. | TRF/FDR NAME | DATE | TIME (in HRS) |  | METER TYPE (MAIN/CHECK/ AUDIT) | OLD METER | NEW METER | S/D DURATION | REMARKS | Mention the Old meter Sl. No., new meter Sl. No., wether audit meter or billing meter, feeder name, MAIN/CHECK meter and duration of shutdown.
| 1 |  |  | START
STOP
TRANSFORMER CAPACITY UPGRADATION |  |  | MAKE & Sl. No. |  | TRF-I/II/III/IV/V | CAPACITY |  | DATE | TIME(HH:MM) | REMARKS | Mention the required details of the old and new transformer and if the respective meters have been changed or altered
|  | OLD TRANSFORMER | NEW 315MVA ICT-III |  |  |  | STOP DATE & TIME
|  | NEW TRANSFORMER |  |  |  |  | CHARGE DATE & TIME
TIME SYNCHRONISATION | SL.NO. | TRF/FDR NAME | METER TYPE (MAIN/CHECK) | MTR SL NO. |  |  |  | REMARKS |  |  | Mention the meters which have been time syncd by Secure Meters Ltd and Audit meters should not be mentioned.
| 1 | NIL
2
3
TRANSFORMER S/D PERIOD/DISCONNECTION TRANSFORMER FROM 33KV SIDE LOAD/ INCOMER FAILURE/ 132KV-220KV-400KV FEEDERS TRIPPINGS OR SHUTDOWNS | SL.NO. | TRF/FDR NAME | INTERRUPTION START |  | INTERRUPTION STOP |  | REASON | REMARKS |  |  | Mention interruption of Power Transformers, 220Kv/132 Kv Industrial feeders and Railway feeder due to any reason or interruption due to incomer failure
|  |  | DATE | TIME | DATE | TIME
|  | 400KV Mendhasal-meramunduli ckt-2 | 02.04.23 | 17:17 | 02.04.23 | 18:59 | Ir=5.78KA,Iy=0.61KA,Ib=0.64KA, Dist=32.9KM, at our end. Ir=4.66KA, 60.3KM, Dist= 71.69KM, at their end.
|  |  | 03.04.23 | 10:11 | 03.04.23 | 19:44 | Ir=5.33KA,Iy=0.51KA,Ib=0.81KA, Dist=33.2KM, at our end. Ir=3.91KA, Dist= 72.5KM, at their end.
|  |  | 04.4.23 | 9:56 | 04.4.23 | 18:35 | Ir=6.67KA,Iy=0.08KA,Ib=0.08KA, Dist= 27.6 KM, at our end. Ir=3.86KA, Dist= 76.3KM, at their end.
|  | 315MVA ICT-2 | 04.4.23 | 11:35 | 04.4.23 | 16:48 | L/C taken for attending of red hot on R-ph bus clamp.
|  |  | 07.04.23 | 6:29 | 07.04.23 | 9:14 | L/C taken for isolater maintance work.
|  |  | 16.4.23 | 6:18 | 16.4.23 | 13:06 | L/C taken for conductor replacement between 89C isolater and newly installed 52B Circuit breaker.
|  | 125MVAR BUS REACTOR | 04.4.23 | 14:48 | 04.4.23 | 17:09 | H/T due to over bus voltage.
|  |  | 27.04.23 | 15:03 | 30.04.23 | Till now | H/T due to over bus voltage.
|  | 220kv Mendhasal-Chandaka-3 | 05.4.23 | 9:04 | 06.04.23 | 15:20 | L/C taken for replacement of wavetrap at chandaka end.
|  | 220KV M.Sal-Chandaka-3 | 16.4.23 | 7:06 | 16.4.23 | 16:47 | L/C taken for jumpering work at new grid Kantabada.
|  | 220KV M.Sal-Chandaka-B | 18.4.23 | 12:32 | 18.4.23 | 15:12 | L/C issued to chandaka for maintance work.
|  | 315MVA ICT-1 | 05.4.23 | 10:05 | 05.4.23 | 16:08 | L/C taken for withdraw of online oil filtaration machine.
|  | 220kv Mendhasal-nayagarah | 06.04.23 | 19:24 | 06.04.23 | 20:19 | Ir=3.10KA, Dist=47.2KM, 861 862 optd
|  |  | 18.4.23 | 13:14 | 19.4.23 | 2:05 | H/T due to reducing the ICT load.
|  |  | 19.4.23 | 14:59 | 21.4.23 | 7:17 | H/T due to reducing the ICT load.
|  |  | 16.4.23 | 6:16 | 16.4.23 | 13:06 | H/T due to restrict load of ICT's at mendhasal
|  |  | 25.4.23 | 7:07 | 25.4.23 | 16:27 | L/C issued to Nayagarah for stringing of conductor work at LOC. No. 238
|  | 132KV Mendhasal - chandaka | 11.04.23 | 7:26 | 11.04.23 | 12:45 | L/C issued to chandaka for maintance work.
|  | 132KV Mendhasal - Khurdha | 11.04.23 | 13:18 | 12.04.23 | 4:09 | H/T due to minimize the load of ICT.
|  |  | 12.4.23 | 18:14 | 12.4.23 | 19:01 | tripped on following relay condition on dp relay=Iy=7.18KA, dist=6.2KM at remote end AR not successful Iy=4.33A, Dist= 17.1KM
|  |  | 18.4.23 | 13:08 | 18.4.23 | 21:43 | H/T due to reducing the ICT load.
|  |  | 19.4.23 | 13:08 | 19.4.23 | 18:00 | H/T due to reducing the ICT load.
|  |  | 20.4.23 | 7:56 | 20.4.23 | 22:50 | H/T for tree cutting work.
|  | 315MVA ICT-3 | 11.4.23 | 15:52 | 11.4.23 | 17:56 | L/C taken for checking of TC-1 and TC -2 of 52 Breaker.
|  |  | 25.4.23 | 6:29 | 25.4.23 | 10:24 | L/C taken for T isolater maintance work at LV side.
|  | 400KV Mendhasal-Pandibili ckt-2 | 11.4.23 | 18:07 | 11.4.23 | 23:28 | H/T due to snaping of conductor at their end.
|  | 100MVA AUTO-1 | 12.4.23 | 18:14 | 12.4.23 | 19:00 | Tripped on following relay condition on O/C and E/F dp relay=Ir= 0.11KA,Iy=0.11KA,Ib= 0.11KA 861 and 862 relay opt.
|  |  | 21.4.23 | 15:39 | 21.4.23 | 18:43 | Dismantling of T Isolater at 220KV side.
|  | 220KV Mendhasal - chandaka-I | 20.4.23 | 13:20 | 20.4.23 | 13:41 | IL1=0.30KA, IL2=0.23KA,IL3=0.43KA, 861 862 OPTD
|  | 220KV Mendhasal-Bidanasi ckt-2 | 20.4.23 | 13:20 | 20.4.23 | 16:21 | dist=12.4KM Ia=6.29KA A/R block RYB phase pickup
|  | 220KV M.Sal-B.nagar | 16.4.23 | 12:56 | 17.4.23 | 23:21 | Main 1 DP= y ph pickup e pickup zone 1 dist=117.5KM Ic=1.41KA Main 2 Dp= Yph pickup E pickup C-G loop Backup relay optd. , 86 1 and 86 2 optd.
|  |  | 25.4.23 | 16:31 | 25.4.23 | 19:25 | L/C taken for maintance work.
|  | 220/132KV 100MVA Auto-2 | 29.4.23 | 11:42 | 29.4.23 | 13:32 | To rectification of Red hot at B-phase bushing.
DC supply fail to meters, Problem in download of meter data,any other issue related to Billing meter |  | TRF/FDR NAME | DATE |  |  | TIME (in HRS) |  | REMARKS |  |  | Mention DC supply related issues and any other issues that affects the billing meters
|  | NIL |  |  |  | START
STOP
SL.NO.
NEW ELEMENTS (TRF/FDR/STN.) ADDED |  | TRF/FDR NAME/STN TRF | DATE | TIME (in HRS) |  | MAIN METER | CHECK METER | STN. METER | REMARKS |  | Mention the elements added newly to the substation
|  | 315MVA ICT-III |  | START
STOP
SL.NO.
ANY OTHER ISSUES (like work done by E&MR on billing meters) |  | TRF/FDR NAME | DATE |  |  | TIME (in HRS) |  | REMARKS |  |  | Mention if any work has been done by E&MR on billing meters
START
STOP
SL.NO.
Load sharing pattern by all the Transformers |  | TRF-I | [8 empty] | Mention wether the transformers are always in parallel or the load is divided among them or if any TRF has been kept ideal/ unloaded.
TRF-II
TRF-III
*TRF=Transformer
FDR=Any 220/132/33 kv Feeder |  | N.B :- from 14.6.19 ,19:30Hrs Mendhasal grid availing station supply from CESU due to 33KV cable brusting.
N.B=33kv gothaptana feeder charged 26.4.22 at 13:37
CT RATIO OF 132KV MND-KHORDA FDR CHANGED TO 800/1 FROM 400/1 BUT RATIO IN APEX METER IS 400/1 ,SECURE METER RERESENTIVE CONTACTED FOR RECTIFICATION
Note on A30: Mendhasala: