## Sheet1
Sl. No. | Substation | Date | From | To | Duration | Transmission element (Line / Tfr. / CB etc.)not available | Reason for non-availability of Transmission element (schedule maintenance outage / forced outage*)with details | Grid Sub-stations affected (it can be more than one) |  | Interruptio n time (Hr. Min.) | Extent of Generation Rescheduling |  | Energy lost in MU | Remarks | Feeders Affected
[11 empty] | MW reschedul ed or estimated capacity restriction affected | Time: This should match with hours of non- availability in a month in Format B-2 as the case may be
1 | Lapanga | 2024-04-01 | 08:53 | 09:19 | 00:26 | 160MVA Auto TRF-I | O/C, Ir- 2.18kA, Iy- 0.76kA, Ib- 0.23kA | Hirakud |  | 00:56 | - | - | 0.004084 | R Ph insulator burst at Loc No 118 from Lapanga end. | -
[6 empty] | 160MVA Auto TRF-II | O/C, Ir- 2.27kA, Iy- 0.08kA, Ib- 0.28kA
|  |  |  | 02.04.24 17:26 | 32:33:00 | 132kV Lapanga-Hirakud Feeder | At Lapanga end: R-N, Zone 1, Dist- 3.4km, Ir- 13.76kA At Hirakud end: E/F, Ir- 1.512kA
|  |  |  | 10:21 | 01:28 | 132kV Burla PH-Hirakud Feeder | At Burla PH end: E/F
2 | Bolangir | 2024-04-04 | 20:02 | 20:12 | 00:10 | 132kV Bolangir New-Bolangir CKT I | At Bolangir New end: O/C, Ir- 1.41kA At Bolangir Old end: O/C (Y-N), Zone 1, Dist- 3.946km, Iy- 4.285kA | Bolangir old ACME BEL |  | 00:10 00:49 00:09 | - | - | 0.007527 | - | -
|  |  |  | 20:25 | 20:25 | 132kV Bolangir New-Bolangir CKT II | O/C
|  |  |  | 20:54 | 20:54 | 132kV Bolangir-ACME Feeder | Zone 2, Ir- 2.846kA, Iy- 0.217kA, Ib- 0.299kA
|  |  |  | 20:07 | 00:05 | 132kV Saintala-BEL Solar Feeder | E/F
3 | Bidanasi | 2024-04-19 | 12:14 | 14:21 | 02:07 | 220kV Godisahi-Bidanasi Feeder | Y-B, Dist- 14.62km, Iy- 1.38kA, Ib- 2.33kA | Bidanasi, Brajabiharipur Godisahi Mania OCL Cuttack Jagatsinghpur Choudwar Choudwar RTSS |  | 00:25 00:45 00:40 00:24 00:11 00:04 00:12 00:39 | - | - | 0.076169 | - | -
|  |  | 12:21 | 12:45 | 00:24 | 220kV Mendhasal-Bidanasi Feeder | At Bidanasi end: Y-B, Zone 1, Dist- 14.62km, Iy- 1.33kA, Ib- 2.33kA At Mendhasal end: Y-B, Zone 1, Dist- 24.8km, Iy- 1.26kA, Ib- 5.35kA
|  |  |  | 12:50 | 00:29 | 132kV Mania-OCL Feeder | Remote end Tripping
|  |  |  | 14:34 | 02:13 | 220kV Cuttack-Bidanasi CKT I & II | Remote end Tripping 220kV Bidanasi- Cuttack CKT I & II H/T at Cuttack end due to overloading and alternate power supply availed from Phulnakharaa end.
|  |  |  | 16:42 | 04:21 | 132kV Mania-ICCL Feeder | Remote end Tripping
|  |  |  | 13:10 | 00:49 | 132kV Brajabiharipur-BPPL Feeder | Distance Protection, At BPPL end, Fault Distance-5.4km, Ir-0.19kA, Iy- 0.09kA, Ib-5.19kA. rnAt Brajabiharipur end, O/C & E/F Back up relay pick up in B-phase
|  |  |  | 15:07 | 02:46 | 132kV Jagatsinghpur-Cuttack Feeder | Remote end Tripping
4 | Bolangir New | 2024-04-19 | 16:27 | 18:08 | 01:41 | 132kV Bolangir New-Bolangir CKT I & II | Distance Protection, Ia- 532A, Ib- 2.813kA, Ic-2.514kA, Distance- 34.54km | Bolangir New, AFTAB Solar Bolangir old Patnagarh, Padampur, Nuapada, ALEX Solar, JYOTI Solar, Nuapada RTSS Sonepur, Birmaharajpur, Boudh, |  | 00:23 00:17 00:24 01:41 | - | - | 0.045736 | At 16:50hrs, 132kV Main bus charged through 160MVA Auto-II & III. At 18:40hrs, 160MVA Auto-I charged. | -
|  |  |  | 16:51 | 00:24 | 132kV Bolangir New-Patnagarh CKT I, II | Remote end Tripping
|  |  |  | 16:51 | 00:24 | 132kV Patnagarh-Padampur Feeder
|  |  |  | 16:51 | 00:24 | 132kV Nuapada-Padampur Feeder
|  |  |  | 18:08 | 01:41 | 132kV Boudh-Sonepur Feeder
|  |  |  | 18:08 | 01:41 | 132kV Sonepur-Birmaharajpur Feeder
5 | Choudwar | 2024-04-19 | 18:23 | 18:50 | 00:27 | 132kV Bidanasi-Choudwar Feeder | At Bidanasi end: Zone 2, Dist- 7.44km, Ir- 1.055kA, Iy- 1.25kA, Ib- 4.97kA At Choudwar end: O/C (R-Y-B), Zone 4, Dist- -0.199km, Ir- 4.985kA, Iy- 1.058KA, Ib- 1.254kA | Choudwar Choudwar RTSS, Mania, OCL |  | 00:27 00:26 | - | - | 0.032456 | - | -
|  |  |  | 20:54 | 02:31 | 132kV Mania-ICCL Feeder | Source failure
|  |  |  | 18:59 | 00:36 | 132kV Mania-OCL Feeder
6 | Pratapsasan | 2024-04-23 | 14:22 | 14:38 | 00:16 | 220kV Main Bus-1 of Pratapsasan | Bus bar Protection and 96 relay operated. | Pratapsasan Badagada Phulnakhara Jagatsinghpur |  | 00:16 00:08 00:20 00:10 | - | - | 0.02951 | - | -
|  |  |  | 14:47 | 00:25 | 132kV Phulnakhara-Bhubaneswar Feeder | O/C767.9,762.5,815.1A
|  |  |  | 14:48 | 00:26 | 132kV Jagatsinghpur-Cuttack Feeder | Remote end Tripping
|  |  |  | 14:44 | 00:22 | 132kV Nimapara-Pratapsasan Feeder | Distance ProtectionZ1 , BN, D- 24.05km , Ia-493.4A , Ib-2.165kA , Ic- 310.5A,
7 | Nimapara | 2024-04-26 | 07:25 | 07:34 | 00:09 | 132kV Nimapara-Pratapsasan Feeder | R-N, Zone 4, Dist- 0.188km, Ir- 2.517kA | Nimapara Samangara, Satasankha, Malatipatapur RTSS Konark |  | 00:08 00:18 00:26 | - | - | 0.023023 | Power supply availed from GSS Pratapsasan | -
|  |  | 07:25 | 08:00 | 00:35 | 132kV Chandaka-Nimapara Feeder | R-N, Zone 4, Dist- 0.674km, Ir- 1.77kA
|  |  | 07:26 | 07:45 | 00:19 | 132kV Samangara-Nimapara Feeder | Zone 1, Dist- 21.1km, Ir- 0.54kA
|  |  | 07:27 | 07:45 | 00:18 | 132kV Samangara-Satasankha CKT I & II | Remote end Tripping D/P, Zone 1, Ir- 0.54kA
8 | Joda | 2024-05-03 | 12:32 | 15:18 | 02:46 | 220kV Joda-JSPL Feeder | At Joda end: E/F At Jindal end: Y Ph, Iy- 0.718kA | JSPL |  | 02:48 | - | - | 0.13498 | During tripping Joda GSS availed power from 220kV Joda-TTPS CKT I (Telkoi), 220kV Joda- Ramchandrapur CKT. | -
|  |  |  | 15:18 | 02:46 | 220kV JSPL-Jamshedpur Feeder | At Joda end: E/F At Jamshedpur end: Y Ph, Zone 2, Dist- 147km,Iy- 0.77kA
|  |  |  | 15:37 | 03:05 | 220kV Joda-TTPS Feeder | At TTPS end: Ir- 0.019kA, Iy- 0.076kA, Ib- 0.125kA
9 | Kesinga | 2024-05-07 | 07:15 | 08.05.24 19:36 | 12:21 | 132kV Kesinga-POWMEX Feeder | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped | Kesinga, Junagarh POWMEX, SADIPALI Solar, Kesinga RTSS, Vento Power Solar Bhawanipatna, Bhawanipatna RTSS, Lanjigarh RTSS Khariar, Kantabanji, Kantabanji RTSS Tusura Deogaon RTSS BEL Solar, ABREL Solar, Aditya Solar Ordnance |  | 00:51 00:52 00:55 00:35 00:27 00:22 00:33 00:23 | - | - | 0.11019 | 220kV Bolangir PG-Kesinga line tripped from Bolangir PG end. All power transformers are pulled out.No power supply to Kesinga command are. Power supply resumed at 08:07 hrs. | -
|  |  |  | 08:59 | 02:09 | 132kV Kesinga-Bhawanipatna Feeder | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  |  |  | 08:14 | 01:09 | 132kV Bhawanipatna-Junagarh Feeder | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  |  |  | 08:12 | 00:57 | 132kV Kesinga-Junagarh Feeder | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  |  |  | 07:52 | 00:37 | 132kV Kesinga-Khariar Feeder | Transformer Failed from Kesinga end
|  |  |  | 07:38 | 00:23 | 132kV Saintala-Tusura Feeder | At Saintala end: O/C
|  |  |  | 07:38 | 00:23 | 132kV Saintala-ABREL Feeder | At Saintala end: E/F
10 | Bhadrak | 2024-05-12 | 14:58 | 15:49 | 00:51 | 220kV New Duburi-Bhadrak Feeder | At Bhadrak end: Remote End Tripping,IL1-2.05KA,IL2-0.41KA, IL3- 0.83KA | Bhadrak, FACOR Bhadrak RTSS, FACOR Power Dhamra Port Jajpur Town |  | 01:01 00:56 00:50 00:12 | - | - | 0.098393 | - | -
|  |  |  | 16:10 | 01:12 | 220kV Bhadrak-Balasore Feeder | At Bhadrak end: Remote End Tripping,IL1-1876.15A, IL2- 417.31A,IL3-850.12A, IN-915.85A At Balasore end: Distance Protection,Main-I: Dist R-ph, Optd,Zone-2,Zone-3,Auto reclose lock out OPTD,fault distance- 115.35KM, fault current- Ir=1876.151A, Iy=417.328 A, Ib=850.123A,In-915.858A.
|  |  |  | 16:54 | 01:56 | 132kV Bhadrak-Jajpur Town Feeder | At Jajpur Town end: Remote End Tripping
|  |  |  | 18:04 | 03:06 | 132kV Bhadrak-Soro Feeder | At Bhadrak end: Distance Protection,IL1-914.2A,IL2-279.8A,IL3- 147.3A, Zone-4,Distance-765.3Mtr
11 | Katapali | 2024-05-23 | 19:14 | 20:07 | 00:53 | 132kV Katapali-Thuapali Feeder | At Katapali end: Distance Protection,Distance protection optd in zone1 with fault distance of 1.02km, time duration=0.108ms IR=15KA, IY=100A, IB=69.2A At Thuapali end: Distance Protection,L1 to Earth Fault,Zone-1 trip FD-29.3KM,IL1-1.18KA,IL2- 0.01KA,IL3-0.00KA | Thuapali Bargarh New, Ghens, Bhatli |  | 00:53 00:21 | - | - | 0.02357 | - | -
|  |  |  | 19:29 | 00:15 | 132kV Katapali-Sambalpur Feeder | At Sambalpur end:Tripped on Z2, Z3, Bph E/F, Ia=645A, Ib=514A,Ic=2802A, Ig=2178A, Fault dist.=23.04KM, fault duration= 435.348ms No tripping at Katapali end
|  |  |  | 19:35 | 00:21 | 220kV Katapali-Bargarh New Feeder | At Bargarh New end: Earth Fault,IA- 0.09kA, IB-0.25kA,IC-0.21kA
|  |  |  | 19:35 | 00:21 | 132kV Bargarh New-Bhatli CKT I & II | At Bhatli end: Remote End Tripping,220kV Line tripped at source grid GSS Bargarh New.
|  |  |  | 20:09 | 00:55 | 100MVA Auto TRF III | At Katapali end: Earth Fault,Tripped with differential pick up and back relay pick up , weather condition is windy and heavy lightning
|  |  |  | 24.05.24 10:48 | 15:34 | 132kV Katapali-Burla PH CKT I | At Katapali end: Earth Fault,Back up relay optd with IR=0A, IY=0A, IB=5.94KA fault duration=0.108ms
12 | Budhipadar | 2024-06-01 | 19:30 | 20:21 | 00:51 | 220kV Budhipadar-IB CKT-III | At Budhipadar end: D/P operated, F.L=R-N, F.D=12 km, Ia=9.93kA Ib=491.2A, Ic=160.7 A, F. Resistance=1.57ohm Zone1, F. Duration=63.27ms | Rajgangpur, Rajgangpur RTSS OCL Bamra |  | 00:23 00:24 01:30 | - | - | 0.031262 | - | -
|  |  | 19:32 | 19:51 | 00:19 | 220kV Budhipadar-IB CKT-II | At Budhipadar end: D/P operated, F.L=R-N, F.D=9.17 km, Ia=11.13kA, Ib=636A, Ic=190.6 A, F. Resistance=1.27ohm, Zone1, F. Duration=76.69ms
|  |  | 19:36 | 20:03 | 00:27 | 220kV Budhipadar-Korba CKT-II | At Budhipadar end: D/P operated: F.L=R-N R-Phase CB Blast at Korba end. F.D=71.77 km, Ia=2.336kA Ib=176.83A, Ic=189.21A, In-2.353KA, Zone1, F. Duration=66.69ms At Korba end: D/P operated, F.L=R-N F.D=103.7 km, Ia=1.712kA Zone1, F. Resistance=7.8ohm
|  |  | 19:30 | 22:03 | 02:33 | 220kV Bamra-Tarkera Feeder | At Tarkera end: Distance Protection, DP MAIN1: DIST= 57.475 KM, LOOP=L1-N, ZONE-2, IL1=2644.49 A, IN= 2668.91 A DP MAIN2 : DIST=57.97 KM, ZONE- 2, LOOP : A-N, IA= 2.487 A, MT OPERATED
|  |  | 19:43 | 20:43 | 01:00 | 132kV Bamra-Rajgangpur Feeder | At Rajgangpur end: Over Current,TRIPPED AT BAMRA SIDE ZONE I,DISTANCE=8.193 KM,IA=4.64 KA,IB=288.6 A,IC=4.75 KA, FD=46.72 ms,FR=8.681 Ω,RT Time=80.09 ms
13 | Lapanga | 2024-06-01 | 20:53 | 22:37 | 01:44 | 132kV Lapanga-Hirakud Feeder | At Lapanga end: Distance Protection,MAIN RELAY-1:- FAULT LOOP-L1-E ZONE-1 IL1-13.86KA IL2- 0.06KA IL3-0.01KA DIST-1.7KM | Hirakud Aryan Ispat |  | 01:44 01:53 | - | - | 0.015914 | - | -
|  |  | 20:53 | 22:46 | 01:53 | 132kV Lapanga-Aryan Ispat Feeder | At Lapanga end: Distance Protection, MAIN RELAY-1:- FAULT LOOP-L1- L2 ZONE-1 IL1-9.2KA IL2-9.2KA IL3- 0.02KA DIST-6.2KM
|  |  | 20:55 | 02.06.24 13:26 | 16:31 | 132kV Budhipadar-Lapanga Feeder | At Lapanga end: Over Current,O/C,L1 L2 IL1-0.0KA IL2-0.03KA IL3-8.62KA PUT-441mSec
|  |  | 20:50 | 23:14 | 02:24 | 400kV Lapanga-OPGC CKT I | At Lapanga end: Distance Protection
|  |  | 20:57 | 23:49 | 02:52 | 400kV Lapanga-OPGC CKT II | At Lapanga end: Distance Protection, MAIN RELAY-1:- FAULT LOOP-L1-E ZONE-1 IL1-21.86KA IL2-0.47KA IL3- 0.60KA DIST-1.516KM
14 | Budhipadar | 2024-06-02 | 19:23 | 21:03 | 01:40 | 132kV Budhipadar-Bamra Feeder | At Bamra end: Distance Protection,D.P-Fault Loop- L2-N, Zone- 1, Distance-9.037KM, F.D- 71.58ms,RTT=79.90ms, Ia=287.5A, Ib=3.292KA,Ic=253.5A At Budhipadar end: D/P operated, F.L=Y-N, F.D=38.57 km, Ia=291A,Ib=1.804kA, Ic=241 A, F. Resistance=21.09ohm,Zone1, F. Duration=58.26 ms | Rajgangpur, OCL, Rajgangpur RTSS Kalunga Bamra |  | 00:23 00:21 01:40 | - | - | 0.053379 | - | -
|  |  | 19:41 | 03.06.24 10:38 | 14:57 | 132kV Bamra-Rajgangpur Feeder | At Bamra end: Earth Fault,Fault type= E/F & O/C, R-phase operated, , F.D=620 ms, RTT=65 ms ,Ia= 1.837KA, Ib= 170.3A, Ic= 203A, In=1.616KA Make & type of Relay- ALSTOM Micom & P141 At Rajgangpur end: Earth Fault,R- PH,Z1-PU/Z1 TRIP, ZONE- 1,IR=1.322 KA, IY=160.3 A, IB=192 A, DISTANCE=22.69 KM, MASTER TRIP RELAY OPERATED
|  |  | 19:27 | 22:36 | 03:09 | 132kV Kalunga-Budhipadar Feeder | At Kalunga end: DP Relay- Tripped Phase- R-N, Zone- 1, Fault location- 31.20 km, Fault duration- 53.31 ms,relay trip time - 79.97 ms, Ir-442.9 A, Iy-252.8A, Ib-448.5A,Vrn-23.07 kv,Vyn-74.73 kv , Vbn-73.99 kv, Fault Resistance- 30.03 ohm At Budhipadar end: zone-1,fault location-61.73 km,fault duration-54.97 ms, Ir-1.743 kA,Iy-234.1 A,Ib-443.6 A,fault resistance-1.424 ohm
|  |  | 19:49 | 20:03 | 00:14 | 220kV Budhipadar-VAL CKT II | At Budhipadar end: D/P operated, F.L=R-N,F.D=9 km,Ia=8.54kA,Ib=1.39kA, Ic=1.05kA, Zone 1
15 | Lapanga | 2024-06-05 | 03:46 | 16:30 | 12:44 | 132kV Budhipadar-Lapanga Feeder | At Lapanga end: O/C (R-N) | Budhipadar, MSP AAL BHUSAN Power MCL SMC Jharsuguda, Jharsuguda RTSS Ultratech |  | 00:46 01:08 01:06 06:18 00:43 01:02 01:14 | - | - | 0.27439 | - | -
|  |  | 03:47 | 10:05 | 06:18 | 132kV Budhipadar-MCL Feeder | At Budhipadar end: Over Current,(B.padar end ) D/P u2013 Tripped Phase-ABC, Fault loop- Bph to E, Zone 1, Dist- 1.57km, IL1- 135.9A, IL2-181.5A, IL3- 10.77kA, Fault duration- 70.01ms.
|  |  | 04:11 | 05:00 | 00:49 | 160MVA Auto TRF II Lapanga | At Lapanga end: Differenial
|  |  |  | 05:12 | 01:01 | 132kV Lapanga-Jharsuguda Feeder | At Lapanga end: R-N, Zone 1, Dist- 10.6km, Ir- 8.7kA | Bamra, Bamra RTSS Lephripada Brajarajnagar, Belpahar RTSS, Jurabanga MCL, Kechhobahal RTSS, Lakhanpur Kalunga |  | 00:30 01:04 01:03 00:47
|  |  |  | 06:03 | 01:52 | 132kV Budhipadar-Jharsuguda CKT II | At Jharsuguda end: B-N, Zone 1, Ir- 0.242kA, Iy- 0.819kA, Ib- 0.658kA
|  |  |  | 06:40 | 02:29 | 132kV Budhipadar-Jharsuguda CKT I | At Jharsuguda end: Y-B, Zone 1, Iy- 0.592kA, Ib- 0.683kA
|  |  | 04:12 | 08:20 | 04:08 | 220kV Budhipadar-Raigarh PG Feeder | At Budhipadar end: O/C (Y-B), Zone 4, Dist- -2.648km, Iy- 3.398kA, Ib- 3kA
|  |  |  | 08:21 | 04:09 | 220kV Budhipadar-Korba CKT III | At Budhipadar end: O/C (Y-B), Zone 4, Dist- -2.098km, Iy- 1.68kA, Ib- 1.487kA At Korba end): B-N, Zone 2, Dist- 201km, Ib- 0.94kA
|  |  |  | 05:04 | 00:52 | 220kV Bus Coupler | B/U Relay Trip, Fault Trip-BC to G Trip, Ia-261.1A, Ib-3.029Kamp, Ic- 2.681Kamp, In-0.14A, Ig-2.618Kamp
|  |  |  | 05:10 | 00:58 | 220kV Budhipadar-IB CKT I | D/P 1- Fault loop-L2 to E, Dist- 7km, IL1-2.13KA, IL2-2.5Kamp, IL3-2.16kA,
|  |  |  | 06:06 | 01:54 | 220kV Budhipadar-IB CKT II | Started phase-BC-N, tripped phase- ABC,zone-4,FD=-6.722KM,Ia- 629.4A,Ib-955.9A,Ic-799.5A,fault
|  |  |  | 20:24 | 16:12 | 220kV Budhipadar-IB CKT III | D/P 1-Zone-1, IL1-0A, IL2-309.8Amp, IL3-137.1A, Fault Duration-15.04ms,
|  |  |  | 06:07 | 01:55 | 220kV Budhipadar-IB CKT IV | D/P 1:-started phase BC-N, tripped phase-ABC,-Zone-4, Trip Phase-BCN,
|  |  |  | 09:05 | 04:53 | 220kV Budhipadar-Korba CKT I | Tripped from Korba KTPS end only
|  |  |  | 04:54 | 00:42 | 220kV Budhipadar-Lapanga CKT-I | D/P 1:-started phase ABC-N, tripped phase-ABC,Zone-4, Fault Duration- 302.5ms,Dist.1.912km,IL1-1.17KA, IL2- 4.452KAmp, IL3-3.944KA,
|  |  |  | 05:06 | 00:54 | 220kV Budhipadar-Lapanga CKT-II | D/P1-started phase-ABC-N, tripped phase-ABC,Zone-4,Dist.-2.3km,IL1- 1.18KA,IL2-4.08KAmp, IL3-3.6KA, /DP- 2 FL-L2-L3,Fault Duration-310.8 ms,Zone-4,IL1-1.18KA, IL24.08KA, IL3-
|  |  |  | 10:08 | 05:56 | 220kV Budhipadar-Bamra Feeder | D/P:-started phase-BC-N, tripped phase-ABC,FD-13.72KM, FD-304.1ms, Zone-4, IL1-111.7A, IL2-414.7A, IL3-
|  |  |  | 09:50 | 05:38 | 220kV Budhipadar-VAL CKT I | D/P1:- Fault Loop-B to C, Dist-7.4Kms, Fault current IL1-2.63KA, IL2-7.18KA,
|  |  | 04:35 | 05:17 | 00:42 | 220kV Budhipadar-BPSL CKT-I | H/T for restoration of power supply
|  |  |  | 09:22 | 04:47 | 220kV Budhipadar-BPSL CKT-II
|  |  |  | 05:37 | 01:02 | 220kV Budhipadar-Kuarmunda Feeder
|  |  |  | 05:20 | 00:45 | 220kV Budhipadar-AAL CKT-I & II
|  |  |  | 05:19 | 00:44 | 220kV Budhipadar-VAL CKT-II
|  |  |  | 06:56 | 02:21 | 220kV Budhipadar-SMC Feeder
|  |  | 04:41 | 04:57 | 00:16 | 160MVA Auto-I Budhipadar
|  |  |  | 06:12 | 01:31 | 160MVA Auto-II Budhipadar
|  |  | 04:55 | 05:08 | 00:13 | 132kV Budhipadar-Sundargarh CKT-I
|  |  |  | 05:50 | 00:55 | 132kV Budhipadar-Sundargarh CKT-I
|  |  |  | 11:11 | 06:16 | 132kV Budhipadar-Kalunga Feeder
|  |  |  | 18:41 | 13:46 | 132kV Budhipadar-Bamra Feeder
|  |  |  | 05:12 | 00:17 | 132kV Budhipadar-Brajarajnagar Feeder
|  |  |  | 08:52 | 03:57 | 132kV Budhipadar-Lakhanpur Feeder
|  |  |  | 05:30 | 00:35 | 132kV Budhipadar-MSP Feeder
16 | Therubali | 2024-06-06 | 18:31 | 19:22 | 00:51 | 220kV Therubali-Upper Kolab Feeder | At Upper Kolab end: Y-N, Zone 2, Dist-156.3km, Iy- 0.775kA | Rayagada |  | 00:10 | - | - | 0.002174 | - | -
|  |  |  | 19:25 | 00:54 | 220kV Therubali-Indravati CKT II | At Indravati end: YN,Z- 2,108.4KM,Iy=614.1A
|  |  |  | 19:25 | 00:54 | 220kV Therubali-Indravati CKT III | At Indravati end: YN,Z- 2,121.3KM,Iy=564.1A
|  |  |  | 19:27 | 00:56 | 220kV Therubali-Kasipur Feeder | At Kasipur end: YN,Z- 2,46.4KM,Iy=464.7A
|  |  |  | 21:05 | 02:34 | 160MVA Auto TRF-III | Tripped due to overfluxing.
|  |  |  | 20:32 | 02:01 | 220kV Therubali-Indravati CKT I | At Therubali end: YN,Z1,0.33KM,Iy=4.8KA No tripping at Indravati end.
|  |  |  | 22:05 | 03:34 | 220kV Therubali-Gunupur Feeder | At Therubali end: YN,Z1,0.06KM,Iy=8.6KA At Gunupur end: YN,Z2.73.9KM,Iy=869.6A
|  |  | 18:33 | 19:15 | 00:42 | 220kV Therubali-Aska New Feeder | At Aska New end: Earth Fault,Aska New end: rnALSTOM P444 D.P relay: A/.R lockout,Y phase to E/f,zone 2,distance= 197.7Km and IY= 667.5A. SIEMENS SIPROTEC 7SA52 D.P relay: A/R lockout,zone 2,L2E , distance=198.7Km and IL2= 0.79KA. At Therubali end: No tripping.
|  |  | 18:34 | 18:44 | 00:10 | 132kV Transfer BUS Rayagada | At Rayagada end:Earth Fault,Back up relay P141 operated, E/F, Ia=324.6 A, Ib=282 A, Ic=186.2 A, In=788.9 A
|  |  |  | 18:45 | 00:11 | 132kV Rayagada-Podagada Feeder | At Rayagada end:Earth Fault,132kV rayagada Buscoupler Feeder tripped on E/F relay indication. P141 back up relay operated, Ia=324.6 A, Ib=282 A, Ic=186.2 A, In=788.9 A
|  |  |  | 18:56 | 00:22 | 132kV Akhusingh-Rayagada Feeder | At Rayagada end:Earth Fault,132kV Rayagada Buscoupler CB tripped on E/F relay indication. Back up relay operated Ia=324.6 A, Ib=282 A, Ic=186.2 A, In=788.9 A
17 | Budhipadar | 2024-06-13 | 19:06 | 14.06.24 06:05 | 10:59 | 132kV Budhipadar-Jharsuguda CKT II | At Budhipadar end: Over Current, D/P(Areva P4): F.L-C-N, ZONE 1, il1- 531.3a,il2-235.3a,il3-13.5ka,F.R- 1.805ohm, F.D- 1.299km,F.DUR- 51.72ms, RTT- 80.06msrn At Jharsuguda end: Distance Protection,CN, zone-I, Ir= 532.1 A, Iy=236.5 A, Ib= 3.715 kA, Fault Resistance= 5.930 ohm1.299km,F.DUR- 51.72ms, RTT- 80.06ms | Jharsuguda MCL Bhusan SMC Aryan Ispat Rengali RTSS |  | 00:41 12:20 00:55 00:27 00:57 00:23 |  |  | 0.16536 | 132kV Budhipadar-Jharsuguda CKT I H/T at Budhipadar end for load management
|  |  | 19:09 | 23:05 | 03:56 | 220kV Budhipadar-Bhusan CKT II | At Budhipadar end: Over Current, D/P(MICOM P444) F.L- ABC, F.D- 977.5m, IA-25.99ka,IB-350.5a, IC- 354.0A,F.dur-51.07m. SOTF |  |  |  | - | - |  |  | -
|  |  | 19:11 | 20:07 | 00:56 | 220kV Budhipadar-Bhusan CKT I | At Budhipadar end: Over Current,(At Budhipadar end):D/P(MICOM P444):F.L- C-N,zone 1, F.D- 1.37km,IL1-182.2A,il2-377.7A,il3- 5.971ka,F.R-306.7mohm,F.dur-40ms
|  |  |  | 21:43 | 21:43 | 220kV Budhipadar-Raigarh PG Feeder | At Budhipadar end: Over Current, D/P 1(MICOM P444)- F.D- 1.104km, IA-20.97ka,IB-931.7a, IC- 266.0a,F.dur-524.9ms D/P 2(SIEMENS 7SA52)- F.L-L1`-E, pu time-521ms,F.D-1.2km ,IL1-21.49ka, IL2-0.9KA,IL3-0.2KArn R-phase limb of the CB burst.
|  |  |  | 22:56 | 03:45 | 220kV Budhipadar Korba CKT II | BB Protection & D/P 1- AR Block,IL1- 793.7A,IL2- 265.98,IL3-204.3A
|  |  |  | 20:02 | 00:51 | 160MVA Auto TRF II | Busbar Protection
|  |  |  | 21:46 | 02:35 | 220kV Budhipadar -IB CKT I
|  |  |  | 21:38 | 02:27 | 220kV Budhipadar -IB CKT II
|  |  |  | 20:46 | 01:35 | 220kV Budhipadar -IB CKT IV
|  |  |  | 19:46 | 00:35 | 220kV Budhipadar-Lapanga CKT II
|  |  |  | 20:11 | 01:00 | 220kV Budhipadar -AAL CKT I
|  |  |  | 20:10 | 00:59 | 220kV Budhipadar -AAL CKT II
|  |  | 19:19 | 14.06.24 07:40 | 12:21 | 132kV Budhipadar-MCL Feeder | At Budhipadar end: Over Current, D/P(MICOM P444): F.L- A-N, ZONE 1,F.DU- 65.07ms,F.D- 11.63km, IL1- 2.76ka,IL2-4.7A,IL3-4.112A
|  |  | 19:20 | 19:47 | 00:27 | 132kV Kuchinda-SMC Power Feeder | At Kuchinda end: Distance Protection, zone-2, location=47.07km Tripped phase Yph,Fault duration=130.3ms, Ir=59.59A,Iy=723A, Ib=45.87A, Fault resistnace=9.832 Ohm" At SMC end: zone-1, Tripped phase Yph,Fault duration=137ms, Ir=55.17A,Iy=392.3A, Ib=74.71A"
|  |  | 19:20 | 20:17 | 00:57 | 132kV Lapanga-Aryan Ispat Feeder | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE- 1 IL1-0.18KA IL2-0.13KA IL3- 11.10KA DIST-1.9KM
|  |  | 19:20 | 20:51 | 01:31 | 400kV Lapanga-OPGC CKT II | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE- 1 IL1-20.72KA IL2-0.375KA IL3- 0.39KA DIST-1.5KM
|  |  | 19:20 | 21:02 | 01:42 | 132kV Lapanga-SMC Feeder | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE- 1 IL1-0.07KA IL2-10.45KA IL3- 0.06KA DIST-1.8KM
|  |  | 19:29 | 20:50 | 01:21 | 132kV Lapanga-Hirakud Feeder | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE- 1 IL1-0.38KA IL2-0.25KA IL3- 12.38KA DIST-1.8KM
|  |  | 19:32 | 20:20 | 00:48 | 132kV Budhipadar-Lapanga Feeder | At Budhipadar end: Over Current,(AT Budhipadar end): D/P(SIEMENS 7SA52): F.L- L3-E, IL1-0.65KA,IL2- 0.42KA,IL3-2.98KArn At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L3-E ZONE- 1 IL1-0.65KA IL2-0.42KA IL3-9.12KA DIST-NA
|  |  | 19:33 | 20:02 | 00:29 | 132kV Lapanga-Jharsuguda Feeder | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE- 1 IL1-0.07KA IL2-0.23KA IL3- 10.03KA DIST-1.9KM At Jharsuguda end: No tripping
|  |  | 19:40 | 20:03 | 00:23 | 132kV Lapanga-Rengali RTSS Feeder | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L1-L3 ZONE- 1 IL1-6.4KA IL2-0KA IL3-6.47KA DIST-5.812KM
18 | Paradeep | 2024-06-20 | 12:41 | 12:51 | 00:10 | 132kV Kendrapara-Pattamundai Feeder | At Kendrapara end: Over Current,TRIPPED ON MASTER TRIP RELAY WITH IR=500A, IY=90A, IB=197.4A | Kendrapara Marshaghai, Kendrapada RTSS Paradeep, A. M. Nippon Steel, IFFCO, IOCL, PPL, PPT, Siju RTSS |  | 00:08 00:07 00:05 | - | - | 0.01419 | BOTH INCOMER FROM PARADEEP END TRIPPED CAUSING OVERLOADING OF PATTAMUNDAI FEEDER | -
|  |  |  | 12:46 | 00:05 | 220kV New Duburi-Paradeep CKT I | At Paradeep end: Over Current,O/C R,Y,B , Ir= 750 A , Iy= 1.02 kA , Ib= 1.18 kA
|  |  |  | 14:35 | 01:54 | 220kV New Duburi-Paradeep CKT II | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  |  |  | 12:48 | 00:07 | 132kV Marsaghai-Paradeep Feeder | At Marshaghai end: Remote End Tripping,source fail
|  |  |  | 12:48 | 00:07 | 132kV Marsaghai-Kendrapara Feeder | At Marshaghai end: Remote End Tripping,source failure
|  |  |  | 21:11 | 01:33 | 132kV Chainpal-TTPS CKT II | At Chainpal end: Remote End Tripping,DISTANCE PROTECTION, DISTANCE=19.68KM, L1-N, IA=1.88KA
19 | New Duburi | 2024-08-12 | 15:56 | 17:16 | 01:20 | 220kV New Duburi-Paradeep CKT I | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA | Paradeep, A. M. Nippon Steel, IFFCO, IOCL, PPL, PPT, Siju RTSS, tIRTOL Kendrapada, Marsaghai, Kendrapada RTSS Salipur Maithan Bamnipal | 00:25 00:47 00:09 01:27 00:35 | - | - | 0.074557 | GSS Bhadrak was availing P/S from Balasore GSS. Pattamundai Grid was availing power supply from Olaver Grid.No power interruption at Pattamundai GSS. | -
|  |  |  | 17:17 | 01:21 | 220kV New Duburi-Paradeep CKT II | At New Duburi end: Bus Bar Protection, Dist- 111.6km, Ir- 0.312kA, Iy- 0.195kA, Ib- 0.506kA At Paradeep end: O/C (B Ph), Zone 2, Dist- 111.6km, Ir- 0.392kA, Iy- 0.574kA, Ib- 0.941kA
|  |  |  | 13.08.24 12:20 | 20:24 | 220kV Main Bus-2 New Duburi | Bus Bar Protection
|  |  |  | 17:14 | 01:18 | 220kV New Duburi-Balimunda Feeder | B-N, Zone 4, Ir- 0304kA, Iy- 0.13kA, Ib- 0.831kA
|  |  |  | 17:23 | 01:27 | 220kV New Duburi-Maithan Feeder | At New Duburi end: Bus Bar Protection At Maithan end: B Ph, Ir-1.229kA, Iy- 1.934kA, Ib-3.172kA
|  |  |  | 19:58 | 04:02 | 220kV Duburi-New Duburi CKT I | At Duburi end: Y-B Ph, Dist- 4.897km, Iy-2.45kA, Ib- 2.337kA
|  |  |  | 17:34 | 01:38 | 220kV Duburi-New Duburi CKT II | At New Duburi end: Iy- 2.417kA, Ib- 2.337kA, Dist- 4.89km At Duburi end: Y-B Ph, Zone 1, Dist- 5.812km, Iy- 0.091kA, Ib- 2.533kA
|  |  |  | 16:31 | 00:35 | 132kV Daitari-Bamnipal Feeder | At Daitari end: O/C, Ir- 0.113kA, Iy- 0.126kA, Ib- 0.128kA
|  |  |  | 17:12 | 01:16 | 220kV New Duburi-Bhadrak Feeder | At Bhadrak end: Zone 2, O/C (B Ph), Ib-1.497kA, Dist- 67.34km
|  |  |  | 17:48 | 01:52 | 132kV Kendrapara-Pattamundai Feeder | At Pattamundai end: O/C (R-Y-B) , Ir- 0.53kA, Iy- 0.54kA, Ib- 0.52kA
|  |  |  | 16:15 | 00:19 | 220kV Meramundali-Meramundali B- Duburi Feeder | At Meramundali B end: Dist Protection
|  |  |  | 17:33 | 01:37 | 132kV Marsaghai-Paradeep Feeder | Source failure at Paradeep end
|  |  |  | 18:11 | 02:15 | 132kV Salipur-Kendrapara Feeder
20 | New Duburi | 2024-08-18 | 14:45 | 20:53 | 06:08 | 220kV New Duburi-JSL CKT I | At New Duburi end: O/C,Dist Protection, Remote End Tripping,BT BACK UP RELAY OPERATED,Dist- 5.381km,IL-1.039kA | Jindal | 06:08 | - | - | 0.28584 | - | -
|  |  |  | 29.08.24 17:50 | 267:05:00 | 220kV New Duburi-JSL CKT II | At New Duburi end: Dist Protection, Remote End Tripping,GENERAL TRIP ,B-PHASE PU,Zone 1 TRIP EF L3E LOOP Dist-1.3km I3- 6.82kA,GENERAL TRIP, B-PH PICK UP, E/F PU, ,Dist-4.358km,IL-1.3kA
|  |  |  | 21:28 | 06:43 | 220kV New Duburi-Paradeep CKT I | At New Duburi end: Zone 1 IL1- 7.09kA IL2-6.9kA IL3-1.4kA Dist- 0.2km At Paradeep end: O/C,Due to CT burst of jindal ckt II at New duburi end
|  |  |  | 15:21 | 00:36 | 315MVA ICT-2 New Duburi | Differenial,NO RECORD
|  |  |  | 15:33 | 00:48 | 220kV New Duburi-Dhamra Feeder | At New Duburi end: Dist Protection
|  |  |  | 15:34 | 00:49 | 220kV Duburi-New Duburi CKT II | At Duburi end: O/C,Back up Relay :- ,pick up - 535 ms,Trip Time - 447 ms
|  |  |  | 19:08 | 04:23 | 220kV Duburi-New Duburi CKT I | At Duburi end: Dist Protection,DP Relay :-,Started phase - C N,Fault Duration -346.4 ms,System Frequency - 50.04 Hz,Ia =94.67 Amp ,Ib- 136.0 Amp ,Ic= 2.893 kAmp,Van =120.2 KV ,Vbn =118.7 KV ,Vcn =19.18 KV,Back up Relay :-,Pick up - 543 ms,Trip time -450 ms,B-ph ,E/F
|  |  |  | 16:02 | 01:17 | 132kV Kendrapara-Ramco Feeder | At Kendrapara end: Dist Protection,Tripped on E/F and DP,Zone 1, Dist-25.17km, IR=2.84kA
21 | Budhipadar | 2024-08-30 | 18:42 | 20:07 | 01:25 | 132kV Budhipadar-Bamra Feeder | At Budhipadar end: A-N, ZONE 1, Dist-27.25km, IA-2.628kA, IB-68.50A, IC-821.8A At Bamra end: E/F, L1-N, Zone- 1, Dist-34.76km, Ia=1.536kA | MCL | 00:53 | - | - | 0.016834 | - | -
|  |  | 18:43 | 19:57 | 01:14 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: E/F, R-B-N, Zone-2, Dist-86.17 km, Ir=1.428 kA, Iy-22.28 A, Ib-1.403 kA At Budhipadar end: A-C-N, ZONE 1, Dist-18.26km, IA-3.45kA, IB-132.1A, IC-7.969kA
|  |  | 19:02 | 19:55 | 00:53 | 132kV Budhipadar-MCL Feeder | At Budhipadar end: Dist Protection,D/P operated: F.L- A-N, ZONE 2, Dist-17.78km, Distur- 340.0ms, IA-3.828kA, IB-117.4A, IC- 110.8A F.resistance-3.37ohm,
|  |  | 19:02 | 20:38 | 01:36 | 132kV Brajrajnagar-MCL Feeder | At Brajarajnagar end: Dist Protection,Zone 1, IL1= 1.15 kA, IL1- E, fault Dist- 20.6 km, fault duration- 352 ms
22 | Jaleswar | 2024-09-11 | 11:49 | 16:15 | 04:26 | 132kV Bhograi-Jaleswar | At Bhograi end: DP RELAY OPTD,Z- 1, 25KM,Bph-Gnd,Ir-63.2A,Iy- 20.1KA,Ib-831.9A At Jaleswar end: DP RELAY OPTD, Z-1, 25KM,Bph-Gnd,Ir-63.2A,Iy- 20.1KA,Ib-831.9A | Jaleswar, Jaleswar RTSS | 00:36 | - | - | 0.013894 | 132kV Trf-2 B Phase cross bus insulator was punctured and fallen on 132kV Main Bus at Jaleswar end. | -
|  |  |  | 12:20 | 12:20 | 132kV Jaleswar-Basta Feeder | At Basta end: Distance Protection,ABCN TRIPPED,ZONE- 2,Location-24.61km,IA-2.089KA,IB- 2.264KA,IC-2.27KA,Van- 23.35KV,Vbn-23.49KV,Vcn-21.36KV.
|  |  |  | 17:06 | 17:06 | 132kV Jaleswar-Baripada PG Feeder | At Jaleswar end: Distance Protection,Z4, Y-B-Gnd, Distance :2.2 KM , Ir-1695.3A, Iy-1662.8A, Ib- 1792.1A, Vrn-2.175 KV, Vyn-1.614 KV, Vbn-1.301 KV. At Baripada PG end: No tripping
|  |  |  | 12.09.24 22:45 | 34:56:00 | 132/33 kV 31.5MVA Trf-2 Jaleswar | Over Current,NO Logging of fault current.
23 | Chainpal | 2024-09-19 | 10:48 | 11:14 | 00:26 | 132/33 kV 40MVA Trf-1 Chainpal | 132kV Source failure. | Chainpal, Global, Talcher Fert. Ltd Chainpal RTSS Heavy Water | 00:37 00:32 00:57 | - | - | 0.029356 | 132kV Chainpal-Meramundali CKT- I was under L/C. Supply availed from TTPS by 132kV Bus Coupler. | -
|  | 2024-09-19 | 10:48 | 11:19 | 00:31 | 132kV Chainpal-RTSS Talcher Road
|  | 2024-09-19 | 10:48 | 11:26 | 00:38 | 132kV Chianpal-TFL-Global
|  | 2024-09-19 | 10:48 | 11:48 | 01:00 | 132/33 kV 40MVA Trf-2 Chainpal
|  | 2024-09-19 | 10:48 | 12:02 | 01:14 | 132kV Meramundali-Chainpal CKT II | At Chainpal end: Distance Protection,ZONE-1, L2-N, DISTANCE=5.12KM, IA=0.53kA, IB=0.39kA, IC=0.23kA At Meramundali end: Distance Protection,Remote End Tripping,Y-E, Z1, Iy-12.4 kA,Z1, Ir-533 A, Iy- 390 A, Ib- 230 A
|  | 2024-09-19 | 10:48 | 12:05 | 01:17 | 132/33 kV 20MVA Trf-3 Chainpal | 132kV Source failure.
24 | Kesinga | 2024-09-21 | 23:48 | 22.09.24 00:14 | 00:26 | 132kV Khariar-Kantabanji | TRIP FROM SOURCE END GSS KHARIAR END | Kesinga, POWMEX Kesinga RTSS Khariar, Kantabanji, Kantabanji RTSS Bhawanipatna, Junagarh, Bhawanipatna RTSS, | 00:23 00:24 00:26 00:40 | - | - | 0.057549 | - | -
|  |  |  | 22.09.24 00:10 | 00:22 | 220kV 160 MVA Auto Trf-1 Kesinga | Over Current,R ph-1.2 KA,Y ph-1.2 KA, B ph- 0.5 KA
|  |  |  | 22.09.24 00:45 | 00:57 | 220kV 160 MVA Auto Trf-2 Kesinga | Over Current,R ph-903.6 A,Y ph-235 A,B ph-503 A
|  |  |  | 22.09.24 00:31 | 00:41 | 132/33kV 20MVA Trf-3 Junagarh | Tripped on B/U relay.
25 | Marshaghai | 2024-09-29 | 22:41 | 23:00 | 00:19 | 132kV Marsaghai-kendrapara Feeder | At Marshaghai end: Relay Not Operated,incoming failure | Kendrapara Marsaghai, Kendrapara RTSS | 00:23 00:26 | - | - | 0.018528 | - | -
|  |  | 22:41 | 23:52 | 01:11 | 132kV Marsaghai-Paradeep Feeder | At Marshaghai end: Distance Protection,Distance-Zone-1(1.5 km), IL3 =2.15 KA
|  |  | 22:42 | 23:16 | 00:34 | 132kV Kendrapara-Paradeep Feeder | Earth Fault
|  |  | 22:43 | 22:46 | 00:03 | 132kV Salipur-kendrapara Feeder | At Salipur end: Relay Not Operated,No relay indication or tripping at Salipur end.
|  |  | 22:43 | 23:06 | 00:23 | 132kV Kendrapara-Pattamundai Feeder | At Pattamundai end: Over Current,Directional O/C(R,Y,B) Ir=0.41kA, Iy=0.39kA, Ib=0.43kA
|  |  | 23:01 | 23:09 | 00:08 | 132kV Marsaghai-kendrapara Feeder | At Marshaghai end: Relay Not Operated,source failure
|  |  | 23:16 | 23:19 | 00:03 | 132kV Marsaghai-kendrapara Feeder | At Marshaghai end: Relay Not Operated,source failure
26 | Rourkela | 2025-02-04 | 15:57 | 16:14 | 00:17 | 132kV Tarkera-Rourkela CKT-II | At Tarkera end: E/F, Ir- 0.312kA, Iy- 0.202kA, Ib- 0.271kA | Rourkela Bhalulata RTSS | 00:12 01:12 | - | - | 0.0104 | - | -
|  |  |  | 16:21 | 00:24 | 40MVA TRF-I | Ir- 0.223kA, Iy- 0.277kA, Ib- 0.253kA
|  |  |  | 16:16 | 00:19 | 35MVA TRF-II | Ir- 0.261kA, Iy- 0.151kA, Ib- 0.271kA
|  |  |  | 16:11 | 00:14 | 35MVA TRF-III | Ir- 0.233kA, Iy- 0.295kA, Ib- 0.29kA
|  |  |  | 16:09 | 00:12 | 35MVA TRF-IV | Ir- 0.369kA, Iy- 0.215kA, Ib- 0.256kA
|  |  |  | 17:09 | 01:12 | 132kV Rourkela-Bhalulata RTSS-Shree Jagannath Steel Feeder | At Rourkela end: Y-N, Zone 1, Dist- 1.33km, Iy- 5.598kA
27 | Khajuriakata | 2025-02-07 | 12:20 | 12:24 | 00:04 | 132kV Meramundali-Khajuriakata Feeder | At Khajuriakata end: Rph-N ,Z-1,Ir- 1.491kA,Dist-11.5kM At Meramundali end: R-N, Z1, 16.837 KM Ir -5.57 KA, In -5.08 KA | Khajuriakata Dhenkanal, Joranda RTSS, Khuntuni, Shree Cement Nuapatna, Banki | 00:04 00:07 00:06 | - | - | 0.008181 | - | -
|  |  |  | 12:27 | 00:07 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end: Incoming supply failed from Dhenkanal end
|  |  |  | 12:27 | 00:07 | 132kV Dhenkanal-Meramundali Feeder | At Dhenkanal end: R-Ph O/C, IR=379.9 A At Meramundali end: No tripping
|  |  |  | 12:26 | 00:06 | 132kV Nuapatna-Banki Feeder | Incomer Failure from GSS, Nuapatna
28 | Choudwar | 2025-02-12 | 07:49 | 08:12 | 00:23 | 132kV Bidanasi-Choudwar Feeder | At Choudwar end: Over Current At Bidanasi end: O/C R,Y,B phase, E/F. Ir-1.5kA, Iy-1.3kA, Ib-4.5kA | Choudwar, Choudwar RTSS Mania, Tata Steel Minning Ltd | 00:23 00:24 | - | - | 0.026124 | - | -
|  |  |  | 08:16 | 00:27 | 132kV Choudwar-TS Alloys Feeder | At Choudwar end: Over Current At TS Alloys: O/C , E/F
|  |  |  | 08:48 | 00:59 | 132kV ICCL-Choudwar Feeder | At Choudwar end: Over Current, O/C R,Y,B phase, E/F. At ICCL end: No tripping
29 | Patnagarh | 2025-02-22 | 17:50 | 18:02 | 00:12 | 132kV Patnagarh-Bolangir New CKT-I | Tripped during E&MR testing | Patnagarh, Padampur, Nuapada, Nuapada RTSS | 00:12 | - | - | 0.01486 | - | -
|  |  |  | 18:01 | 00:11 | 132kV Patnagarh-Bolangir New CKT-I | Tripped on O/C due to tripping of 132KV ckt-I
|  |  |  | 18:02 | 00:12 | 132kV Nuapada-Padampur Feeder, 132kV Padampur-Patnagarh Feeder | Source failure
30 | Bolangir New | 2025-03-15 | 13:08 | 13:37 | 00:29 | 160 MVA Auto Trf-3 | At Bolangir New end: Over Current,Started ph- Y B, Tripped ph- RYB, Ia=187.3A, Ib=572.1A, Ic=444.9A, Fault duration= 198ms | GSS Barpali | 0:08 | - | - | - | At 13.08hrs, 132KV Barpali ckt & 220KV Kesinga ckt tripped automatically as LADR scheme is implemented. 220KV Kesinga ckt charged at 13.42hrs & 132KV Barpali ckt charged at 13.43 hrs. | -
|  |  |  | 13:16 | 00:08 | 132 kV Saintala-Tusura Feeder | At Saintala end: B AND C, ZONE-2, LOCATION-25.31KM,Ia-56.3A,Ib- 1.227kA,Ic-1.99kA
|  |  |  | 13:16 | 00:08 | 132 kV Tusura-Vento Solar ckt-2 | O/C, Fault Loaction- 6.41Km, Zone-2, Ia- 34.22A, Ib- 3.19KA, Ic- 3.19KA
31 | Jayanagar | 2025-03-24 | 02:38 | 07:55 | 05:17 | 132 kV Sunabeda-Jayanagar Ckt-1 | At Jayanagar end: Distance Protection,Z1,R-G,DIST-7.3KM,If- 0.75KA | Jayanagar Sunabeda Jayanagar RTSS Tentulikhunti Potangi, Dabugaon, Umerkote | 01:26 04:05 02:45 00:52 01:02 | - | - | - | - | -
|  |  |  | 07:56 | 05:18 | 132 kV Sunabeda-Jayanagar Ckt-2 | At Jayanagar end: Over Current,Backup relay operated. B- G,If-0.268KA
|  |  |  | 02:51 | 00:13 | 132 kV Jayapatna-Dabugaon Feeder | At Jayapatna end: Distance Protection,Ia=461.5Amp,Ib=773.9Amp ,Ic=248.5Amp,Zone-3,Fault Distance=134.1KM, O/C(R&Y Ph)
|  |  |  | 03:30 | 00:52 | 132 kV Tentulikhunti-Jayanagar Feeder Feeder | At Jayanagar end: Over Current,- Reverse protection zone-5 of 656A (Y phase)
|  |  |  | 07:03 | 04:25 | 132 kV Main BUS Jayanagar | At Jayanagar end: Relay Not Operated,Y-Phase jumper from 132KV Main bus to Single Isolator is snapped.
|  |  |  | 07:03 | 04:25 | 220/132 kV 160 MVA Auto Trf-1 Jayanagar | At Jayanagar end: Over Current,If- 4KA
|  |  |  | 08:56 | 06:18 | 220/132 kV 160 MVA Auto Trf-2 Jayanagar | At Jayanagar end: Over Current,If- 4KA
|  |  |  | 02:57 | 02:57 | 132 kV Dabugaon-Umerkote | Failure from Dabugaon end.
32 | Meramundali | 2025-01-11 | 18:08 | 18:43 | 00:35 | 132kV Meramundali-Dhenkanal Feeder | At Meramundali end: R-N, Zone 1, Ir- 3.85kA, Dist- 24.6km At Dhenkanal end: R-N, Ir- 1.35kA, Zone 1, Dist- 16.65km | Dhenkanal, Joranda RTSS Khuntuni, Shree Cement | 00:23 00:29 | - | - | 0.016912 | - | -
|  |  |  | 18:30 | 00:22 | 132kV Khajuriakata-Nuapatana- Dhenkanal Feeder | At Khajuriakata end: R-N, Zone 1, Dist- 142.9km, Ir- 0.631kA No tripping at Dhenkanal end.
|  |  |  | 18:34 | 00:26 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end: Remote End Tripping
33 | Rourkela | 2025-02-04 | 15:57 | 16:14 | 00:17 | 132kV Tarkera-Rourkela CKT-II | At Tarkera end: E/F, Ir- 0.312kA, Iy- 0.202kA, Ib- 0.271kA | Rourkela Bhalulata RTSS | 00:12 01:12 | - | - | 0.0104 | - | -
|  |  |  | 16:21 | 00:24 | 40MVA TRF-I | Ir- 0.223kA, Iy- 0.277kA, Ib- 0.253kA
|  |  |  | 16:16 | 00:19 | 35MVA TRF-II | Ir- 0.261kA, Iy- 0.151kA, Ib- 0.271kA
|  |  |  | 16:11 | 00:14 | 35MVA TRF-III | Ir- 0.233kA, Iy- 0.295kA, Ib- 0.29kA
|  |  |  | 16:09 | 00:12 | 35MVA TRF-IV | Ir- 0.369kA, Iy- 0.215kA, Ib- 0.256kA
|  |  |  | 17:09 | 01:12 | 132kV Rourkela-Bhalulata RTSS-Shree Jagannath Steel Feeder | At Rourkela end: Y-N, Zone 1, Dist- 1.33km, Iy- 5.598kA
34 | Khajuriakata | 2025-02-07 | 12:20 | 12:24 | 00:04 | 132kV Meramundali-Khajuriakata Feeder | At Khajuriakata end: Rph-N ,Z-1,Ir- 1.491kA,Dist-11.5kM At Meramundali end: R-N, Z1, 16.837 KM Ir -5.57 KA, In -5.08 KA | Khajuriakata Dhenkanal, Joranda RTSS, Khuntuni, Shree Cement Nuapatna, Banki | 00:04 00:07 00:06 | - | - | 0.008181 | - | -
|  |  |  | 12:27 | 00:07 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end: Incoming supply failed from Dhenkanal end
|  |  |  | 12:27 | 00:07 | 132kV Dhenkanal-Meramundali Feeder | At Dhenkanal end: R-Ph O/C, IR=379.9 A At Meramundali end: No tripping
|  |  |  | 12:26 | 00:06 | 132kV Nuapatna-Banki Feeder | Incomer Failure from GSS, Nuapatna
35 | Choudwar | 2025-02-12 | 07:49 | 08:12 | 00:23 | 132kV Bidanasi-Choudwar Feeder | At Choudwar end: Over Current At Bidanasi end: O/C R,Y,B phase, E/F. Ir-1.5kA, Iy-1.3kA, Ib-4.5kA | Choudwar, Choudwar RTSS Mania, Tata Steel Minning Ltd | 00:23 00:24 | - | - | 0.026124 | - | -
|  |  |  | 08:16 | 00:27 | 132kV Choudwar-TS Alloys Feeder | At Choudwar end: Over Current At TS Alloys: O/C , E/F
|  |  |  | 08:48 | 00:59 | 132kV ICCL-Choudwar Feeder | At Choudwar end: Over Current, O/C R,Y,B phase, E/F. At ICCL end: No tripping
36 | Therubali | 2025-03-10 | 13:46 | 14:36 | 00:50 | 220 kV Gunupur-Therubali Feeder | At Therubali end: Distance Protection,At Therubali end:RG,- 2.6KM,Ir=4.201KArnAt Gunupur end:No TRIPrn | - | - | - | - | - | - | -
|  |  | 13:46 | 17:30 | 03:44 | 220 kV Therubali-Indravati PH Ckt-1 | At Therubali end: Distance Protection,At Therubali end:RY,Z1,9.41KM,Ir=6.322KA,Iy=6.3 56KArnAt Indrabati end:RY,Z1,68.9KM,Ir=1.119KA,Iy=1.0 76KArn
|  |  | 13:50 | 14:08 | 00:18 | 220 kV Therubali-Aska New Feeder | At Therubali end: Distance Protection,At Therubali end:No TriprnAt Aska New end:RY,Z3,276.7KM,Ir=0.618KA,Iy=0. 54KArn
37 | Bolangir New | 2025-03-15 | 13:08 | 13:37 | 00:29 | 160 MVA Auto Trf-3 | At Bolangir New end: Over Current,Started ph- Y B, Tripped ph- RYB, Ia=187.3A, Ib=572.1A, Ic=444.9A, Fault duration= 198ms | GSS Barpali | 0:08 | - | - | - | At 13.08hrs, 132KV Barpali ckt & 220KV Kesinga ckt tripped automatically as LADR scheme is implemented. 220KV Kesinga ckt charged at 13.42hrs & 132KV Barpali ckt charged at 13.43 hrs. | -
|  |  |  | 13:16 | 00:08 | 132 kV Saintala-Tusura Feeder | At Saintala end: B AND C, ZONE-2, LOCATION-25.31KM,Ia-56.3A,Ib- 1.227kA,Ic-1.99kA
|  |  |  | 13:16 | 00:08 | 132 kV Tusura-Vento Solar ckt-2 | O/C, Fault Loaction- 6.41Km, Zone-2, Ia- 34.22A, Ib- 3.19KA, Ic- 3.19KA
38 | Jayanagar | 2025-03-24 | 02:38 | 07:55 | 05:17 | 132 kV Sunabeda-Jayanagar Ckt-1 | At Jayanagar end: Distance Protection,Z1,R-G,DIST-7.3KM,If- 0.75KA | Jayanagar Sunabeda Jayanagar RTSS Tentulikhunti Potangi, Dabugaon, Umerkote | 01:26 04:05 02:45 00:52 01:02 | - | - | - | - | -
|  |  |  | 07:56 | 05:18 | 132 kV Sunabeda-Jayanagar Ckt-2 | At Jayanagar end: Over Current,Backup relay operated. B- G,If-0.268KA
|  |  |  | 02:51 | 00:13 | 132 kV Jayapatna-Dabugaon Feeder | At Jayapatna end: Distance Protection,Ia=461.5Amp,Ib=773.9Amp ,Ic=248.5Amp,Zone-3,Fault Distance=134.1KM, O/C(R&Y Ph)
|  |  |  | 03:30 | 00:52 | 132 kV Tentulikhunti-Jayanagar Feeder Feeder | At Jayanagar end: Over Current,- Reverse protection zone-5 of 656A (Y phase)
|  |  |  | 07:03 | 04:25 | 132 kV Main BUS Jayanagar | At Jayanagar end: Relay Not Operated,Y-Phase jumper from 132KV Main bus to Single Isolator is snapped.
|  |  |  | 07:03 | 04:25 | 220/132 kV 160 MVA Auto Trf-1 Jayanagar | At Jayanagar end: Over Current,If- 4KA
|  |  |  | 08:56 | 06:18 | 220/132 kV 160 MVA Auto Trf-2 Jayanagar | At Jayanagar end: Over Current,If- 4KA
|  |  |  | 02:57 | 02:57 | 132 kV Dabugaon-Umerkote | Failure from Dabugaon end.
39 | Kendrapara | 2025-04-05 | 12:56 | 13:11 | 0:15 | 132kV Kendrapara-Chandikhol Feeder | At Kendrapara end: E/F, Zone 3, Dist- 56.34km, Iy- 1.57kA, Ib- 1.72kA | Chandikhol, MTPCL | 0:15 | - | - | 0.008435 | - | -
|  |  |  | 13:19 | 0:23 | 132kV Jajpur road-Chandikhole Feeder | At Jajpur Road end: Ir- 0.25kA, Iy- 4.5kA, Ib- 4.29kA, Zone 1, Dist- 16.16km
|  |  |  | 14:29 | 1:33 | 132kV Chandikhol-MTPCL CKT-I | Tripped due to synchronization failure
|  |  |  | 13:25 | 0:29 | 132kV Chandikhol-MTPCL CKT-II
40 | Rairangpur | 2025-04-06 | 7:56 | 8:26 | 0:30 | 132kV Rairangpur-Karanjia Feeder | At Rairangpur end: B-N, Zone 2, Dist- 70.13km, Ib- 0.559kA | Karanjia Dhenkikote MSP | 00:30 01:02 00:33 | - | - | 0.0152 | - | -
|  |  |  | 8:29 | 0:33 | 132kV Polasponga-Turumunga Feeder | At Polasponga end: Remote end Tripping
|  |  |  | 9:28 | 1:32 | 132kV Karanjia-Dhenkikote Feeder | Source failure from Karanjia end
41 | Khajuriakata | 2025-04-07 | 03:19 | 3:34 | 0:15 | 132kV Khajuriakata-Nuapatana- Dhenkanal Feeder | At Khajuriakata end: E/F (R-N), Zone 1, Ir- 0.981kA, Dist- 49.6km | Khuntuni, Dhenkanal, Joranda RTSS, Shree Cement | 0:15 | - | - | 0.015181 | At the time fault 132kV Khajuriakata-Meramundali Line is in service. | -
|  |  |  | 3:34 | 0:15 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end: Incoming supply failed from Meramundali GSS
|  |  |  | 3:41 | 0:22 | 132kV Meramundali-Dhenkanal Feeder | At Meramundali end: R-N, Ir- 3.15kA, Zone 1, Dist- 24.64km At Dhenkanal end: R-N, Ir- 0.318kA, Zone 1, Dist- 17.53km
42 | Bargarh New | 2025-04-16 | 5:57 | 10:38 | 4:41 | 220kV Bargarh New-Bolangir New Feeder | BUS BAR PROTECTION 96 | Bargarh, ACC, Bhatli Bargarh New Barapalli, Dunguripali RTSS Ghess | 00:35 00:53 00:33 01:00 | - | - | 0.10154 | - | -
|  |  |  | 6:50 | 6:50 | 220kV Bargarh New-Katapali Feeder | BUS BAR PROTECTION 96
|  |  |  | 6:51 | 6:51 | 160MVA AUTO TRF II | BUS BAR PROTECTION 97, Buchholz trip alarm
|  |  |  | 6:56 | 6:56 | 100MVA AUTO TRF I | BUS BAR PROTECTION 96, O/C & E/F (Ia- 0.31, Ib-0.31 & Ic-0,31)
|  |  |  | 6:57 | 1:00 | 132kV Bargarh New-Ghess CKT-I & II | Source failure from 220/132/33kV Bargarh New end.
43 | Budhipadar | 2025-04-18 | 17:49 | 19.04.25 00:45 | 6:56 | 220kV Budhipadar-Kuarmunda Feeder | D/P-1(Micom P444):-FL-Bph-E, Zone-2, FD- 97.39KM, IL1-192.3A, IL2-325.5A, IL3- 1.84KA,fault duration-126.9ms AR Successfully from Budhipadar end. | Kuarmunda | 1:15 | - | - | 0.017537 | - | -
|  |  | 17:53 | 19.4.25 12:06 | 18:13 | 220kV Budhipadar-Bamra Feeder | At Budhipadar end: D/P-1(Micom P444):-FL- Rph-E, Zone 1, FD-13.63KM, IL1-9.633KA, IL2- 73.31A, IL3-160.5A,fault duration-66.78ms D/P-2(Siemens):-FL-Rph-E, Zone 1, FD- 13.13KM, IL1-10.77KA, IL2-0.11KA, IL3- 0.15KA At Bamra end: D/P-1(Micom P444):-FL-Rph- E, Zone 1, FD-34.83KM, IL1-2.424KA, IL2- 86.45A, IL3-160.9A,fault duration-51.75ms D/P-2(GE D60):-FL-Rph-E, Zone 1, FD- 37.8KM, IL1-1215.266A, IL2-45.831A, IL3-
|  |  | 17:58 | 18:46 | 0:48 | 132kV Kuchinda-SMC Feeder | 1)Fault Loop - R-N,E/F, 2) Zone -01, 3) Dist : 29.53 KM, 4) IR=968.2A, Iy=50.41A, IB=60.92A, 5)Fault duration = 49.94 ms 6) Fault Resistance= 6.192 ohm
|  |  | 17:58 | 19:51 | 1:53 | 132kV Budhipadar-Lapanga Feeder | At Lapanga end: Dist Protection, MAIN-1:- FAULT LOOP-B-E Zone-2 IL1-0.01KA IL2- 0.0KA IL3-4.0KA DIST-15.1KM FD=426ms AR NOT SUCCESSFUL B/U : NA REMOTE end: Zone 1 IL1-0.01KA IL2- 0.3KA IL3-0.53KA DIST=1.5KM At Budhipadar end: D/P-1(Siemens):-FL-Bph- E, Zone 1, FD-1.5KM, IL1-0.54KA, IL2-0.6KA, IL3-6.61KA
|  |  | 18:00 | 18:01 | 0:01 | 132kV Budhipadar-Kalunga Feeder | At Kalunga end: Earth Fault, D.P.RELAY- Micom p444- tripped ph-R-N, Zone 1, Fault duration- 59.84 ms, Relay trip time- 79.79 ms, Fault Distation- 66.83 km, Ir-1.258 kA, Iy- 24.50 A, Ib- 24.95 A, Fault resistance- 10.41 ohm (Auto reclosure- sucessful) At Budhipadar end: No tripping
|  |  | 18:00 | 19:00 | 1:00 | 132kV Budhipadar-Jharsuguda CKT-I | At Jharsuguda end: Earth Fault,Ir=0.00A, Iy=2.291A,Ib=5.976kA
44 | Bargarh New | 2025-04-22 | 13:18 | 14:50 | 1:32 | 220kV Bargarh New-Katapali Feeder | At Bargarh New end: M-I RELAY (Z-1, C- N,Dist;-23.8km) M-II RELAY(Z-1, C-N,F. Durat;-78.31ms, relay trip:-79.97ms, Dist;-27.9km & Ic;-2.267KA | Bargarh, ACC, Bhatli, Bargarh New, Barapalli, Dunguripali RTSS, Ghess, Thuapali | 0:22 | - | - | 0.070501 | - | -
|  |  |  | 13:54 | 0:36 | 160MVA AUTO TRF | DIFFERENTIAL TRIP
|  |  |  | 13:41 | 0:23 | 100MVA AUTO TRF | O/C & E/F RELAY(Ia:-0.46, Ib-0.45 & Ic:- 0.47)KA
|  |  |  | 13:56 | 0:38 | 132kV Katapali-Thuapali Feeder | At Katapali end: Over Current,Back up relay optd, O/C, Ir=0.90KA , Iy=0.92KA, Ib=0.94KA
|  |  |  | 14:46 | 1:28 | 220kV Bargarh New-Bolangir New Feeder | At Bolangir New end: Dist Protection,Zone Z1, Fault loop- B N, Fault Dist=41.63KM, Fault duration=73.31ms, Ia=16.81A, Ib=18.43A, Ic=3.457KA, Relay trip
45 | Angul | 2025-04-24 | 12:04 | 12:12 | 0:08 | 132kV Chainpal-Angul Feeder | At Angul end: Master Trip | Angul, MCL Boinda, Boinda RTSS Rairakhol, Rairakhol RTSS | 00:08 00:38 00:22 | - | - | 0.023997 | Tripped due to overloading. | -
|  |  |  | 12:40 | 0:36 | 132kV TTPS-Angul Feeder | At Angul end: Tripped on DP Relay,Fault Abs. Dist=7.203KM, Fault Loop -L3- L1,fault current IL1=1.636KA, IL3=1.385KA
|  |  |  | 12:51 | 0:47 | 132kV Rairakhol-Boinda Feeder | At Rairakhol end: Remote end Tripping,Incoming power supply to Boinda grid end failed due to Source failure at TTPS end.
46 | Anandapur | 2025-04-25 | 04:00 | 5:32 | 1:32 | 132kV Anandapur- Jajpur Road CKT-I | At Anandapur end: Y-N, Zone 4, Dist- 0.1km, Ib- 1.69kA At Jajpur Road end: No tripping | Anandapur Jajpur Road | 00:08 00:41 | - | - | 0.033083 | - | -
|  |  |  | 5:32 | 1:32 | 132kV Anandapur- Jajpur Road CKT-II | At Anandapur end: Y-N, Zone 4, Dist- 0.2km, Ib- 1.649kA At Jajpur Road end: No tripping
|  |  |  | 4:38 | 0:38 | 132kV Duburi-Jajpur Road CKT-II | At Duburi end: O/C, Ir- 0.16kA, Iy- 0.33kA, Ib- 1.67kA At Jajpur Road end: No tripping
|  |  |  | 4:39 | 0:39 | 132kV Duburi-Jajpur Road CKT-I | At Duburi end: O/C, Ir- 0.13kA, Iy- 0.33kA, Ib- 1.647kA At Jajpur Road end: No tripping
47 | Katapali | 2025-04-29 | 19:54 | 30.4.25 15:16 | 19:22 | 220kV Katapali-Bolangir PG Feeder | At Katapali end:Dist Protection,Main -II - DP optd in Zone 1 in R Phase ground Dist=9.805km, Ir=8.009KA , Iy=408.9A, Ib=145.2A, Fault duration=75.28ms rn | Katapali, Godbhaga RTSS Bargarh, Thuapali | 00:45 01:51 | - | - | 0.14486 | OPGW snapped at loc 28 to 29 | -
|  |  |  | 21:45 | 1:51 | 132kV Thuapali-Bargarh Feeder | At Thuapali end: E/F, Zone 1, Dist- 32.9km, Iy- 1.6kA At Bargarh end: E/F (Y-N), Zone 1, Dist- 0.17 Km, Iy- 3.11kA
|  |  | 21:06 | 21:58 | 0:52 | 132kV Katapali-Sambalpur Feeder | At Katapali end: B-N, Zone 4, Ib- 2.6kA, Dist- 18.37km At Sambalpur end: E/F (B-N), Zone 1, Dist- 7.22km, Ib- 1.933kA
48 | Meramundali | 2025-04-29 | 21:51 | 22:42 | 0:51 | 100MVA Auto TRF-I | Over Current,220kV Side - M/T 132kV Side - O/C, E/F, M/T Ib-4.305 KA, In-3.96 KA | BRG, RML-DSP, RML-FAD Dhenkanal, Khajuriakata, Joranda RTSS Khuntuni, Shree Cement Chainpal Talcher Fert. Ltd, Chainpal RTSS Kharagprasad, | 00:51 00:23 00:13 00:20 00:28 01:02 | - | - | 0.069786 | - | -
|  |  |  | 22:50 | 0:59 | 100MVA Auto TRF-III | Over Current,220kV Side-M/T 132kV Side - O/C, E/F, M/T Ib-4.117 kA, In- 4.078 kA
|  |  |  | 30.4.25 12:31 | 14:40 | 100MVA Auto TRF-II | Over Current,220kV Side- M/T 132kV Side - O/C, E/F, M/T Ib-4.299 kA, In-4.04
49 | Budhipadar | 2025-05-03 | 17:11 | 23:13 | 6:02 | 220kV Budhipadar-Korba CKT-I | At Budhipadar end: D/P I(MiCOM p444): Fault loop- A-N, Zone 1, Fault duration- 71.61ms, Dist- 1.777 Km, Ia- 26.39kA, Ib- 309.9A, Ic- 337A, Fault duration- 74.98ms D/P II(SIEMENS 7SA52): Rph-E, Zone 1, Dist- 6.1km,IL1- 23.59kA, IL2-250A,IL3- 320A At Korba end: Rph-E, Zone 2, Dist- 167.34km,IL1- 1.32kA, IL2-259A,IL3- 350A | - | - | - | - | - | Heavy Lightening and rainfall | -
|  |  | 17:11 | 17:46 | 0:35 | 220kV Bus Coupler | Schneider MiCOM p141- A-N, Duration- 70ms, RTT- 70ms, Ia- 15.28kA, Ib- 125A, Ic- 87.75A
|  |  | 17:11 | 17:58 | 0:47 | 220kV Budhipadar-IB CKT-III | Tripped from IB end only
50 | Mania | 2025-05-03 | 21:17 | 21:36 | 0:19 | 132kV Mania-ICCL Feeder | At Mania end: Remote End Tripping,INCOMER SUPPLY FAILED. | Mania, OCL Choudwar Choudwar RTSS | 00:19 00:20 00:18 | - | - | 0.021274 | Power availed from Kendrapada end through Salipur and OCL. | -
|  |  | 21:37 | 21:47 | 0:10 | 12.5MVA TRF-I, 20MVA TRF-II, 40MVA TRF-III | Over Excitation,V Over voltage (150.11kV)
|  |  | 21:17 | 23:00 | 1:43 | 132kV ICCL-Bahugram Feeder | At Bahugram end: Relay Not Operated
|  |  | 21:17 | 04.05.25 00:34 | 4:17 | 132kV Bidanasi-Choudwar Feeder | At Choudwar end: Distance Protection, Zone 1, dist 1.012km, Ir-1.274ka, Iy- 1.111kA, Ib-6.447kA At Bidanasi end: Zone 1, dist 10.91km, Ir- 1.1ka, Iy-5.31kA, Ib-1.28kA
51 | Baripada | 2025-05-11 | 19:52 | 20:43 | 0:51 | 132kV Baripada-Baripada PG Feeder | At Baripada end: Distance Protection, Y ph,started ph YN, Fault duratin=66.67ms,Relay trip time=0.00ms, Fault location= -352.3m, Ir=729.4A, Iy=5.061KA, Ib=306A, Van=78.41KV, Vbn=1.535KV, Vcn=80.32KV, Fault resistance= - 136.3ohm, Fault zone=Z4 At Baripada PG end: Distance relay operated,Zone-1, Y to ground, Distance=9.41KM, Iy=5.11KA | Baripada | 0:51 | - | - | 0.022326 | Power availed after Baripada-PGCIL line charged at 20:43Hrs on same date. | -
|  |  | 19:52 | 20:43 | 0:51 | 40 MVA TRF-I, TRF-II, TRF-III | Remote End Tripping,Source failure |  |  |  | - |  | At 20:43hrs 132kV BARIPADA-PGCIL Line was charged & P/S was restored at baripada GSS . | -
|  |  | 19:52 | 12.05.25 17:58 | 22:06 | 132kV Baripada-Betanati Feeder | At Baripada end: Remote End Tripping At Betanati end: Distance relay operated ,started ph=BN, Tripped phase=ABC, Distance trip=Z2, Fault duration= 66.68ms, Relay trip time= 80.00ms, Fault location: 20.89KM, Ia=195.5A, Ib= 1.086KA, Ic= 169.5A, Van= 64.3KV, Vbn=14.86KV, Vcn=63.40KV, fault resistance= 1.017ohm, Auto reclosure blocked. |  |  |  | - |  | After replacement of 132kV Y-Phase CT of the line bay at baripada grid end ,it was charged at 17:58hrs on dtd:12/05/2025 & it stood ok . | -
52 | Chainpal | 2025-05-26 | 16:28 | 16:51 | 0:23 | 132kV Chainpal-TTPS CKT-II | Tripped on over load from TTPS S/Y end | Chainpal TFL Talcher RTSS Angul MCL | 00:08 00:31 00:08 00:27 00:19 | - | - | 0.033557 | - | -
|  |  | 16:28 | 16:54 | 0:26 | 40MVA TRF-II | Source Failure
|  |  | 16:28 | 18:43 | 2:15 | 132kV Chainpal-Angul Feeder | Source Failure
|  |  | 16:28 | 16:59 | 0:31 | 132kV Chainpal-TFL Angul | Source Failure
|  |  | 16:28 | 17:09 | 0:41 | 40MVA TRF-III | Source Failure
|  |  | 16:28 | 18:40 | 2:12 | 132kV Meramundali-Chainpal CKT-I | Tripped on Zone-ii with fault distance 7.9Km | [5 empty] | bus fault in 132kV Bus of gss Meramundali
|  |  | 16:28 | 18:50 | 2:22 | 132kV Meramundali-Dhenkanal Feeder | At Dhenkanal end: Remote End Tripping, At Meramundali end: R-E,IR=1.47 KA,SOTF,Z1, | [5 empty] | 132kV Dhenkanal- Khajuriakata-Nuapatana T-Line was charged from Nuapatana end and incoming supply availed.
|  |  | 16:28 | 16:53 | 0:25 | 132kV Chainpal-Chainpal RTSS Feeder | Source Failure | [5 empty] | -
|  |  | 16:28 | 16:51 | 0:23 | 40MVA TRF-I | Source Failure
|  |  | 16:30 | 16:35 | 0:05 | 132kV Dhenkanal-Khuntuni Feeder | At Khuntuni end: Remote End Tripping | [5 empty] | Incoming supply failed from Meramundali GSS
53 | Paradeep | 2025-05-27 | 4:03 | 4:27 | 0:24 | 132kV Paradeep-Marshaghai | O/C RYB-ph , Ia- 1.2KA Ib = 857A Ic = 1.4KA | Olaver Rajnagar Pattamundai Kendrapara Marshaghai | 00:31 00:30 00:30 00:15 00:15 |  |  | 0.03166
|  |  | 4:03 | 4:23 | 0:20 | 132kV Paradeep-Kendrapara | O/C R-ph , Ia- 650A Ib = 775A Ic = 691A
|  |  | 4:04 | 4:33 | 0:29 | 132kV Olaver-Chandbali CKT-I | Source failure
|  |  | 4:04 | 4:33 | 0:29 | 132kV Olaver-Chandbali CKT-II | Source failure
|  |  | 4:04 | 6:19 | 2:15 | 132kV Dhamra-Chandbali CKT-I | At Chandbali end: Distance protection zone-1, phase-R,B, , fault location-370.5 MTRs, Ia=1.583KA, Ib=524.9A, Ic=3.687KA, fault resistance=1.864 Ohm At Dhamra end: Distance Protection,Zone-1,Fault Location- 16.62KM, Ia-1.586KA, Ib-506.3A,Ic- 1.764 KA, |  |  | - | - |  | - | -
|  |  | 4:04 | 6:21 | 2:17 | 132kV Dhamra-Chandbali CKT-II | At Chandbali end: Distance protection zone-1, phase-R,B , fault location-2.119 KMs, Ia=3.658KA, Ib=531.2A, Ic=1.767KA, fault resistance=633.9mOhm At Dhamra end: Distance Protection,Zone-1,Fault Location- 19.22KM, Ia-1.714KA, Ib-509.5A,Ic- 1.678KA
|  |  | 4:04 | 4:34 | 0:30 | 132kV Pattamundai-Rajnagar CKT-I | Source failure
|  |  | 4:04 | 4:34 | 0:30 | 132 kV Pattamundai-Rajnagar CKT-II | Source failure
54 | Podagada | 2025-05-27 | 07:15 | 7:28 | 0:13 | 132kV Podagada-Jayanagar Feeder | At Jayanagar end: Distance Protection,Z1,Y-G,DIST-20KM,If-1.5KA At Podagada end: Power Swing Block in announciation, Distance Protection Operated, Zone -1, distance= 19.8 KM , Pick up time 86 ms, trip time 15 ms, IL1=0.34 KA, IL2=0.23 KA, IL3=0.11 KA , Load= 30.61 MW | Podagada | 0:13 | - | - | 0.001313 | - | -
|  |  | 07:15 | 7:28 | 0:13 | 20MVA TRF-I Podagada | Interrupted due to tripping of Jayanagar Incomer supply at both end.
|  |  | 07:15 | 7:28 | 0:13 | 12.5MVA TRF-II | Interrupted due to tripping of Jayanagar Incomer supply at both end.
55 | Sambalpur | 2025-05-30 | 19:44 | 20:02 | 0:18 | 132kV Sambalpur-Katapali Feeder | At Sambalpur end: Tripped on Z1,T1, B- ph E/F, Ia=873A, Ib=225A,Ic=2036A, Ig=1465A,Fault dist.=9.72KM, fault duration=67.554 ms At Katapali end: tripped with B-ph E/F, Z1,Ib=4339A, F.D.= 14.65KM. | - | - | - | - | - | Transient fault | -
|  |  | 19:44 | 20:21 | 0:37 | 132kV Katapali-Burla PH Feeder | At Katapali end: Main DP optd in ZONE- 1 in R B Phase ground, distance=9km, Ir=5.663KA , Iy=85.9A, Ib=9.924KA, Fault duration=106.7ms | - | - | - | - | - | - | -
|  |  | 19:45 | 19:52 | 0:07 | 132kV Sambalpur-Burla PH Feeder | At Sambalpur end: No tripping At Burla PH end: Tripped at BPH end on Z1, R-B-ph,Fault impedance=0.02 ohms ,I nominal=0.54A | - | - | - | - | - | Transient fault due to heavy rain,wind & thunderstorm. | -
56 | Joda | 2025-05-31 | 12:06 | 12:21 | 0:15 | 220kV Telkoi-Joda Feeder | At Telkoi end: Distance Protection,NO Tripping from Telkoi end. DP Main-1 (i) Started phase ABCN, Tripped Element NO,over current start I > 3 (ii) Zone-2 , (iii) Distance =100.8 KM ,(iv) Ia= 230.4 A , Ib=1.576 KA , Ic= 1.353 KA (v) Van=129.3 KV, Vbn=91.28 KV, Vcn=85.60 KV At Joda end: (i) Started phase-ABCN ,Tripped phase ABC, Zone-4 (ii) Ia= 220.1 A , Ib= 1.581 KA , Ic= 1.377 KA (iii) Van=129.9 KV, Vbn=78.06 KV, Vcn=46.26 KV | Polasponga, OSISL, Kendujhargarh RTSS ESIL MSP, Barbil, Bolani, ARYA Steel, BRPL, IMTCPL, Karakolha Joda, Bansapani RTSS Tata Steel, TSLP FAP | 00:14 00:36 00:41 00:39 00:15 01:06 | - | - | 0.085516 | Power availed from TTPS end. | -
|  |  | 12:07 | 12:25 | 0:18 | 220kV Joda-Jindal Feeder | At Jindal end: DP Main-1,A/R lock out shot, Started Phase- ABCN, Tripped Phase-ABC,Zone-1 fault. Ia= 1.569KA, Ib= 1.694KA,Ic= 1.476K A, Van= 18.33KV,Vbn= 12.46KV,Vcn=19.24KV, Distance-9.698KM | [5 empty] | -
|  |  | 12:07 | 12:38 | 0:31 | 220kV Joda-Ramchandrapur | At Joda end: DP Main-1(Event-1), Started Phase- ABCN,Tripped Phase-ABC Zone-4 fault, Ia= 262.4A, Ib= 2.165KA, Ic= 2.255K A, Van= 130.3 KV,Vbn= 77.80KV, Vcn=46.70KV, DP Main- 1(Event-0), Started Phase- ABCN, Zone-4fault Ia= 2.173KA,Ib= 2.361KA, Ic= 2.255KA, Van= 11.66 KV, Vbn= 7.56KV At Ramachandrapur end: B/U O/C 86.1/86.2 Relay Operated R,Y&B Phase Tripped Fault current not displayed | [5 empty] | -
|  |  | 12:07 | 12:48 | 0:41 | 132kV Joda-Polasponga Feeder | At Polasponga end: Remote End Tripping,JODA GRID BLACK OUT | [5 empty] | 132 KARANJIA WITH RESTRICTED LOAD TO Kendujhargarh RTSS
|  |  | 12:07 | 12:48 | 0:41 | 132kV Bolani-Barbil Feeder | Incoming power supply from Joda GSS fail. | [5 empty] | -
|  |  | 12:07 | 12:48 | 0:41 | 132kV Bolani-Arya Feeder | Incoming power supply from Joda GSS fail. | [5 empty] | -
57 | Sunabeda | 2025-05-31 | 14:13 | 14:20 | 0:07 | 132kV Sunabeda-Jayanagar CKT-I | At Jayanagar end: Distance Protection,Z1,B-G,DIST-41.7KM,If- 2.34KA At Sunabeda end: B'ph to Gnd Fault current=2.5KA,Dist=41km,z-1. | Sunabeda Potangi HAL | 0:19 | - | - | 0.005435 | - | -
|  |  | 14:13 | 14:29 | 0:16 | 132kV Sunabeda-Jayanagar CKT-II | At Jayanagar end: Distance Protection,Z1,B-G,DIST-97KM,If-0.82KA At Sunabeda end: IR=108A,IY=195A, IB=820A, Z-1,Dist=97KM
|  |  | 14:13 | 14:30 | 0:17 | 132kV Sunabeda-Potangi Feeder | I/C P/S failed from Sunabeda end
|  |  | 14:13 | 14:32 | 0:19 | 132/33 kV TRF-II Sunabeda | Source Failure
|  |  | 14:13 | 14:33 | 0:20 | 132/33 kV TRF-I Sunabeda | Source Failure
58 | Jayanagar | 2025-06-05 | 10:00 | 10:24 | 0:24 | 132kV Transfer Bus Jayanagar | Ir-8.49KA,Iy-0.38KA,Ib-0.17KA | Jayanagar Jayanagar RTSS Borigumma, Nabarangpur, Tentulikhunti, Dabugaon, Umerkote Megalift | 00:08 00:26 00:27 00:32 | - | - | 0.033072 | - | -
|  |  |  | 10:31 | 0:31 | 132kV Tentulikhunti-Jayanagar Feeder | Z4,Ir-.56KA,Iy-.19KA,Ib-.07KA
|  |  |  | 10:24 | 0:24 | 132kV Dabugaon-Jayapatna Feeder | Tripped on O/C (R-Ph), Zone- 2,Distance=25.4KM
|  |  |  | 10:27 | 0:27 | 132kV Jayanagar-Borigumma Feeder | Source end failure
132kV Borigumma-Nabarangpur Feeder
132kV Tentulikhunti-Dabugaon Feeder
132kV Dabugaon-Jayapatna Feeder
132kV Tentulikhunti-Nabarangpur Feeder
132kV Tentulikhunti-Dabugaon Feeder
132kV Dabugaon-Umerkote Feeder
59 | Paradeep | 2025-06-06 | 16:57 | 17:08 | 0:11 | 132kV Paradeep-Kendrapada Feeder | Tripped on O/C on R,Y & B-Ph , Ir=1.2 kA,Iy= 1.3 kA, Ib = 1.1 kA | Pattamundai, Olaver, Rajnagar, Chandabali | 0:33 | - | - | 0.028208 | DUE TO OVERLOADING | -
|  |  |  | 17:30 | 0:33 | 132kV Olaver-Chandbali CKT-I | At Olaver end: Y-B, Zone 2, Dist- 11.3km, Iy- 1.7kA, Ib- 1.67kA At Chandabali end: Y-B, Zone 1, Dist- 2.73km, Iy- 3.87kA, Ib- 4.118kA
|  |  |  | 17:30 | 0:33 | 132kV Olaver-Chandbali CKT-II | At Olaver end: R-N, Zone 2, Dist- 7.1km, Ir- 4.04kA At Chandabali end: R-N, Zone 1, Dist- 1.512km, Ir- 4.04kA
60 | Meramundali | 2025-06-07 | 19:12 | 21:41 | 2:29 | 400kV Meramundali-Mendhasal CKT- II | Main CB tripped. TC-1 faulty. | Gondia | 1:09 | - | - | 0.008815 | - | -
|  |  |  | 08.06.25 07:09 | 11:57 | 132kV Kharagprasad-Meramundali CKT-II | At Kharagprasad end: Y-B, Iy - 13.58 kA, I B -13.69 kA, Z1, 0.33 KM At Meramundali end: Iy - 1.69 kA, Ib - 1.88 kA, Z2, 5.35 KM
|  |  |  | 20:21 | 1:09 | 132kV Gondia-TTPS Feeder | Tripped at Both end.
|  |  | 19:37 | 19:37 | 0:00 | 220kV Meramundali-Bhanjanagar Feeder | At Meramundali end: A/R successful, B- E, Ib - 3.92 kA, 36. 56 KM At Bhanjanagar end: A/R successful, B-E, IB - 942.3 A, 105.5 KM
|  |  | 19:37 | 19:37 | 0:00 | 220kV Meramundali-Narsinghpur Feeder | At Meramundali end: M1: B-N, Ib - 4.08 KA, Z1, 35.17 KM At Narsinghpur end: A/R successful, R-E, Ir - 1.39 kA, Z1, 112.9 KM
|  |  | 19:39 | 19:48 | 0:09 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end
|  |  | 19:45 | 20:09 | 0:24 | 132kV Goda-Kamakhyanagar Feeder | At Goda end: ZONE-1,IA-184.1A,IB- 40A,IC-1.33KA,DISTANCE-20.19KM At Kamakhyanagar end: ZONE-1,IA- 183A,IB-39.73A,IC-6.29KA,DISTANCE- 5.31KM
|  |  | 19:48 | 20:24 | 0:36 | 400kV Meramundali-Duburi New CKT I | At Duburi New end: A/R Successful, M1: L3-E, B-ph, IL3 - 5.41 KA, Z1, 49 KM At Meramundali end: B-N, Z1, 44.6 KM
|  |  | 19:50 | 20:48 | 0:58 | 132kV Gondia-JFAL Feeder | Tripped from JFAL end
61 | Rourkela | 2025-06-17 | 11:58 | 14:19 | 2:21 | 132kV Rourkela-Tarkera CKT-I | At Tarkera end: IL1=706.8A, IL2=646.8 A, IL3=669 A, IN=487.2 | Rourkela | 2:26 | - | - | 0.093319 | DUE TO BURNING AND BURSTING OF 40MVA TRANSFORMER NO. 2 33KV VCB. | -
|  |  |  | 14:21 | 2:23 | 132kV Rourkela-Tarkera CKT-II | At Tarkera end: IL1=1446.3 A, IL2=1286.7 A, IL3=1300 A
|  |  |  | 14:33 | 14:33 | 132kV Rourkela-Tarkera CKT-III | H/T
|  |  |  | 14:24 | 2:26 | 35MVA TRF-I | ACTIVE GROUP 1,IA=2.514KA,IL2=2.255KA,IL3=251.1A,I N MEASURED =0A,IN DERIVED=2.046KA
|  |  |  | 23.07.25 14:16 | 868:18 | 40MVA TRF-II | DC SUPPLY FAIL
|  |  |  | 14:28 | 2:30 | 35MVA TRF-III | IA=2.693KA,IB=2.248KA,IC=388.1KA,IN MEASURED=0A, IN DERIVED=1.804KA
|  |  |  | 14:22 | 2:24 | 40MVA TRF-IV | STARTED PHASE ABC N,TRIPPED PHASE AB, ACTIVE GROUP 1,IA=2.221KA,IB=2.060KA,IC=1.225KA,I N MEASURED=0A,IN DERIVED=243.7A