## ANNEXURE IV
99.9802 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2023-24
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) / ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) / (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Lapanga -IBTPS Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
3 | 400kV Lapanga -IBTPS Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.491 | 8760 | 100% | 0 | 429082.32
4 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
5 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
6 | 400kV Meramundali -Lapanga Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
7 | 400kV Meramundali -Lapanga Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
8 | 400kV Lapanga-Vedant Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
9 | 400kV Lapanga-Vedant Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
10 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
11 | 400kV Meramundali -Mendhasal Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
12 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
13 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.916 | 8760 | 100% | 0 | 664288.32
14 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 241.5 | 8760 | 100% | 0 | 4231080
1196.886
220KV LINES
15 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
16 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
17 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
18 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
19 | 220kV Pandiabil- Pratapsasan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.688 | 8760 | 100% | 0 | 268826.88
20 | 220kV Pandiabil- Pratapsasan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.688 | 8760 | 100% | 0 | 268826.88
21 | 220kV Balasore- Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 67.95 | 8760 | 100% | 0 | 595242
22 | 220kV Balimela-Jayanagar Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
24 | 220kV Balimela-Jayanagar Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
25 | 220kV Balimela-Jayanagar Ckt-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 93.46 | 8760 | 100% | 0 | 818709.6
26 | 220kV Balimela-Kalimela |  |  |  |  | 0.11597 | 2 | 47 | [7 empty] | 55.15 | 8760 | 99.97% | 153.5008 | 483114
|  | 2023-06-17 | 13:00 | 2023-06-17 | 15:47 | 0.11597 | 2 | 47 | [5 empty] | L/3,E/F =5.5 KA
27 | 220kV Kalimela-Malkangiri |  |  |  |  | 1900-01-02 11:15 | 14 | 52 | [7 empty] | 38.76 | 8760 | 99.83% | 576.232 | 339537.6
|  | 2023-06-17 | 13:47 | 2023-06-17 | 15:42 | 0.079861 | 1 | 52 | [5 empty] | Incomer failure
|  | 2023-07-21 | 08:33 | 2023-07-21 | 08:53 | 0.013889 | 0 | 20 | [5 empty] | DP, R-ph 0/c.
|  | 2023-08-18 | 3:59 | 2023-08-18 | 11:22 | 0.30764 | 0 | 14 | [5 empty] | Y-ph O/C,Distance Relay optd. Tripped due to fault occurred at 220kV Malkangiri- Kalimela ckt-1 feeder
|  | 2023-08-25 | 18:05 | 2023-08-25 | 18:15 | 0.0069444 | 0 | 7 | [5 empty] | R-ph O/C,Distance Relay optd. Tripped due to fault occurred at 220kV Malkangiri- Kalimela ckt-1 feeder
|  | 2023-10-01 | 10:51 | 04.10.23 | 12:18 | 1900-01-02 01:27 | 0 | 19 | [5 empty] | R ph, E/F, Zone 2, Ir-2.226kA. Tripped at Balimela end due to fault occurred at 220kV Malkangiri- Kalimela CKT I
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
28 | 220kV Balimela-Malkangiri Ckt - II |  |  |  |  | 0.11458 | 14 | 44 | [7 empty] | 22.41 | 8760 | 99.83% | 330.174 | 196311.6
|  | 2023-06-17 | 13:48 | 2023-06-17 | 15:37 | 0.075694 | 1 | 49 | [5 empty] | Incomer failure
|  | 2023-07-21 | 08:33 | 2023-07-21 | 08:53 | 0.013889 | 0 | 20 | [5 empty] | DP, R-ph 0/c.
|  | 2023-08-25 | 18:06 | 2023-08-25 | 18:13 | 0.0048611 | 0 | 7 | [5 empty] | At Balimela end:- O/C(R-ph), E/F, Ir=3.7KA, Iy=0.09kA, Ib=0.12kA. Tripped at Balimela end due to fault occurred at 220kV Malkangiri-Kalimela ckt-1 feeder
|  | 2023-10-01 | 10:51 | 2023-10-01 | 11:10 | 0.013194 | 0 | 19 | [5 empty] | No relay indication. Tripped at Balimela end due to fault occurred at 220kV Malkangiri- Kalimela CKT I
|  | 2023-10-23 | 05:35 | 2023-10-23 | 05:45 | 0.0069444 | 0 | 9 | [5 empty] | Tripped at Balimela end.. Balimela-Malkangiri CKT I already in OFF condition
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
29 | 220kV Balimela PH -Balimela |  |  |  |  | 0.11597 | 3 | 38 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 0.2 | 8760 | 99.96% | 0.72667 | 1752
|  | 2023-06-17 | 13:00 | 2023-06-17 | 15:47 | 0.11597 | 3 | 38 | [5 empty] | L/3,E/F =5.5 KA
30 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
31 | 220kV Barkote-Bonai |  |  |  |  | 0.044444 | 13 | 2 | [7 empty] | 55.807 | 8760 | 99.85% | 727.3512 | 488869.32
|  | 2023-04-24 | 21:33 | 2023-04-24 | 21:54 | 0.014583 | 0 | 21 | [5 empty] | At Barkote end:- start ph- AN, Trip ph- ABC, fault location- 43.98km, Zone-2, Ia- 1.688kA, Ib-73.79A, Ic- 102.6A, Van-52.41kV, Vbn- 440.8kV, Vcn-138.8V At Bonai end:- Fault type- AGT, Dist-44.40km, Zone-2, Ia-1700A, Ib- 75A, Ic-107A, In-1530A.
|  | 2023-09-08 | 15:23 | 2023-09-08 | 15:40 | 0.011806 | 0 | 17 | [5 empty] | At Barkote end:- Group-1, Start ph- AN, Trip ph- ABC, Trip Zone- 1, fault location- 21.20Km, Ia- 2.077KA, Ib- 45.61A, Ic- 105.8A, fault resistance- 10.49 ohm, Auto reclosed of breaker but did not stand, Start Ph- AN, Trippred ph- ABC, SOTF TOR- Trip, Fault location- 21.20Km, Ia- 2.077KA, Ib- 45.61A, Ic- 105.8A, Fault resistance- 10.49ohm, zone-I. LIGHTENING AND BAD WEATHER CONDITION
|  | 2023-04-10 | 11:43 | 2023-04-10 | 11:54 | 0.0076389 | 0 | 9 | [5 empty] | At Rengali-B/U Relay Operated Ia=59.2A Ib=159.9A Ic=744.7A In=584.07A Ig=592.53A.
|  | 2023-06-24 | 16:10 | 2023-06-24 | 16:25 | 0.010417 | 0 | 15 | [5 empty] | SUPPLY FAIL FROM BARKOTE END (LA BRUST AT DEOGARH RENGALI FDR). SUPPLY RESUME FRON TARKERA END
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
32 | 220kV Bonai-Tarkera |  |  |  |  | 0 | 0 | 0 | [7 empty] | 47.467 | 8760 | 100% | 0 | 415810.92
33 | 220kV Bonai-RTSS Bimlagarh |  |  |  |  | 0.026389 | 0 | 38 | [7 empty] | 20.218 | 8760 | 99.99% | 12.8047 | 177109.68
|  | 2023-04-24 | 21:33 | 2023-04-24 | 21:54 | 0.014583 | 0 | 21 | [5 empty] | At Barkote end:- start ph- AN, Trip ph- ABC, fault location- 43.98km, Zone-2, Ia- 1.688kA, Ib-73.79A, Ic- 102.6A, Van-52.41kV, Vbn- 440.8kV, Vcn-138.8V At Bonai end:- Fault type- AGT, Dist-44.40km, Zone-2, Ia-1700A, Ib- 75A, Ic-107A, In-1530A.
|  | 2023-09-08 | 15:23 | 2023-09-08 | 15:40 | 0.011806 | 0 | 17 | [5 empty] | At Barkote end:- Group-1, Start ph- AN, Trip ph- ABC, Trip Zone- 1, fault location- 21.20Km, Ia- 2.077KA, Ib- 45.61A, Ic- 105.8A, fault resistance- 10.49 ohm, Auto reclosed of breaker but did not stand, Start Ph- AN, Trippred ph- ABC, SOTF TOR- Trip, Fault location- 21.20Km, Ia- 2.077KA, Ib- 45.61A, Ic- 105.8A, Fault resistance- 10.49ohm, zone-I. LIGHTENING AND BAD WEATHER CONDITION
34 | 220kV Bhanjanagar-Narasinghpur |  |  |  |  | 0.024306 | 0 | 35 | [7 empty] | 87.17 | 8760 | 99.99% | 50.8492 | 763609.2
|  | 2023-04-16 | 21:20 | 2023-04-16 | 21:55 | 0.024306 | 0 | 35 | [5 empty] | LBB operated.
35 | 220kV Narasinghpur- Meramundali |  |  |  |  | 1899-12-31 00:55 | 1 | 6 | [7 empty] | 87.17 | 8760 | 99.99% | 95.887 | 763609.2
|  | 2023-04-16 | 20:49 | 2023-04-16 | 21:20 | 0.021528 | 0 | 31 | [5 empty] | At Meramundali-MAIN-1 : NOT OPERATED MAIN-2 : Y-E,IY=3.4 KA,DISTANCE : 46.2 KM,Z1 At Narasinghpur-LBB OPERATED. [Y-ph CT( 220 KV side) of 40 MVA Transformer failure occurred at N.pur end.].
|  | 2023-04-16 | 21:20 | 2023-04-17 | 21:44 | 1899-12-31 00:24 | 0 | 35 | [5 empty] | LBB operated[When 220 kV side of 40 MVA PT-1 was test charged it operated LBB. Tripped at both ends of Meramundali-Nspur Fdr-1 and only Local end of Nspur-Bhanjanagar end.].
36 | 220kV Bhanjanagar-Meramundali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
37 | 220kV Bhanjanagar-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
38 | 220kV Bhanjanagar-Nayagarh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 69 | 8760 | 100% | 0 | 604440
39 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
40 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
41 | 220kV Bidanasi -Godisahi |  |  |  |  | 0.13125 | 3 | 9 | [7 empty] | 4.32 | 8760 | 99.96% | 13.608 | 37843.2
|  | 2023-04-20 | 13:21 | 2023-04-20 | 16:30 | 0.13125 | 3 | 9 | [5 empty] | Tripped.
42 | 220kV Godisahi -Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.754 | 8760 | 100% | 0 | 94205.04
43 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.3 | 8760 | 100% | 0 | 81468
44 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.3 | 8760 | 100% | 0 | 81468
45 | 220kV Bisra PG-Tarkera Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
46 | 220kV Bisra PG-Tarkera Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
47 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0.052083 | 0 | 39 | [7 empty] | 20.507 | 8760 | 99.99% | 13.3296 | 179641.32
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 39 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
48 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0.082639 | 1 | 6 | [7 empty] | 20.507 | 8760 | 99.99% | 22.5577 | 179641.32
|  | 2023-10-06 | 16:16 | 2023-10-06 | 17:00 | 0.030556 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 39 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
49 | 220kV Budhipadar-Lephripada |  |  |  |  | 1899-12-31 01:51 | 18 | 36 | [7 empty] | 30.744 | 8760 | 99.79% | 571.8384 | 269317.44
|  | 2023-05-19 | 17:23 | 2023-05-19 | 18:16 | 0.036806 | 0 | 53 | [5 empty] | triped on D/P relay,FL=R ph-N,Zone-1,FD=12.68KM,fault current:- Ia=6.927KA,Ib=111.1A,Ic=140.3A AT remote end CB did not tripped.. Wheather=lightning and storm.
|  | 2023-08-10 | 0:25 | 2023-08-10 | 0:42 | 0.011806 | 0 | 17 | [5 empty] | At Budhipadar end:- D/P operated(make-ALSTOM,Micom P444): Yph - E fault, zone 2, fault location-36.2km, fault duration-384.7ms, IL1-82.3A, IL2-3.78kA, IL3-51.34A. 220kV y-Phase Bus Suspension String Insulator Bursted At Basundhara Grid End.
|  | 2023-12-29 | 13:47 | 2023-12-29 | 18:48 | 0.20903 | 5 | 1 | [5 empty] | At Budhipadar end: DP 1: Y-N, Zone 1, Iy- 28.66 kA; DP 2: Y-N, Zone 1, Dist 0.2 km, Iy- 32.80 kA. The fault is due to bursting of 220kV Budhipadar-Lephripada Y phase L.A at Budhipadar end.
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
50 | 220kV Lephripada-Basundhara |  |  |  |  | 1899-12-31 04:33 | 21 | 18 | [7 empty] | 15.2 | 8760 | 99.76% | 323.76 | 133152
|  | 2023-08-10 | 0:25 | 2023-08-10 | 4:40 | 0.17708 | 4 | 15 | [5 empty] | At Lephripada end:- Fault Loop- Y Ph to E, Zone-2, Dist-15.27km, Current in R, Y, B, N- IR-5.695A, IY-3.876kA, IB-7.304A, Fault duration -384.7ms, Fault Resistance- AR if Zone1 -NA, Make & type of Relay- D/P- II( MICOM P444). 220kV y-Phase Bus Suspension String Insulator Bursted At Basundhara Grid End, CB Didn't tripped at Basundhara end, The said feeder CB only charged from Lephripada end at 04:40 Hrs.The Feeder was charged after getting clearance from Basundhara end .
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
|  | 2023-07-20 | 09:44 | 2023-07-20 | 14:10 | 0.18472 | 4 | 26 | [5 empty] | At Lephripada end:- B/U Protection operated (Siemens Siprotec 7SJ66) R,Y,B-Phase O/C, Fault current- IR- 0.34kA, IY- 0.32kA, IC- 0.35kA. DC System Problem(Battery) at Basundhara end
|  | 2023-07-25 | 12:17 | 2023-07-25 | 12:29 | 0.0083333 | 0 | 12 | [5 empty] | At Lephripada end:- D/P opertaed, D/P-I (SIEMENS SIPROTEC 7SA52) Fault Loop- Yph-BpH, Zone-1,F.D- 10.3Kms, Fault Current- IR- 0.02KA, IY-6.08KA, IB-6,04KA, D/P-II( MICOM P444)Fault Loop Yphase-Bphase, Zone-1, F.D- 10.29 Kms, Fault Current IR- 0.2137KA, IY-6.055KA, IB-6.02KA. 33 KV KULDA Feeder at Basundhara end tripped on R,Y&B-Phase O/C Fault, this fault caused tripping of CB of 220 KV Lephripada-Basundhara Ckt CB at Lephripada end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
51 | 220kV Budhipadar-IbTPS Ckt-I |  |  |  |  | 0.011111 | 0 | 32 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.99% | 13.8667 | 227760
|  | 2023-07-29 | 19:14 | 2023-07-29 | 19:30 | 0.011111 | 0 | 32 | [5 empty] | At Budhipadar end:- D/P operated(make-SIEMENS 7SA52): B ph to E fault loop, Dist-13.2km, IL3-6.56kA At IBTPS end:- D/P operated:B-ph to E fault loop, Zone1, Dist- 22km, IL3-2.8kA. The feeder (Idle charged) tripped at Brajrajnagar end only. Weather: Heavy Lightning and rain weather-lightening and rain weather-lightening and rain (delay in charging due to CB spring charge problem and rain)
52 | 220kV Budhipadar-IbTPS Ckt-II |  |  |  |  | 0.58264 | 1 | 51 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.98% | 48.1 | 227760
|  | 2023-07-29 | 19:14 | 2023-07-30 | 8:37 | 0.55764 | 1 | 24 | [5 empty] | At Budhipadar end:- D/P operated (makeALSTOM Micom P444): B ph to E fault loop, Zone-1, Dist-13.17km, IL1=457.4A, IL2=177.5A, IL3-6.874kA, Fault Duration=101.8ms At IBTPS end:- D/P operated:B-ph to E fault loop, Zone1, Dist- 20km, IL3-3.0kA. The feeder (Idle charged) tripped at Brajrajnagar end only. Weather: Heavy Lightning and rain weather-lightening and rain weather-lightening and rain (delay in charging due to CB spring charge problem and rain)
|  | 2023-10-06 | 16:16 | 2023-10-06 | 16:52 | 0.025 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
53 | 220kV Budhipadar-IbTPS Ckt-III |  |  |  |  | 0.022917 | 1 | 6 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.99% | 27.918 | 222328.8
|  | 2023-07-29 | 19:20 | 2023-07-29 | 19:53 | 0.022917 | 1 | 6 | [5 empty] | At Budhipadar end:- D/P operated D/P-1 (make-SIEMENS 7SA52): R-ph to E fault loop, Zone 1, Dist-10.8km, IL1- 10.7kA, IL2- 0.95kA, IL3-0.28kA, D/P-2 (make-ALSTOM Micom P444) R-ph to E fault loop, Zone 1, Dist-11.39km, IL1- 10.67kA, IL2-963.9A, IL3- 315.3A, fault duration=73.35ms At IBTPS end:- D/P operated: R-ph to E fault loop, Zone1, Dist- 13.8km, IL3-5.7kA. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
54 | 220kV Budhipadar-IbTPS Ckt-IV |  |  |  |  | 0.026389 | 0 | 27 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.99% | 11.421 | 222328.8
|  | 2023-10-06 | 16:16 | 2023-10-06 | 16:54 | 0.026389 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
55 | 220kV Budhipadar-Raigarh Ckt-I |  |  |  |  | 0.41528 | 2 | 54 | [7 empty] | 60 | 8760 | 99.97% | 174 | 525600
|  | 2023-08-16 | 16:53 | 2023-08-16 | 18:32 | 0.06875 | 1 | 39 | [5 empty] | At Budhipadar end:- D/P I operated (Make-Siemens Siprotech 7SA52) F.L-L1-E, Dist-1.1Km, Zone 1, IL1-20.31Ka, IL2-0.67Ka, IL3-0.2 KA, DP-II Operated(make-ALSTOM,Micom P444):zone 1, fault location- 1.455km, fault duration-76.72ms, Il1-21.25kA, Il2-674.5A, Il3-219.2A. Auto Reclosure sucessful at B.padar end.
|  | 2024-03-09 | 14:05 | 2024-03-09 | 22:24 | 0.34653 | 1 | 15 | [5 empty] | Main1- B-N, Zone 1, Dist- 57.29km, Ib- 2.448kA, Main2- B-N, Zone 1, Ib- 2.57kA. Tripped due to B-phase conductor snapped at Loc no.144
56 | 220kV Budhipadar-Korba Ckt-II |  |  |  |  | 0.28472 | 15 | 24 | [7 empty] | 60 | 8760 | 99.82% | 924 | 525600
|  | 2023-10-06 | 16:16 | 2023-10-06 | 20:09 | 0.16181 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
|  | 2024-03-09 | 14:05 | 2024-03-09 | 15:41 | 0.066667 | 1 | 36 | [5 empty] | B-N. Tripped due to B-phase conductor snapped at Loc no.144
|  | 2024-03-18 | 19:15 | 2024-03-18 | 20:36 | 0.05625 | 1 | 21 | [5 empty] | tripped at Korba end only. Stormy weather, E/F, 86. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
57 | 220kV Budhipadar-Lapanga Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
58 | 220kV Budhipadar-Lapanga Ckt-II |  |  |  |  | 0.11389 | 1 | 17 | [7 empty] | 20 | 8760 | 99.99% | 25.6667 | 175200
|  | 2023-10-06 | 16:16 | 2023-10-06 | 18:10 | 0.079167 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
|  | 2024-03-09 | 13:45 | 2024-03-10 | 14:35 | 0.034722 | 0 | 50 | [5 empty] | At Budhipadar end: Main1- B-N, Zone 2, Dist- 15.25km, Ib- 10.62kA, Main2- B-N, Dist- 15.2km, Ib- 10.55kA At Lapanga end: Main1- B-N, Zone 1, Dist- 0.2km, Ib- 22.16kA, Main2- Y-N, Zone 1, Dist- 0.2km, Ib- 22.16kA, A/R unsuccessful, B/C relay- B Ph O/C. Tripped due to B Ph isolator string broken at gantry tower from Lapanga end. 220kV Budhipadar- Lapanga CKT I H/Ted at Budhipadar end only for load management.
59 | 220kV Budhipadar-SMC (Unit-II) Feeder Ckt-I |  |  |  |  | 0.052083 | 0 | 9 | [7 empty] | 13.424 | 8760 | 100% | 2.0136 | 117594.24
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 9 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
60 | 220kV Budhipadar-SMC (Unit-II) Feeder Ckt-II |  |  |  |  | 0.052083 | 0 | 9 | [7 empty] | 13.424 | 8760 | 100% | 2.0136 | 117594.24
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 9 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
61 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.92 | 8760 | 100% | 0 | 130699.2
62 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0.053472 | 0 | 27 | [7 empty] | 14.92 | 8760 | 99.99% | 6.714 | 130699.2
|  | 2023-10-06 | 16:16 | 2023-10-06 | 17:33 | 0.053472 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
63 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19 | 8760 | 100% | 0 | 166440
64 | 220kV Chandaka- Mendhasal ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
65 | 220kV Chandaka- Mendhasal ckt-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 372 | 100% | 0 | 7402.8
66 | 220kV Chandaka- Kantabada |  |  |  |  | 0.093056 | 0 | 14 | [7 empty] | 8.5 | 8388 | 100% | 1.9833 | 71298
|  | 2023-09-02 | 14:38 | 2023-09-02 | 16:52 | 0.093056 | 0 | 14 | [5 empty] | At Mendhasal end:- Ir=3.13KA, Iy=0.5KA, Ib=3.59KA, Dist=18.5, Zone-1 At Chandaka end:- Ir=3.91KA, Iy=0.5KA, Ib=4.15KA, Dist=2.7, zone-1. Tripped due to thunderstrom.
67 | 220kV Kantabada- Mendhasal |  |  |  |  | 0.093056 | 0 | 14 | [7 empty] | 12.8 | 8388 | 100% | 2.9867 | 107366.4
|  | 2023-09-02 | 14:38 | 2023-09-02 | 16:52 | 0.093056 | 0 | 14 | [5 empty] | At Mendhasal end:- Ir=3.13KA, Iy=0.5KA, Ib=3.59KA, Dist=18.5, Zone-1 At Chandaka end:- Ir=3.91KA, Iy=0.5KA, Ib=4.15KA, Dist=2.7, zone-1. Tripped due to thunderstrom.
68 | 220kV Chandaka- Chandaka (B) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.1 | 8760 | 100% | 0 | 876
69 | 220kV Chandaka (B)-Mendhasal |  |  |  |  | 0.08125 | 0 | 14 | [7 empty] | 18.96 | 8760 | 100% | 4.424 | 166089.6
|  | 2023-09-02 | 14:38 | 2023-09-02 | 16:35 | 0.08125 | 0 | 14 | [5 empty] | At Mendhasal end:- Ir=3.18kA, Iy=0.5kA, Ib=3.4kA, Dist=18.5km, Zone-1 At Chandaka B end:- Ir=4kA,Iy=0.5kA, Ib=3.8kA, Dist=4.7km, Zone-1. Tripped due to thunderstrom.
70 | 220kV Duburi-New Duburi Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
71 | 220kV Duburi-New Duburi Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.38 | 8760 | 100% | 0 | 55888.8
72 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
73 | 220kV Indravati PH-Therubali Ckt-I |  |  |  |  | 0.089583 | 1 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 99.99% | 112.06 | 755112
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:23 | 0.089583 | 1 | 18 | [5 empty] | DP Relay, IR = 32A, IY = 17A, IB = 17A Indravati end-Broken conductor indication, IR = 288A, IY = 522A, IB = 443A.. System Failure at Therubali Grid
74 | 220kV Indravati PH-Therubali Ckt-II |  |  |  |  | 0.090972 | 1 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 99.99% | 112.06 | 755112
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:25 | 0.090972 | 1 | 18 | [5 empty] | At Therubali-BCGT (Y-ph B-ph to ground), only backup relay, IR = 252A, IY = 1.1kA, IB = 1.05kA No tripping at Indravati end.. System Failure at Therubali Grid
75 | 220kV Indravati PH-Therubali Ckt-III |  |  |  |  | 0.088889 | 1 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 99.99% | 118.3 | 797160
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:22 | 0.088889 | 1 | 18 | [5 empty] | No Tripping at Therubali end Indravati end-Broken conductor indication, IR = 114.3A, IY = 449.6A, IB = 415.8A.. System Failure at Therubali Grid
76 | 220kV Indravati PH-Jayapatna |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.3 | 8760 | 100% | 0 | 169068
77 | 220kV Jayapatna-Kasipur |  |  |  |  | 0.044444 | 1 | 1 | [7 empty] | 39.5 | 8760 | 99.99% | 40.1583 | 346020
|  | 2024-03-09 | 06:25 | 2024-03-09 | 07:29 | 0.044444 | 1 | 1 | [5 empty] | At Jayapatna end: R-ph O/C, E/F, Zone-2, Ir- 1.949kA. PT burst at Kasipur end
78 | 220kV Kasipur-Therubali |  |  |  |  | 1900-01-01 04:05 | 5 | 1 | [7 empty] | 66.7 | 8760 | 99.94% | 334.6117 | 584292
|  | 2024-03-09 | 06:25 | 2024-03-09 | 07:30 | 0.045139 | 1 | 1 | [5 empty] | At Therubali end: R-N, Zone 3, Dist- 66.08km, Ir- 2.5kA At Kasipur end: R-N, Zone 4, Dist- 0.245km, Ir- 1.9kA. PT burst at Kasipur end
|  | 2023-12-28 | 12:32 | 30.12.23 | 15:32 | 1900-01-01 03:00 | 4 | 0 | [5 empty] | No tripping at Therubali end. At Muniguda end: B-N, Dist- 27.5 km, Zone 2, Ib- 0.913 kA. System out at Therubali end
79 | 220kV Jayanagar-Jeypore PG Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
80 | 220kV Jayanagar-Jeypore PG Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
81 | 220kV Jayanagar-Jeypore PG Ckt-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
82 | 220kV Jayanagar-Jeypore PG Ckt-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
83 | 220kV Jayanagar-Laxmipur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
84 | 220kV Jayanagar-Laxmipur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
85 | 220kV Jindal-Jamsedpur DVC |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.8 | 8760 | 100% | 0 | 182208
86 | 220kV Joda-RCPur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.5 | 8760 | 100% | 0 | 135780
87 | 220kV Joda-JSPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 21 | 8760 | 100% | 0 | 183960
88 | 220kV Joda-TSIL |  |  |  |  | 0.70764 | 16 | 59 | [7 empty] | 7.3 | 8760 | 99.81% | 123.9783 | 63948
|  | 2023-09-23 | 13:22 | 2023-09-23 | 14:06 | 0.030556 | 0 | 44 | [5 empty] | At Joda end:- B/U relay: E/F relay, Fault current: Ia=0.02kA, Ib=0.02kA, Ic=0.37kA. Tripped on B/U relay
|  | 2024-01-28 | 06:27 | 2024-01-28 | 22:42 | 0.67708 | 16 | 15 | [5 empty] | At Joda end: Main-1: Zone 1, Dist - 98.08 m, Ib- 8.464 kA; Main-2: Zone 1, B-N, Dist- 98.72 m, Ib- 7.825 kA Relay at TSIL end: No tripped. -
89 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
90 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
91 | 220kV Katapalli- Bargarh New |  |  |  |  | 0 | 0 | 0 | [7 empty] | 52.035 | 8760 | 99.81% | 0 | 455826.6
92 | 220kV Bargarh New- New Bolangir |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65.885 | 8760 | 100% | 0 | 577152.6
93 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 118.45 | 8760 | 100% | 0 | 1037622
94 | 220kV Bolangir PG- New Bolangir Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
95 | 220kV New Bolangir- Kesinga |  |  |  |  | 0.03125 | 0 | 45 | [7 empty] | 83.356 | 8760 | 99.99% | 62.517 | 730198.56
|  | 2023-09-25 | 17:34 | 2023-09-25 | 18:19 | 0.03125 | 0 | 45 | [5 empty] | At Kesinga end:- E/F,R-3.074 KA. E/F Lightning &heavy Rain
96 | 220kV Bolangir PG- Kesinga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 80.596 | 8760 | 100% | 0 | 706020.96
97 | 220kV Bolangir PG- New Bolangir Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.7 | 8760 | 100% | 0 | 23652
98 | 220kV Keonjhar PG - Keonjhar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
99 | 220kV Keonjhar PG - Keonjhar Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
100 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
101 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
102 | 220kV Lapanga-Katapali Ckt-I |  |  |  |  | 0.65486 | 0 | 42 | [7 empty] | 49.72 | 8760 | 99.99% | 34.804 | 435547.2
|  | 2023-07-29 | 19:24 | 1923-07-30 | 11:07 | 0.65486 | 0 | 42 | [5 empty] | At Lapanga end:- MAIN-1: Dist=13.7km, L1-L2-E, Power swing trip, Definite trip, Zone-1, MAIN-2: Dist=14.22km, Ir=8.10kA, Iy=7.9kA, Ib=0.3kA, Zone-1, B/U:- Rph-Yph, O/C, E/F At Katapali end:- MAIN-1: Dist=35.78km, Ir=2.4kA, Iy=2.3kA, Ib=0.016kA, Zone-1, MAIN-2: D=35.13km, Ir=2.4kA, Iy=2.4kA, Ib=0.00183kA, Zone-1. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
103 | 220kV Lapanga-Katapali Ckt-II |  |  |  |  | 0.88681 | 0 | 42 | [7 empty] | 49.72 | 8760 | 99.99% | 34.804 | 435547.2
|  | 2023-07-29 | 19:24 | 2023-07-30 | 16:41 | 0.88681 | 0 | 42 | [5 empty] | At Lapanga end:- MAIN-1: Dist=14.2km, Ir=7.94kA, Iy=7.5kA, Ib=0.3kA, Zone-1, MAIN-2:- Ir=8.0kA, Iy=7.8kA, Ib=0.3kA, Zone-1, B/U:- Rph-Yph, O/C At Katapali end:- MAIN-1: Dist=33.7km, Ir=2.3kA, Iy=0.325kA, Ib=0.001725kA, Zone-1. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
104 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0.20556 | 0 | 44 | [7 empty] | 59 | 8760 | 99.99% | 43.2667 | 516840
|  | 2023-05-15 | 11:13 | 2023-05-15 | 16:09 | 0.20556 | 0 | 20 | [5 empty] | At Laxmipur-O/C in Y&B-Ph,IY=1.7KA,IB=1.5KA, IN=1.8KA, At Therubali-Bph- N, Zone-4, 41.85km, IR = 13.34A, IY = 13.1A, IB =. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 2023-12-28 | 15:51 | 03:19 | 0 | 24 | [5 empty] | No tripping at Therubali end. At Laxmipur end: Y & B, Iy- 0.918 kA, Dist- 178.2 km. System out at Therubali end
105 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 1899-12-31 00:27 | 0 | 44 | [7 empty] | 59 | 8760 | 99.99% | 43.2667 | 516840
|  | 2023-05-15 | 11:13 | 15.05.23 | 07:57 | 0.86389 | 0 | 20 | [5 empty] | At Laxmipur-B-ph,Z-1,IB=2.8KA,IN=3.01KA,SOFT OPTD No tripping at Therubali end.. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:15 | 3:43 | 0 | 24 | [5 empty] | No tripping at Therubali end. At Laxmipur end: Y & B, Iy- 0.918 kA, Dist- 178.2 km. System out at Therubali end
106 | 220kV Laxmipur - Utkal Alumina (Aditya) ckt-I |  |  |  |  | 1899-12-31 05:18 | 0 | 24 | [7 empty] | 31.04 | 8760 | 100% | 12.416 | 271910.4
|  | 2023-12-28 | 12:33 | 29.12.23 | 17:51 | 1899-12-31 05:18 | 0 | 24 | [5 empty] | Master Relay. System out at Therubali end
107 | 220kV Laxmipur - Utkal Alumina (Aditya) ckt-II |  |  |  |  | 0.033333 | 0 | 24 | [7 empty] | 31.04 | 8760 | 100% | 12.416 | 271910.4
|  | 2023-12-28 | 12:33 | 2023-12-28 | 13:21 | 0:48 | 0 | 24 | [5 empty] | Master Relay. System out at Therubali end
108 | 220kV Laxmipur - NALCO ckt-I |  |  |  |  | 0.013889 | 0 | 20 | [7 empty] | 36.99 | 8760 | 100% | 12.33 | 324032.4
|  | 2023-12-28 | 12:33 | 2023-12-28 | 12:53 | 0:20 | 0 | 20 | [5 empty] | Master Relay. System out at Therubali end
109 | 220kV Laxmipur - NALCO ckt-II |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 36.99 | 8760 | 100% | 12.9465 | 324032.4
|  | 2023-12-28 | 12:33 | 2023-12-28 | 12:54 | 0:21 | 0 | 21 | [5 empty] | Master Relay. System out at Therubali end
110 | 220kV Laxmipur - Laxmipur RTSS |  |  |  |  | 0.030556 | 0 | 44 | [7 empty] | 2.45 | 8760 | 99.99% | 1.7967 | 21462
|  | 2023-05-15 | 11:13 | 2023-05-15 | 11:33 | 0.013889 | 0 | 20 | [5 empty] | PSB Fail i.e Under Voltage. System Failure at Therubali Grid
|  | 2023-12-28 | 12:33 | 2023-12-28 | 12:57 | 0:24 | 0 | 24 | [5 empty] | Master Relay. System out at Therubali end
111 | 220kV Meramundali-Bhusan (Tata BSL) Ckt-I |  |  |  |  | 0.20625 | 4 | 57 | [7 empty] | 2.4 | 8760 | 99.94% | 11.88 | 21024
|  | 2023-09-24 | 06:18 | 2023-09-24 | 11:15 | 0.20625 | 4 | 57 | [5 empty] | At Meramundali end:- IR= 23.20kA, IY= 1.13kA, IB= 1.36kA, Dist-0.5km At TATA end:- Diffential relay : R-E, IR= 9.6kA. Earth wire snapped between loc 4 of 132 KV MRDL-K.Prasad DC line and loc 6a of 220 KV MRDL-TATA DC line. The snapped EW lay over 220 KV MRDL-TATA 1
112 | 220kV Meramundali-Bhusan (Tata BSL) Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
113 | 220kV Meramundali-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 95.556 | 8760 | 100% | 0 | 837070.56
114 | 220kV Meramundali-Meramundali(B)-Duburi 'T' Connection |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.658 | 8760 | 100% | 0 | 5764.08
115 | 220kV Meramundali-Goda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 70.97 | 8760 | 100% | 0 | 621697.2
116 | 220kV Goda-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.69 | 8760 | 100% | 0 | 321404.4
117 | 220kV Meramundali-Meramundali(B)-Goda 'T' Connection |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.658 | 8760 | 100% | 0 | 5764.08
118 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
119 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
120 | 220kV Narendrapur-Atri Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
121 | 220kV Atri-Mendhasal Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.85 | 8760 | 100% | 0 | 217686
122 | 220kV Narendrapur-Atri Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
123 | 220kV Narendrapur-Tata Gopalpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.1 | 8760 | 100% | 0 | 70956
124 | 220kV Narendrapur-Tata Gopalpur Ckt-II |  |  |  |  | 0.028472 | 0 | 41 | [7 empty] | 8.1 | 8760 | 99.99% | 5.535 | 70956
|  | 2023-06-16 | 10:47 | 2023-06-16 | 11:15 | 0.019444 | 0 | 28 | [5 empty] | Tripped on M/R operated. Over Fluxing
|  | 2024-03-14 | 23:32 | 2024-03-14 | 23:45 | 0.0090278 | 0 | 13 | [5 empty] | R-N, Zone 1, Dist- 0.239km, Ir- 6.23kA. 220kV Narendrapur-TATA CKT I is under shutdown.
125 | 220kV Atri-Infocity-II Ckt-II |  |  |  |  | 0.025694 | 0 | 37 | [7 empty] | 21.3 | 8760 | 99.99% | 13.135 | 186588
|  | 2023-06-16 | 10:50 | 2023-06-16 | 11:27 | 0.025694 | 0 | 37 | [5 empty] | Tripped due to fault at atri grid end resulted in general trip & o/v at our CB end.. 220kv system failure due to fault at atri grid end resulted in general trip & o/v at our CB end.hence CB was charged after
126 | 220kV Infocity-II-Mendhasal |  |  |  |  | 1899-12-31 21:31 | 0 | 51 | [7 empty] | 5.47 | 8760 | 99.99% | 4.6495 | 47917.2
|  | 2023-06-16 | 10:50 | 18.06.23 | 6:34 | 1899-12-31 19:44 | 0 | 37 | [5 empty] | Tripped due to fault at atri grid end resulted in general trip & o/v at our CB end.. 220kv system failure due to fault at atri grid end resulted in general trip & o/v at our CB end.hence CB was charged after
|  | 2023-09-02 | 14:39 | 2023-09-02 | 16:26 | 0.074306 | 0 | 14 | [5 empty] | Tripped on O/C DP main-1 21.1:- Zone-3 Dist: 54.4Km, DP main 2 21.2:- Zone-3, dist: 46.14Km IR=1.461KA, IY=406.3 & IB=1.613KA but the line tripped only at infocity-II end.. Tripped due to thunderstrom.
127 | 220kV New Duburi -Balasore |  |  |  |  | 0 | 0 | 0 | [7 empty] | 140.97 | 300 | 100% | 0 | 42291
128 | 220kV New Duburi -Dhamara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 125.881 | 8460 | 100% | 0 | 1064953.26
129 | 220kV Dhamara -Balasore |  |  |  |  | 0 | 0 | 0 | [7 empty] | 85.995 | 8460 | 100% | 0 | 727517.7
130 | 220kV New Duburi -Bhadrak |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.798 | 8760 | 100% | 0 | 646470.48
131 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0.032639 | 0 | 47 | [7 empty] | 113.433 | 8760 | 99.99% | 88.8559 | 993673.08
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:25 | 0.018056 | 0 | 26 | [5 empty] | At Paradeep end: Zone 3, Ir- 1.52kA, Iy-1.56 kA, Ib- 1.53 kA, Dist 158.3 km from Duburi end New Duburi end: R-Y-B, Zone-3/4, Ir- 1.52 kA, Iy- 1.56 kA, Ib- 1.53 kA, Dist- 158.3 km. 132kV Y Ph Main Bus-I PPT Feeder jumper snapped
132 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0.036806 | 0 | 26 | [7 empty] | 113.433 | 8760 | 100% | 49.1543 | 993673.08
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 26 | [5 empty] | Zone 3/4, Ir- 1.50 kA, Iy- 1.57 kA, Ib- 1.55 kA, Dist- 158.5 km.
133 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0.074306 | 1 | 47 | [7 empty] | 6 | 8760 | 99.98% | 10.7 | 52560
|  | 2023-05-26 | 02:39 | 2023-05-26 | 04:05 | 0.059722 | 1 | 26 | [5 empty] | O/C ,R Y B- PH ,C-G,Z1,IA-577.6A,IB-608A,IC-5.86KA.
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
134 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 8.868 | 8760 | 100% | 3.1038 | 77683.68
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
135 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 8.868 | 8760 | 100% | 3.1038 | 77683.68
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
136 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 71.337 | 8760 | 100% | 0 | 624912.12
137 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 0.029167 | 0 | 7 | [7 empty] | 0.4 | 8760 | 100% | 0.046667 | 3504
|  | 2023-10-07 | 18:43 | 2023-10-07 | 19:25 | 0.029167 | 0 | 7 | [5 empty] | Ir- 0.297 kA, Iy- 0.118 kA, Ib- 0.105 kA. -
138 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.4 | 8760 | 100% | 0 | 3504
139 | 220kV Rengali GD-Chandiposh (T)-Tarkera - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 162.08 | 8760 | 100% | 0 | 1419820.8
140 | 220kV Rengali GD-Deogarh |  |  |  |  | 1899-12-31 00:21 | 0 | 26 | [7 empty] | 54.8 | 8760 | 100% | 23.7467 | 480048
|  | 2023-04-10 | 11:43 | 2023-04-10 | 11:54 | 0.0076389 | 0 | 11 | [5 empty] | At Rengali-B/U Relay Operated Ia=59.2A Ib=159.9A Ic=744.7A In=584.07A Ig=592.53A.
|  | 2023-06-24 | 16:07 | 25.06.23 | 16:17 | 1899-12-31 00:10 | 0 | 15 | [5 empty] | DP Relay Operated, Dist-45.75km, Zone-II, Tripped phase: ABC, IA=3.368kA, IB=52.80A, IC=141.2A. 220kV R-ph LA burst at Deogarh Grid end. Weather condition heavy thunderstorm.
141 | 220kV Deogarh-Barkote |  |  |  |  | 1899-12-31 00:21 | 0 | 26 | [7 empty] | 23.2 | 8760 | 100% | 10.0533 | 203232
|  | 2023-04-10 | 11:43 | 2023-04-10 | 11:54 | 0.0076389 | 0 | 11 | [5 empty] | At Rengali-B/U Relay Operated Ia=59.2A Ib=159.9A Ic=744.7A In=584.07A Ig=592.53A.
|  | 2023-06-24 | 16:07 | 25.06.23 | 16:17 | 1899-12-31 00:10 | 0 | 15 | [5 empty] | DP Relay Operated, Dist-45.75km, Zone-II, Tripped phase: ABC, IA=3.368kA, IB=52.80A, IC=141.2A. 220kV R-ph LA burst at Deogarh Grid end. Weather condition heavy thunderstorm.
142 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
143 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
144 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 29.5 | 8760 | 100% | 0 | 258420
145 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 34.5 | 8760 | 100% | 0 | 302220
146 | 220kV STPS (Kaniha)-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
147 | 220kV STPS (Kaniha)-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
148 | 220kV Tarkera-Kuarnmunda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.47 | 8760 | 100% | 0 | 266917.2
149 | 220kV Kuarnmunda-Budhipadar |  |  |  |  | 0.033333 | 0 | 48 | [7 empty] | 111.4 | 8760 | 99.99% | 89.12 | 975864
|  | 2023-12-29 | 13:47 | 2023-12-29 | 14:35 | 0.033333 | 0 | 48 | [5 empty] | At Kuarmunda end: Y-N, Zone 2, Dist- 119.1 km, Iy- 1.399 kA No tripping at Budhipadar end. The fault is due to bursting of 220kV Budhipadar-Lephripada Y phase L.A at Budhipadar end.
150 | 220kV Tarkera-Bamra |  |  |  |  | 0.21458 | 0 | 44 | [7 empty] | 70.2 | 8760 | 99.99% | 51.48 | 614952
|  | 2023-08-30 | 17:54 | 2023-08-30 | 22:36 | 0.19583 | 0 | 17 | [5 empty] | At Budhipadar end:- D/P 1(MICOM P444):Y ph-E, Zone 2, Fault dist- 83.37km, D/P 2(SIEMENS ): Y ph-E, Zone 2, Fault Dist-84.4km(164%), IL2- 2.17kA At Bamra end:- CB did not trip. Fault in 220kV Bamra - Tarkera feeder
|  | 2023-10-06 | 16:16 | 2023-10-06 | 16:43 | 0.01875 | 0 | 27 | [5 empty] | At Tarkera end: DP1: Zone 1, B-N, Dist- 6.27 km, Ib-10.617 kA, DP2 : Zone 1, B-N, Dist-6.429 km, Ib-10.67 kA At Bamra end: DP2:- LOOP:- F-T-C-G, Zone 1, Dist:- 28.6 km, Ib-0.588kA. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
151 | 220kV Bamra-Budhipadar |  |  |  |  | 0.87361 | 13 | 9 | [7 empty] | 51.5 | 8760 | 99.85% | 677.225 | 451140
|  | 2023-08-30 | 17:56 | 2023-08-30 | 18:13 | 0.011806 | 0 | 17 | [5 empty] | At Budhipadar end:- D/P 1(MICOM P444):Y ph-E, Zone 2, Fault dist- 83.37km, D/P 2(SIEMENS ): Y ph-E, Zone 2, Fault Dist-84.4km(164%), IL2- 2.17kA At Bamra end:- CB did not trip. Fault in 220kV Bamra - Tarkera feeder
|  | 2023-10-06 | 16:16 | 2023-10-06 | 17:17 | 0.042361 | 0 | 27 | [5 empty] | At Budhipadar end: B-N, Dist- 104.3 km, Ib- 1.73 kA, Zone 3 CB did not trip at Bamra end.. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
152 | 220kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
153 | 220kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
154 | 220kV Tarkera-RSP-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
155 | 220kV Tarkera-RSP-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
156 | 220kV Therubali-Gunupur |  |  |  |  | 1900-01-01 00:29 | 16 | 15 | [7 empty] | 71.911 | 8760 | 99.81% | 1168.5538 | 629940.36
|  | 2023-05-31 | 20:08 | 01.06.23 | 18:55 | 0.94931 | 2 | 18 | [5 empty] | At Therubali end:- BGT(Y-ph), Z-2, Location-60.83 km, Iy- 2.3 kA At Gunupur end:- Busbar relay (LBB)operated. All 3-phs Conductors snap from beam mounted isolators at Gunupur due to heavy wind and rain .Grid blackout. Gunupur availed supply from Akhusingh.
|  | 2024-01-11 | 14:46 | 12.01.24 | 8:33 | 0.74097 | 0 | 11 | [5 empty] | Tripped on Over voltage. -
|  | 2024-03-20 | 05:35 | 2024-03-20 | 08:15 | 0.11111 | 0 | 37 | [5 empty] | At Therubali end: B-N, Zone 1, Dist- 44.43km, Ib- 3.135kA At Gunupur end: B-N, Dist- 15.77km, Ib- 1.73kA. -
|  | 2023-05-15 | 11:14 | 2023-05-15 | 12:48 | 0.065278 | 0 | 39 | [5 empty] | At Therubali-BCGT (Y-ph B-ph to ground), only backup relay, IR =. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:13 | 3:41 | 0 | 30 | [5 empty] | No tripping at Therubali end. At Bhanjanagar end: B-N, Zone 3, Dist- 284 km, Ir- 0.148 kA, Iy- 0.233 kA, Ib- 0.703 kA. System out at Therubali end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
157 | 220kV Gunupur-Narendrapur |  |  |  |  | 1899-12-31 00:17 | 15 | 45 | [7 empty] | 149.669 | 8760 | 99.82% | 2357.2868 | 1311100.44
|  | 2023-05-31 | 20:08 | 01.06.23 | 18:58 | 0.95139 | 2 | 18 | [5 empty] | At Therubali end:- BGT(Y-ph), Z-2, Location-60.83 km, Iy- 2.3 kA At Gunupur end:- Busbar relay (LBB)operated. All 3-phs Conductors snap from beam mounted isolators at Gunupur due to heavy wind and rain .Grid blackout. Gunupur availed supply from Akhusingh.
|  | 2024-03-20 | 05:35 | 2024-03-20 | 06:10 | 0.024306 | 0 | 35 | [5 empty] | Bus-bar trip(96). -
|  | 2023-10-02 | 16:31 | 2023-10-02 | 17:23 | 0.036111 | 0 | 52 | [5 empty] | Main 1: R-Y-B, Zone 2, A/R Distk out , Dist- 131.7 km, Ir- 64.94 A, Iy- 1.659 kA, Ib- 1.536 kA Main 2: B-N, Zone 2, Dist- 131.84 km ,Iy- 1.756 kA, Ib- 1.622 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
158 | 220kV Therubali-Narendrapur |  |  |  |  | 0.24306 | 1 | 14 | [7 empty] | 196 | 8268 | 99.99% | 241.7333 | 1620528
|  | 2023-06-16 | 10:43 | 2023-06-16 | 10:48 | 0.0034722 | 0 | 5 | [5 empty] | At Therubali end:- L1-L2, Z-1, -1KM, IL1=674.69A, IL2=777.32A, IL3=1286.69A At Narendrapur end:- No tripping. Over Fluxing
|  | 2023-05-15 | 11:14 | 2023-05-15 | 12:39 | 0.059028 | 0 | 39 | [5 empty] | At Therubali-BCGT (Y-ph B-ph to ground), only backup relay, IR =. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:52 | 4:20 | 0 | 30 | [5 empty] | No tripping at Therubali end. At Narendrapur end: R-Y-B, Dist- 457.4 km, Zone 3, Ir- 0.196 kA, Iy- 0.158 kA, Ib- 0.441 kA. System out at Therubali end
159 | 220kV Therubali-Aska New |  |  |  |  | 0 | 0 | 0 | [7 empty] | 206.7 | 492 | 100% | 0 | 101696.4
160 | 220kV Aska New-Narendrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.48 | 492 | 100% | 0 | 36152.16
161 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0.21597 | 14 | 18 | [7 empty] | 171.46 | 8760 | 99.84% | 2451.878 | 1501989.6
|  | 2023-05-15 | 11:15 | 2023-05-15 | 11:51 | 0.025 | 0 | 36 | [5 empty] | Tripped At BNJR END - BC, Z-3, D=250.7 KM, IB=520.8 A,IC=525.9 A. Did not Tripped At other End. System Failure at Therubali Grid
|  | 2023-05-15 | 12:20 | 2023-05-15 | 13:32 | 0.05 | 1 | 12 | [5 empty] | At Therubali-Rph Yph fault, Zone-I, 128.9 km, IR = 977.3A, IY =. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 2023-12-28 | 15:55 | 3:23 | 0 | 30 | [5 empty] | No tripping at Therubali end. At Bhanjanagar end: B-N, Zone 3, Dist- 284 km, Ir- 0.148 kA, Iy- 0.233 kA, Ib- 0.703 kA. System out at Therubali end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
162 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0.031944 | 0 | 39 | [7 empty] | 171.46 | 8760 | 99.99% | 111.449 | 1501989.6
|  | 2023-05-15 | 11:14 | 2023-05-15 | 12:00 | 0.031944 | 0 | 39 | [5 empty] | No Tripping at Therubali end Bhanjanagar end-Rph Yph- N fault, A/R lockout, AR block, Zone- III, 250.7Km, IR = 40A, IY = 520A, IB = 525.9A. System Failure at Therubali Grid
163 | 220kV Bhanjanagar- Aska New - I |  |  |  |  | 0.035417 | 0 | 47 | [7 empty] | 28.6 | 8760 | 99.99% | 22.4033 | 250536
|  | 2023-09-05 | 14:24 | 2023-09-05 | 15:15 | 0.035417 | 0 | 47 | [5 empty] | At Bhanjanagar end:- E/F, IA=1.328kA, IB=93.67A, IC=315.4A.
164 | 220kV Bhanjanagar- Aska New - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.6 | 8760 | 100% | 0 | 250536
165 | 220kV TTPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
166 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
167 | 220kV TTPS- Telkoi |  |  |  |  | 0.034722 | 1 | 9 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 78.769 | 8760 | 99.99% | 90.5844 | 690016.44
|  | 2023-06-17 | 13:45 | 2023-06-17 | 14:11 | 0.018056 | 0 | 52 | [5 empty] | Tripped on distance protection from TTPS end while CB of said feeder was in closed condition at Telkoi end. DP relay indication at TTPS end:- (1)Zone-2 (2) IA=23.79A, IB=929.1A, IC=592.8A (3) Fault location- 116.8KM. Pick up data of Main-I DP relay at Telkoi end:-(1) Started phase B C (2) Overcurrent Start I >3 (4) Tripped Elts No (5)IA=118A, IB=1.783KA, IC=2.351KA (6) Fault in zone None.
|  | 2023-06-12 | 12:50 | 2023-06-12 | 13:14 | 0.016667 | 0 | 17 | [5 empty] | Tripped on distance protection from TTPS end while CB of said feeder was in closed condition at Telkoi end. DP relay indication at TTPS end:- (1) IA=27.49A, IB=48.19A, IC=0A No relay indication observed for above said fault at Telkoi end:-.
168 | 220kV Telkoi- Joda |  |  |  |  | 0.080556 | 1 | 43 | [7 empty] | 103.227 | 8760 | 99.98% | 177.2064 | 904268.52
|  | 2023-04-24 | 06:05 | 2023-04-24 | 07:05 | 0.041667 | 1 | 0 | [5 empty] | Tripped at both Joda,Telkoi,TTPS end with following relay indication Relay at Joda end: Relay Details For 220KV JODA-TELKOI-TTPS Ckt-I fdr:- Fault Details at Joda end(DP-I) DP Relay Tripped Tripped PH- ABC Zone-I Fault Dist-61.15KM Fault Current:- IA-1.27KA, IB-143.6A, IC-2.72KA Fault Details at Joda end(DP-II) DP Relay Tripped Tripped PH- CAT Zone-I Fault Dist-79.98KM Fault Current:- IA-1.189KA, IB-105A, IC-2.67KA, IN-2.041KA Fault Details of Telkoi-Joda relay at Telkoi end (Telkoi-TTPS relay not tripped) end:- DP Relay Tripped Tripped PH – ABC Zone-I Fault Dist- 49.95KM Fault Current:- IA-1.74KA, IB-93.5A, IC-2.372KA Fault Details at TTPS end:- DP Relay Tripped Zone-II Dist-126.7KM Fault Current:- IA-442.5A, IB-33.94A, IC-855.8A. At 07:20Hrs 220KV Telkoi- TTPS fdr. charged at both Telkoi & TTPS end.
|  | 2023-06-17 | 13:45 | 2023-06-17 | 14:24 | 0.027083 | 0 | 26 | [5 empty] | Tripped at both end with following relay indication At Joda end:-DP Relay(Main-I): Zone-1, Dist=44.15KM, Fault Current: Ia=116.2A, Ib=1.776KA, Ic=3.162KA, VAN=128.3KV, VBN=130.0KV, VCN=103.3KV, DP Relay(Main-II): Zone-1, BCT, FD=56.09KM, Fault Current: A=113A, B=1775A, C=3049A, N=1730A, G=1729A AT Telkoi end: DP relay, Zone-I, Fault Dist=41.09KM, Fault current: Ia=79.95A, Ib=1.801kA, Ic=2.367KA.
|  | 2023-06-12 | 12:50 | 2023-06-12 | 13:07 | 0.011806 | 0 | 17 | [5 empty] | Tripped at both end with following relay indication At Joda end:-DP, Relay(Main-I): Zone-1, Dist=50.78km, SOTF trip, Fault Current: Ia=37.56A, Ib=39.74A, Ic=1.918kA, VAN=128.3kV, VBN=130.0kV, VCN=103.3kV, DP Relay(Main-II): Zone-1, CG, FD=45.46km, Fault Current: A=148A, B=131A, C=1844A, N=1907A, G=1908A At Telkoi end:- DP relay, Zone-I, Fault Dist=51.22km, Fault current: Ia=190.2A, Ib=264.1A, Ic=1.124kA.
169 | 220kV TTPS-Joda |  |  |  |  | 0.071528 | 15 | 16 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.83% | 2351.0667 | 1349040
|  | 2023-04-24 | 06:05 | 2023-04-24 | 6:59 | 0.0375 | 1 | 48 | [5 empty] | 220KV Joda-TTPS CKT-II fdr. tripped at both Joda & TTPS end. Fault Details at Joda end(DP-I) DP Relay Tripped Tripped PH- A Zone-I Fault Dist-61.09KM Fault Current:- IA-1.23KA, IB-166.9A, IC-887.1KA Fault Details at Joda end(DP-II) DP Relay Tripped Tripped PH- AGT Zone-I Fault Dist-45.58KM Fault Current:- IA-1.248KA, IB-164A, IC-908KA, IN-2.135KA Fault Details of TTP-II end:- Relay Details Not showing at TTPS end. At 07:20Hrs 220KV Telkoi- TTPS fdr. charged at both Telkoi & TTPS end.
|  | 2023-06-17 | 13:45 | 2023-06-17 | 14:16 | 0.021528 | 0 | 52 | [5 empty] | Tripped at both end but A/R success at Joda end with following relay indication At Joda end:- DP Relay(Main-I): Zone-1, A/R Success, Dist.=47.70km, Fault Current: Ia=152.8A, Ib=1.411kA, Ic=795A,VAN=127.7kV, VBN=152.8kV, VCN=77.47kV, DP Relay(Main-II): A/R Success, Zone-1, BGT, FD=37.29km, Fault Current: A=149A, B=1382A, C=750A, N=2183A, G=2182A At TTPS end:- DP relay, Zone-I, Fault Dist=79.52km, Fault current: Ia=112.7A, Ib=2.240kA, Ic=752.1A.
|  | 2023-06-03 | 14:12 | 2023-06-03 | 14:30 | 0.0125 | 0 | 36 | [5 empty] | Tripped at both end but A/R success at Joda end with following relay indication At Joda end:- DP Relay(Main-I): Zone-1, A/R Success, Dist- 50.48km, Fault Current: Ia=93.59A, Ib=239.6A, Ic=2.178kA, VAN=129.9kV, VBN=130.5kV, VCN=85.14kV, DP Relay(Main-II): Zone-1, CGT, FD=47.07km, Fault Current: A=97A, B=248A, C=2298A, N=2614A, G=2614A At TTPS end:- DP relay, Zone-I, Fault Dist=91.59km, Fault current: Ia=43.62A, Ib=45.8A, Ic=1.967kA.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
170 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
171 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
172 | 220kV U. Kolab-Therubali Ckt-III |  |  |  |  | 0.093056 | 1 | 18 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 99.99% | 166.4 | 1121280
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:28 | 0.093056 | 1 | 18 | [5 empty] | No Tripping at therubali end. Kolab end-DP relay, 0 km, IR = 393.1A, IY = 581A, IB = 511.9A. System Failure at Therubali Grid
132 KV
173 | 132kV Akhusing-Mohana |  |  |  |  | 0.95903 | 14 | 15 | [7 empty] | 69.2 | 8760 | 99.84% | 986.1 | 606192
|  | 2023-04-04 | 23:44 | 2023-04-04 | 23:57 | 0.0090278 | 0 | 13 | [5 empty] | E/F
|  | 2023-07-17 | 04:12 | 2023-07-17 | 17:05 | 0.53681 | 0 | 59 | [5 empty] | DP Relay operated, Dist=11.67km, Zone=1, Fault type=ABT, Ia=30A, Ib=290A, Ic=20A
|  | 2023-07-17 | 04:00 | 2023-07-17 | 04:12 | 0.0083333 | 0 | 12 | [5 empty] | DP Relay operated, Dist=11.67km, Zone=1, Fault type=ABT, Ia=660A, Ib=551A, Ic=25A, In=118A
|  | 2023-07-22 | 14:38 | 2023-07-22 | 14:47 | 0.00625 | 0 | 9 | [5 empty] | Back up Relay operated on O/C & E/F. Dist=63.3km, Ia=50A, Ib=4700A, Ic=0A
|  | 2023-11-03 | 09:03 | 2023-11-03 | 18:22 | 0.38819 | 0 | 27 | [5 empty] | Breakdown of Line
|  | 2024-03-09 | 10:20 | 2024-03-09 | 10:35 | 0.010417 | 0 | 15 | [5 empty] | At Akhusingh end: R-Y, O/C, Dist- 9.7km. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
174 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 1899-12-31 07:03 | 15 | 0 | [7 empty] | 76.1 | 8760 | 99.83% | 1141.5 | 666636
|  | 2023-04-04 | 23:44 | 2023-04-04 | 23:57 | 0.0090278 | 0 | 13 | [5 empty] | E/F
|  | 2023-09-29 | 10:19 | 2023-09-29 | 10:42 | 0.015972 | 0 | 23 | [5 empty] | Incomer failure
|  | 2023-10-02 | 18:08 | 2023-10-02 | 18:38 | 0.020833 | 0 | 5 | [5 empty] | Machhkund I/C failed
|  | 2023-10-03 | 20:18 | 2023-10-03 | 20:27 | 0.00625 | 0 | 9 | [5 empty] | Machhkund I/C failed
|  | 2024-01-31 | 11:22 | 2024-01-31 | 11:31 | 0.00625 | 0 | 9 | [5 empty] | Failed from Source
|  | 2024-01-31 | 16:47 | 2024-01-31 | 16:54 | 0.0048611 | 0 | 7 | [5 empty] | Failed from Source
|  | 2023-08-03 | 11:32 | 2023-08-03 | 11:39 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Machhkund end. -
|  | 2023-08-03 | 11:42 | 2023-08-03 | 12:45 | 0.04375 | 0 | 25 | [5 empty] | AutoTripped on General trip, E/F PU, IL1= 0.17kA, IL2= 0.62kA, IL3= 0.11kA 1614mS, Rsec= 94ohm, Xsec= 9.34ohm, Rpri= 282.01ohm, Xpri= 28.02 ohm, Dist= 71.8KM.. the line was declared faulty.Akhusingh gss availed load from Gunupur
|  | 2023-08-03 | 12:45 | 04.08.23 | 16:05 | 1899-12-31 03:20 | 0 | 20 | [5 empty] | AutoTripped on General trip, E/F PU, L2-E, Dir. O/C & E/F relay optd.IL1= 0.02kA, IL2= 0.36kA, IL3= 0.02kA 1614mS, Rsec= 44.96ohm, Xsec= 13.80ohm, Rpri= 134.88 Ohm, Xpri= 41.41 ohm, Dist= 98.6 KM.. Yph insulator puncture at Loc 4,10 & 428
|  | 2023-08-07 | 11:09 | 2023-08-07 | 11:17 | 0.0055556 | 0 | 8 | [5 empty] | Tripped from Rayagada end. -
|  | 2023-08-28 | 6:50 | 2023-08-28 | 6:59 | 0.00625 | 0 | 9 | [5 empty] | E/F. -
|  | 2023-09-26 | 14:09 | 2023-09-26 | 14:20 | 0.0076389 | 0 | 11 | [5 empty] | O/C & M/T.
|  | 2023-09-26 | 14:20 | 2023-09-26 | 14:54 | 0.023611 | 0 | 34 | [5 empty] | O/C & M/T.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
175 | 132kV Akhusing-Gunupur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.296 | 8760 | 100% | 0 | 204072.96
176 | 132kV Gunupur- Palasingi RTSS |  |  |  |  | 0.85278 | 14 | 52 | [7 empty] | 16.214 | 7188 | 99.79% | 241.0481 | 116546.232
|  | 2023-07-12 | 18:03 | 2023-07-12 | 18:10 | 0.0048611 | 0 | 7 | [5 empty] | Tripped on Master trip relay (86A & 86B ).
|  | 2023-07-12 | 18:12 | 2023-07-12 | 18:35 | 0.015972 | 0 | 23 | [5 empty] | Tripped on Master trip relay (86A & 86B ).
|  | 2023-07-12 | 18:52 | 2023-07-12 | 19:13 | 0.014583 | 0 | 21 | [5 empty] | Tripped on Master trip relay (86A & 86B ).
|  | 2023-12-31 | 12:26 | 2023-12-31 | 12:33 | 0.0048611 | 0 | 7 | [5 empty] | O/C (R & B Ph). -
|  | 2024-01-11 | 14:46 | 12.01.24 | 8:33 | 0.74097 | 0 | 11 | [5 empty] | Tripped on Over voltage. -
|  | 2024-01-23 | 12:19 | 2024-01-23 | 12:27 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on O/C (R-Ph & B-Ph). -
|  | 2024-02-05 | 10:08 | 2024-02-05 | 10:31 | 0.015972 | 0 | 23 | [5 empty] | O/C (R & B-Ph). -
|  | 2024-02-05 | 13:43 | 2024-02-05 | 14:05 | 0.015278 | 0 | 22 | [5 empty] | O/C (R & B-Ph). -
|  | 2024-03-20 | 17:11 | 2024-03-20 | 17:24 | 0.0090278 | 0 | 13 | [5 empty] | O/C (R & B Ph). -
|  | 2024-03-20 | 05:35 | 2024-03-20 | 06:12 | 0.025694 | 0 | 37 | [5 empty] | Bus-bar trip(96). -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
177 | 132kV Angul-Boinda |  |  |  |  | 0.59306 | 12 | 52 | [7 empty] | 38.1 | 8760 | 99.85% | 490.22 | 333756
|  | 2023-07-30 | 00:00 | 2023-07-30 | 14:06 | 0.5875 | 0 | 44 | [5 empty] | At Boinda end:- Yph-Bph-E, If=3.12kA. wire snapped and fell on Ma
|  | 2023-06-19 | 01:26 | 2023-06-19 | 01:28 | 0.0013889 | 0 | 2 | [5 empty] | THE FEEDER TRIPPED AT ANGUL GRID END. 132 KV P/S AVAILED AT 01:28 . FROM BOINDA GRID END.
|  | 2023-06-19 | 01:29 | 2023-06-19 | 01:35 | 0.0041667 | 0 | 6 | [5 empty] | THE FEEDER TRIPPED AT ANGUL GRID END. 132 KV P/S AVAILED AT 01:28 . FROM BOINDA GRID END.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
178 | 132kV Boinda- RTSS Boinda |  |  |  |  | 0.5875 | 0 | 44 | [7 empty] | 2.947 | 8760 | 99.99% | 2.1611 | 25815.72
|  | 2023-07-30 | 00:00 | 2023-07-30 | 14:06 | 0.5875 | 0 | 44 | [5 empty] | At Boinda end:- Yph-Bph-E, If=3.12kA. wire snapped and fell on Ma
179 | 132kV Boinda-Rairakhol |  |  |  |  | 0.093056 | 13 | 6 | [7 empty] | 59 | 8760 | 99.85% | 772.9 | 516840
|  | 2023-07-30 | 00:01 | 2023-07-30 | 00:16 | 0.010417 | 0 | 9 | [5 empty] | No relay indication. The feeder was tripped at Boinda and Angul grid end. 132kV p/s availed at
|  | 2023-06-10 | 14:44 | 2023-06-10 | 16:00 | 0.052778 | 0 | 14 | [5 empty] | At Boinda end:- R-ph, Zone-1, L1 -N, Dist-30.566km, If=1431.59A At Rairakhol end:- TRIPPED DUE TO E/F & IL1=1.431A,3PH TRIP,TRIP-R,ZONE-1. 132 KV P/S AVAILED AT 15:07 . FROM MANESWAR GRID END.
|  | 2023-10-01 | 20:57 | 2023-10-01 | 21:12 | 0.010417 | 0 | 15 | [5 empty] | At Rairakhol end: R Ph,Zone 1, Dist- 26.54 km, Ir- 125.6 A At Boinda end: E/F. The Feeder tripped at Boinda grid end and 132kV power supply availed at 21:12 Hrs from Maneswar grid end.
|  | 2024-03-24 | 00:14 | 2024-03-24 | 00:34 | 0.013889 | 0 | 20 | [5 empty] | R-Y-B, Zone 1, Dist- 6.663km, If- 2.634kA. 132kV P/S availed at 00:34Hrs from Maneswar GSS end
|  | 2023-06-19 | 01:26 | 2023-06-19 | 01:28 | 0.0013889 | 0 | 2 | [5 empty] | THE FEEDER TRIPPED AT ANGUL GRID END. 132 KV P/S AVAILED AT 01:28 . FROM BOINDA GRID END.
|  | 2023-06-19 | 01:29 | 2023-06-19 | 01:35 | 0.0041667 | 0 | 6 | [5 empty] | THE FEEDER TRIPPED AT ANGUL GRID END. 132 KV P/S AVAILED AT 01:28 . FROM BOINDA GRID END.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
180 | 132kV Maneswar-Rairakhol |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 57.46 | 8760 | 100% | 7.6613 | 503349.6
|  | 2023-07-29 | 20:10 | 2023-07-29 | 20:18 | 0.0055556 | 0 | 8 | [5 empty] | No relay indication. The feeder was tripped at Sambalpur grid end. 132kV p/s availed at
181 | 132kV Sambalpur-Maneswar |  |  |  |  | 0.063194 | 0 | 12 | [7 empty] | 11.2 | 8760 | 100% | 2.24 | 98112
|  | 2023-07-29 | 20:10 | 2023-07-29 | 21:37 | 0.060417 | 0 | 8 | [5 empty] | power supply failure from Sambalpur end. Weather- Thunderstorm
|  | 2023-10-07 | 17:23 | 2023-10-07 | 17:27 | 0.0027778 | 0 | 4 | [5 empty] | Incomer Failure. -
182 | 132kV Maneswar- RTSS Maneswar |  |  |  |  | 0.20069 | 16 | 49 | [7 empty] | 5.2 | 8760 | 99.81% | 87.4467 | 45552
|  | 2023-12-11 | 17:31 | 2023-12-11 | 17:33 | 0.0013889 | 0 | 2 | [5 empty] | Tripped on over-current Relay. -
|  | 2024-01-11 | 09:58 | 2024-01-11 | 10:20 | 0.015278 | 0 | 22 | [5 empty] | O/C, E/F. -
|  | 2024-02-23 | 14:12 | 2024-02-23 | 18:23 | 0.17431 | 4 | 11 | [5 empty] | R-N, Ir- 1.045A. -
|  | 2024-03-12 | 19:51 | 2024-03-12 | 19:53 | 0.0013889 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-07-29 | 20:10 | 2023-07-29 | 20:18 | 0.0055556 | 0 | 8 | [5 empty] | No relay indication. The feeder was tripped at Sambalpur grid end. 132kV p/s availed at
|  | 2023-10-07 | 17:23 | 2023-10-07 | 17:27 | 0.0027778 | 0 | 4 | [5 empty] | Incomer Failure. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
183 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 1899-12-31 13:31 | 24 | 52 | [7 empty] | 10.826 | 8760 | 99.72% | 269.2065 | 94835.76
|  | 2023-05-29 | 15:25 | 2023-05-29 | 15:52 | 0.01875 | 0 | 27 | [5 empty] | Tripped at both Chainpal & Angul end on Distance Proection Relay. Relay indication at Chainpal end Z1, IA=6.2kA, Distance=9.64Km. Relay indication at Angul end Z1, IA=3.4kA, Distance=5.387Km.. Heavy rain and severe lighting
|  | 2023-05-30 | 15:46 | 2023-05-30 | 13:38 | 0.90417 | 0 | 21 | [5 empty] | Tripped on DP Relay,Fault loop-L1N,Fault current -3.73KA, Fault abs. distance-8.4KM
|  | 2023-06-19 | 01:16 | 2023-06-19 | 14:46 | 0.5625 | 10 | 12 | [5 empty] | Tripped on DP Relay,Fault loop-L1N,Fault current - 3.06KA, Fault abs. distance-5.438KM
|  | 2023-07-20 | 13:06 | 2023-07-20 | 13:15 | 0.00625 | 0 | 9 | [5 empty] | O/C(R-ph)
|  | 2024-03-19 | 00:49 | 2024-03-19 | 01:19 | 0.020833 | 0 | 30 | [5 empty] | O/C (B Ph) & E/F, Ib- 3.44kA
|  | 2024-03-31 | 07:26 | 2024-03-31 | 07:58 | 0.022222 | 0 | 32 | [5 empty] | O/C (B Ph) & E/F, Ib- 3.52kA
|  | 2023-05-18 | 15:05 | 2023-05-18 | 15:46 | 0.028472 | 0 | 41 | [5 empty] | Tripped on DP Relay,Fault loop-L2N,Fault current -4.042KA, Fault abs. distance-4.54KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
184 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0.12917 | 15 | 26 | [7 empty] | 10.826 | 8760 | 99.72% | 167.0813 | 94835.76
|  | 2023-05-30 | 15:46 | 2023-05-30 | 16:07 | 00:21 | 0 | 21 | [5 empty] | Tripped on DP Relay,Fault loop-L1N,Fault current -4.292KA, Fault abs. distance-6.9KM
|  | 2023-06-19 | 01:16 | 2023-06-19 | 01:51 | 0.024306 | 0 | 35 | [5 empty] | Tripped on DP Relay,Fault loop-L1N,Fault current - 3.29KA, Fault abs. distance-5.941KM
|  | 2023-07-20 | 13:06 | 2023-07-20 | 13:15 | 0.00625 | 0 | 9 | [5 empty] | O/C(R-ph)&E/F
|  | 2024-03-19 | 00:49 | 2024-03-19 | 01:30 | 0.028472 | 0 | 41 | [5 empty] | B-N, Ib- 4.6kA, Dist- 5.833km
|  | 2024-03-31 | 07:26 | 2024-03-31 | 07:59 | 0.022917 | 0 | 32 | [5 empty] | R-N, Zone 1, Dist- 5.87km, Ir- 4.7kA
|  | 2023-05-18 | 15:05 | 2023-05-18 | 15:46 | 0.028472 | 0 | 41 | [5 empty] | Tripped on DP Relay,Fault loop-L2N,Fault current -4.042KA, Fault abs. distance-4.54KM
|  | 2023-05-29 | 15:25 | 2023-05-29 | 15:52 | 0.01875 | 0 | 27 | [5 empty] | Tripped at both Chainpal & Angul end on Distance Proection Relay. Relay indication at Chainpal end Z1, IA=6.2kA, Distance=9.64Km. Relay indication at Angul end Z1, IA=3.4kA, Distance=5.387Km.. Heavy rain and severe lighting
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
185 | 132kV Joda -Barbil |  |  |  |  | 0.052778 | 13 | 9 | [7 empty] | 10.22 | 8760 | 99.85% | 134.393 | 89527.2
|  | 2023-05-19 | 19:12 | 2023-05-19 | 20:01 | 0.034028 | 0 | 49 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- Fault-O/C Relay- 86(A), 86(B) Fault Current:- Ia- 5.17KA, Ib- 3.2KA, Ic- 0.37KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
186 | 132kV Barbil- RML (Karakolha) |  |  |  |  | 1899-12-31 00:45 | 24 | 38 | [7 empty] | 31.811 | 8760 | 99.72% | 783.611 | 278664.36
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-07-21 | 12:56 | 2023-07-21 | 14:03 | 0.046528 | 1 | 7 | [5 empty] | At Barbil end:- Relay- D/P Relay, Started phase:- A,B,C,N, Tripped Phase:- A,B,C, Zone-I, Fault Loc.:- 19.76km, Fault current:- Ia- 3.319kA, Ib-3.456kA, Ic- 3.497kA At KSP end:- Relay- D/P Relay, Tripped Phase:- A,B,C, Zone-I, Fault Loc.:- 17.75km, Fault current:- Ia- 321.6A, Ib-313.7A, Ic- 326.7A. 132KV BARBIL-KSP fdr made idle charged and stood OK.
|  | 2023-07-28 | 20:04 | 2023-07-28 | 20:23 | 0.013194 | 0 | 19 | [5 empty] | At Barbil end:- Relay- D/P Relay, Started phase:- A,N, Tripped Phase:- A,B,C, Zone-I, Fault Loc.:- 24.2km, Fault current:- Ia- 2.5kA, Ib-125A, Ic- 138A. Heavy lightning and rainfall at Barbil Grid end.
|  | 2023-07-31 | 14:24 | 2023-08-01 | 11:50 | 0.89306 | 21 | 26 | [5 empty] | At Barbil end:- Relay- D/P Relay, Tripped Phase:- A,N, Fault current:- Ia- 4.66kA, Ib-147.6A, Ic- 4.929kA. rain, lightning and thunder s
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
187 | 132kV Barbil - Bolani |  |  |  |  | 0.083333 | 13 | 53 | [7 empty] | 7.8 | 8760 | 99.84% | 108.29 | 68328
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-24 | 18:11 | 2023-06-24 | 18:18 | 0.0048611 | 0 | 7 | [5 empty] | Tripped due to master trip relay ..
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
188 | 132kV Bolani - Arya Iron & Steel |  |  |  |  | 0.085417 | 13 | 56 | [7 empty] | 3.17 | 8760 | 99.84% | 44.1687 | 27769.2
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-24 | 18:15 | 2023-06-24 | 18:25 | 0.0069444 | 0 | 10 | [5 empty] | Tripped due to E/F. ..
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
189 | 132kV Arya Iron & Steel- RML (Karakendra) |  |  |  |  | 0.078472 | 13 | 46 | [7 empty] | 12.639 | 8760 | 99.84% | 173.9969 | 110717.64
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
190 | 132kV Arya Iron & Steel- BRPL |  |  |  |  | 0.078472 | 13 | 46 | [7 empty] | 9.008 | 8760 | 99.84% | 124.0101 | 78910.08
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
191 | 132kV RML (Karakendra)-Nalda RTSS |  |  |  |  | 0.078472 | 13 | 46 | [7 empty] | 6.554 | 8760 | 99.84% | 90.2267 | 57413.04
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-06-18 | 21:05 | 2023-06-18 | 22:07 | 0.043056 | 1 | 2 | [5 empty] | 132KV Barbil-KSP(RML) fdr tripped only at Barbil Grid S/S with following relay indications At Barbil Grid end:- B/U relay:- E/F, Ia=2.4kA, Ib= 49A, Ic- =44A, In=2.1kA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
192 | 132kV RML (Karakendra)- RML (Karakolha) |  |  |  |  | 0.035417 | 12 | 44 | [7 empty] | 0.894 | 8760 | 99.85% | 11.3836 | 7831.44
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:24 | 0.013194 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
193 | 132kV Nalda-Beekay Steel |  |  |  |  | 0.022222 | 0 | 32 | [7 empty] | 5.4 | 8760 | 99.99% | 2.88 | 47304
|  | 2023-05-27 | 20:40 | 2023-05-27 | 21:04 | 0.016667 | 0 | 24 | [5 empty] | 132KV Barbil-Joda fdr tripped only at Joda Grid S/S with following relay indications At Joda Grid S/S End:- B/U Relay- Directional O/C Fault Current:- Ia- 2.34KA, Ib- 0.08KA, Ic- 0.07KA. Heavy rainfall, thunderstorm and windstorm
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
194 | 132kV Beekay Steel - Bhalulata RTSS |  |  |  |  | 0.85 | 30 | 44 | [7 empty] | 27 | 8760 | 99.65% | 829.8 | 236520
|  | 2023-04-19 | 10:20 | 2023-04-19 | 10:38 | 0.0125 | 0 | 18 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=57.71 km, zone-2,event =ABT,Fault current details-: IA=2143 A,IB=2237 A,IC=34 A, IN=0 A,IG=207 A. FDR CHARGED & STOOD OK
|  | 2023-04-25 | 07:20 | 2023-04-25 | 08:35 | 0.052083 | 1 | 15 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=0.75 km, zone-1,event =BGT,Fault current details-: IA=226 A,IB=13480 A,IC=179 A, IN=1 A,IG=13076 A. FDR CHARGED & STOOD OK
|  | 2023-04-27 | 15:33 | 2023-04-27 | 15:43 | 0.0069444 | 0 | 10 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=40.21 km, zone-1,event =AGT,Fault current details-: IA=2338 A,IB=369 A,IC=388 A, IN=0 A,IG=1585 A. FDR CHARGED & STOOD OK
|  | 2023-05-19 | 19:09 | 2023-05-19 | 20:02 | 0.036806 | 0 | 53 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=60.75 km, zone- 2,event =ABT,Fault current details-: IA=2199 A,IB=2236 A,IC=106 A, IN=0 A,IG=1170 A. BAD WEATHER
|  | 2023-09-17 | 13:56 | 2023-09-17 | 14:16 | 0.013889 | 0 | 20 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=34.86 km, zone-1,event =ABCT,Fault current details-: IA=3465 A,IB=3785 A,IC=3568 A,IG=290 A.
|  | 2023-09-19 | 18:25 | 2023-09-19 | 18:36 | 0.0076389 | 0 | 11 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=45 km, zone- 1,event =ABCT,Fault current details-: IA=2921 A,IB=3190 A,IC=2978 A.
|  | 2023-09-26 | 18:26 | 2023-09-26 | 19:29 | 0.04375 | 1 | 3 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=36.02 km, zone-1,event =ABCT,Fault current details-: IA=3460 A,IB=3614 A,IC=3241 A,IG=213 A.
|  | 2023-10-10 | 11:39 | 2023-10-10 | 18:40 | 0.29236 | 7 | 1 | [5 empty] | Zone 1,Y-N, Dist- 12.87 km, Iy- 2.155 kA. -
|  | 2023-10-19 | 19:55 | 2023-10-19 | 20:06 | 0.0076389 | 0 | 11 | [5 empty] | At Rourkela end: Ir- 3.083 kA, Iy- 2.991 kA, Zone 1, Dist- 40.15 km At BK Steel end: Iy- 0.663 kA, Zone 1, Dist- 40.53 km. Feeder Charged but tripped immediately
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
195 | 132 kV Aska New -Chatrapur |  |  |  |  | 0.013889 | 0 | 20 | [7 empty] | 48.8 | 8760 | 100% | 16.2667 | 427488
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:23 | 0.013889 | 0 | 20 | [5 empty] | Y-N, Dist- 0.65 m, Zone 3, Iy- 1.136 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
196 | 132 kV Aska-Aska New-II |  |  |  |  | 0.045833 | 0 | 47 | [7 empty] | 6.98 | 8760 | 99.99% | 5.4677 | 61144.8
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:29 | 0.045833 | 0 | 47 | [5 empty] | At Aska end:- Zone-2, A-N, Dist-9.58km, IA-1.485kA, IB- 244.7A, IC-251.8A At Aska New end:- Zone-4, IR-1.486kA, Dist-434.4m.
197 | 132kV Aska New- Hinjili |  |  |  |  | 0.036806 | 0 | 47 | [7 empty] | 24.6 | 8760 | 99.99% | 19.27 | 215496
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:16 | 0.036806 | 0 | 47 | [5 empty] | At Hinjili end:- DP (Micom P442):- Did not Trip, Pick Up in Z- 2, Dir O/C Relay: (Micom P141), Ir=1.07kA, Iy=0.117kA, Ib=0.067kA, In=1.001kA At Aska New end:- Distance Relay:- (Micom P442) Zone-2, 14.96Km, Ir = 1.077kA. Due to Monkey fault at 40MVA Power Trf-1 (132KV R-ph DI) at Aska New End
198 | 132kV Hinjili- Berhampur |  |  |  |  | 0.043056 | 0 | 56 | [7 empty] | 16.77 | 8760 | 99.99% | 15.652 | 146905.2
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:16 | 0.036806 | 0 | 47 | [5 empty] | At Hinjili end:- DP (Micom P442):- Did not Trip, Pick Up in Z- 2, Dir O/C Relay: (Micom P141), Ir=1.07kA, Iy=0.117kA, Ib=0.067kA, In=1.001kA At Aska New end:- Distance Relay:- (Micom P442) Zone-2, 14.96Km, Ir = 1.077kA. Due to Monkey fault at 40MVA Power Trf-1 (132KV R-ph DI) at Aska New End
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:12 | 0.00625 | 0 | 9 | [5 empty] | B/C Relay. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
199 | 132kV Aska- Aska New- I |  |  |  |  | 0.045833 | 0 | 47 | [7 empty] | 6.66 | 8760 | 99.99% | 5.217 | 58341.6
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:29 | 0.045833 | 0 | 47 | [5 empty] | At Aska end:- Zone-2, A-N, Dist-9.58km, IA-1.485kA, IB- 244.7A, IC-251.8A At Aska New end:- Zone-4, IR-1.486kA, Dist-434.4m.
200 | 132 kV Aska-Purusottampur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.21 | 8760 | 100% | 0 | 247119.6
201 | 132 kV Aska New-Digapahandi-I |  |  |  |  | 0.04375 | 0 | 47 | [7 empty] | 38.187 | 8760 | 99.99% | 29.9131 | 334518.12
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:26 | 0.04375 | 0 | 47 | [5 empty] | At Digapahandi end:- DP relay optd. Zone -3, Dist-48.33km, Fault current- Ia=505.8A, Ib-94.62A, Ic-64.22A. Digapahandi GSS & Chikiti GSS availed P/S from Berhampur end at 14:28Hrs
202 | 132 kV Aska New-Digapahandi-II |  |  |  |  | 0.04375 | 0 | 47 | [7 empty] | 38.187 | 8760 | 99.99% | 29.9131 | 334518.12
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:26 | 0.04375 | 0 | 47 | [5 empty] | At Digapahandi end:- DP relay optd. Zone -3, Dist-48.33km, Fault current- Ia=505.8A, Ib-94.62A, Ic-64.22A. Digapahandi GSS & Chikiti GSS availed P/S from Berhampur end at 14:28Hrs
203 | 132 kV Balasore-Udala |  |  |  |  | 0.025694 | 0 | 37 | [7 empty] | 70.86 | 8760 | 99.99% | 43.697 | 620733.6
|  | 2023-06-13 | 16:03 | 2023-06-13 | 16:07 | 0.0027778 | 0 | 4 | [5 empty] | At Baripada end:- No relay operated At PGCIL end:- Backup relay operated:- Directional L3 pickup, Directional O/C trip(B-phase), IL3=0.7kA, time delay=1492ms. CB was trip from PGCIL (KUCHEI) & Balasore grid end .Weather Condition- Rain & lightening..
|  | 2023-09-23 | 10:58 | 2023-09-23 | 11:31 | 0:33 | 0 | 33 | [5 empty] | 132KV Balasore-Udala line H/T from Balasore grid end due to Over-loading of above said feeder.
204 | 132 kV Betanati-Udala |  |  |  |  | 0.050694 | 13 | 13 | [7 empty] | 49.89 | 8760 | 99.85% | 659.3795 | 437036.4
|  | 2023-06-13 | 16:03 | 2023-06-13 | 16:07 | 0.0027778 | 0 | 4 | [5 empty] | At Baripada end:- No relay operated At PGCIL end:- Backup relay operated:- Directional L3 pickup, Directional O/C trip(B-phase), IL3=0.7kA, time delay=1492ms. CB was trip from PGCIL (KUCHEI) & Balasore grid end .Weather Condition- Rain & lightening..
|  | 2024-02-21 | 08:33 | 2024-02-21 | 09:03 | 0.020833 | 0 | 30 | [5 empty] | Source failure. No source from Balasore grid end because of 220kV Main bus shutdown at Balasore GSS.
|  | 2023-09-23 | 10:58 | 2023-09-23 | 11:37 | 0:39 | 0 | 39 | [5 empty] | Source Failure.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
205 | 132 kV Baripada- Betanati |  |  |  |  | 0.10347 | 13 | 51 | [7 empty] | 24.43 | 8760 | 99.84% | 338.3555 | 214006.8
|  | 2023-06-13 | 16:03 | 2023-06-13 | 16:07 | 0.0027778 | 0 | 4 | [5 empty] | At Baripada end:- No relay operated At PGCIL end:- Backup relay operated:- Directional L3 pickup, Directional O/C trip(B-phase), IL3=0.7kA, time delay=1492ms. CB was trip from PGCIL (KUCHEI) & Balasore grid end .Weather Condition- Rain & lightening..
|  | 2023-09-23 | 10:58 | 2023-09-23 | 11:41 | 0.029861 | 0 | 43 | [5 empty] | P/S failed from Betonoti grid end due to Breaker tripped from Balasore grid end due to overload.. At that time 132 KV Baripada-PGCIL LINE UNDER S/D. P/S to all the 33 kv area Fdr interuppted at Baripada grid S/S.
|  | 2023-09-29 | 20:23 | 2023-09-29 | 21:35 | 0.05 | 0 | 34 | [5 empty] | At Baripada end:- DP relay operated, Distance P/U L12-E, P/U time=60 ms, Trip time=0 ms, R-Ph & Y-Ph trip, Zone-I, Dist=3.7km, IL1=4.88kA, IL2=4.61kA, IL3=0.16kA, Rsec=.28 Ohm, Xsec=.47 KA At Betonoti end:- Started Phase-ABN, Tripped Phase-ABC, Start element-Distance, Zone-II, Relay trip time-80.04m, Fault location-23.48km, Ia=965.1A, Ib=951.1 A, Ic=175A,Van=13.06kV, Vbn=1.341kV, Vcn=76.93kV. P/S to all the 33 kv area Fdr interuppted at Baripada grid S/S.
|  | 2024-02-21 | 08:33 | 2024-02-21 | 09:03 | 0.020833 | 0 | 30 | [5 empty] | Source failure. No source from Balasore grid end because of 220kV Main bus shutdown at Balasore GSS.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
206 | 132 kV Balasore-Basta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 32.51 | 8760 | 100% | 0 | 284787.6
207 | 132 kV Balasore- Balasore Alloy |  |  |  |  | 0.13264 | 15 | 11 | [7 empty] | 6.45 | 8760 | 99.83% | 97.9325 | 56502
|  | 2023-04-14 | 15:37 | 2023-04-14 | 16:24 | 0.032639 | 0 | 47 | [5 empty] | At Balasore end:- fault indication-Overpower, fault current=Ir-275.2A, Iy-268.0A, Ib-270.0A
|  | 2023-04-19 | 10:25 | 2023-04-19 | 11:41 | 0.052778 | 1 | 16 | [5 empty] | At Balasore end:- fault indication-Overpower, fault current:- Ir-259.7A, Iy-270.0A, Ib-270.8A
|  | 2023-04-22 | 19:53 | 2023-04-22 | 20:46 | 0.036806 | 0 | 53 | [5 empty] | At Balasore end:- fault indication- E/F & O/C, fault current= Ir-292.1A, Iy-255.3A, Ib-247.6A
|  | 2023-08-26 | 17:15 | 2023-08-26 | 17:30 | 0.010417 | 0 | 15 | [5 empty] | At Balasore end:- fault indication-O/C and E/F, fault current= Ir-213.3A, Iy-939.3A, Ib-790.2A, In=674.4A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
208 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0.35903 | 8 | 37 | [7 empty] | 2.598 | 8760 | 99.9% | 22.3861 | 22758.48
|  | 2023-11-26 | 03:01 | 2023-11-26 | 11:38 | 0.35903 | 8 | 37 | [5 empty] | B Ph, Zone 1, O/C-E/F Hiset, Dist- 0.18km, Ib-7.588 kA
209 | 132 kV Balasore- Balasore RTSS |  |  |  |  | 0.079167 | 13 | 54 | [7 empty] | 3.565 | 8760 | 99.84% | 49.5535 | 31229.4
|  | 2023-08-07 | 17:28 | 2023-08-07 | 17:36 | 0.0055556 | 0 | 8 | [5 empty] | At Balasore end:- Back up Relay: O/C,R-ph,Y-ph trip fault current:Ir=0.28KA,IY=0.28KA.
|  | 2023-08-15 | 7:15 | 2023-08-15 | 7:22 | 0.0048611 | 0 | 7 | [5 empty] | At Balasore end:- Back up Relay: O/C, R-ph, Y-ph trip fault current:Ir=0.29kA, IY=0.29kA
|  | 2023-12-08 | 17:57 | 2023-12-08 | 18:17 | 0.013889 | 0 | 20 | [5 empty] | B/C Relay: O/C, R-Y, Ir- 0.285 kA, Iy- 0.284 kA
|  | 2023-12-25 | 17:36 | 2023-12-25 | 18:00 | 0.016667 | 0 | 24 | [5 empty] | O/C, R & Y Ph, If- 0.358 kA
|  | 2024-01-08 | 17:36 | 2024-01-08 | 17:46 | 0.0069444 | 0 | 10 | [5 empty] | B/C Relay: O/C, R-Ph, If- 0.327kA
|  | 2024-02-21 | 19:04 | 2024-02-21 | 19:41 | 0.025694 | 0 | 37 | [5 empty] | R-Ph, Zone 1, Ir- 7.996kA, Dist- 2.16km
|  | 2024-02-24 | 07:24 | 2024-02-24 | 07:32 | 0.0055556 | 0 | 8 | [5 empty] | B/C Relay: O/C, R-Ph, Ir- 375.83 A, Iy- 374.47 A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
210 | 132 kV Balasore-Chandipur |  |  |  |  | 0.078472 | 0 | 10 | [7 empty] | 45.76 | 8760 | 100% | 7.6267 | 400857.6
|  | 2024-03-14 | 15:34 | 2024-03-14 | 17:27 | 0.078472 | 0 | 10 | [5 empty] | At Balasore end: Y-N, Zone 1, Dist- 19.34km, Iy- 4.517kA At Chandipur end: Y-N, Zone 1, Dist- 18.54km, Iy- 1.019kA
211 | 132 kV Chandipur-Soro |  |  |  |  | 0.3 | 19 | 11 | [7 empty] | 43.26 | 8760 | 99.78% | 829.871 | 378957.6
|  | 2023-05-15 | 14:38 | 2023-05-15 | 14:54 | 0.011111 | 0 | 16 | [5 empty] | 132 KV Relay details Soro Grid end:- Breaker did not trippeed 132 KV Relay details Chandipur Grid end:- Zone-I,Y-ph, Fault distance-29.89KM. Soro Grid Blackout from 14:38 Hrs to 14:54 Hrs. 11:26 Hrs 132 KV Soro- Bhadrak line H/T from Bhadrak end & charged at 16:55 Hrs.
|  | 2023-05-31 | 18:59 | 2023-05-31 | 20:08 | 0.047917 | 1 | 9 | [5 empty] | 132 KV Relay details Soro Grid end:- Zone-2,C-G, Location- 33.79KM ,A=51 Amp,B=58 Amp,C=1342 Amp ,G-1238Amp 132 KV Relay details Chandipur Grid end:- Zone-I, B-ph. At that time P/S available from Bhadrak Grid. B- Phase Insulator Burst at LOC No-188 of 132 KV BLS Chandipr Line. The feeder was charged at 20:01 hrs but tripped immediately.
|  | 2023-05-31 | 23:22 | 2023-06-01 | 4:42 | 0.22222 | 5 | 20 | [5 empty] | Source Failure. Before The Incident the 132 KV Soro- Chandipur Line was charged from Soro Grid . Soro Grid was getting P/S from Bhadrak Grid through 132 KV Soro- Bhadrak Line . 132KV Soro-Bhadrak Line Tripped at 23:22 Hr at Bhadrak Grid only Soro Grid end Breaker didn't Tripped.At 4:42 Hr Dated 1/06/2023 132 KV Soro- Chandipur Line was charged from Chandipur Grid end & P/S restored at Soro Grid .Black out from 23:22 Hr Dated 31/05/2023 to 4:42 Hr Dated 01/06/2023 at Soro Grid.
|  | 2023-12-28 | 23:56 | 29.12.23 | 0:23 | 0.01875 | 0 | 26 | [5 empty] | At Soro end: Y-N, Dist- 8.95 km, Iy- 1.705 kA, Zone 1, B/U Relay - E/F & O/C in Y ph At Chandipur end: Y-N, Zone 1, Dist- 27.45 km. No fault was found when patrolling was done from LOC No.150 to 170.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
212 | 132 kV Balasore-Somnathpur |  |  |  |  | 0.030556 | 12 | 44 | [7 empty] | 4 | 8760 | 99.85% | 50.9333 | 35040
|  | 2023-05-28 | 16:20 | 2023-05-28 | 16:40 | 0.013889 | 0 | 20 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-8186 A,IL2-141.1 A,IL3- 230.9 A. At Somanathpur end: Breaker didn't trip at Somanathpur end.
|  | 2023-05-29 | 08:40 | 2023-05-29 | 08:46 | 0.0041667 | 0 | 6 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-7391 A,IL2-61.48 A,IL3- 133.4 A. At Somanathpur end: Breaker didn't trip at Somanathpur end.
|  | 2023-08-13 | 23:18 | 2023-08-13 | 23:36 | 0.0125 | 0 | 18 | [5 empty] | At Balasore end:- Fault details:O/C, Y-ph,B-ph, fault current Iy-8628A, Ib-7306A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
213 | 132 kV Somnathpur-Stork |  |  |  |  | 0.018056 | 0 | 26 | [7 empty] | 0.1 | 8760 | 100% | 0.043333 | 876
|  | 2023-05-28 | 16:20 | 2023-05-28 | 16:40 | 0.013889 | 0 | 20 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-8186 A,IL2-141.1 A,IL3- 230.9 A. At Somanathpur end: Breaker didn't trip
|  | 2023-05-29 | 08:40 | 2023-05-29 | 08:46 | 0.0041667 | 0 | 6 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-7391 A,IL2-61.48 A,IL3- 133.4 A. At Somanathpur end: Breaker didn't trip.
214 | 132 kV Somnathpur-EMAMI |  |  |  |  | 0.030556 | 12 | 44 | [7 empty] | 6 | 8760 | 99.85% | 76.4 | 52560
|  | 2023-05-28 | 16:20 | 2023-05-28 | 16:40 | 0.013889 | 0 | 20 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-8186 A,IL2-141.1 A,IL3- 230.9 A. At Somanathpur end: Breaker didn't trip at Somanathpur end.
|  | 2023-05-29 | 08:40 | 2023-05-29 | 08:46 | 0.0041667 | 0 | 6 | [5 empty] | At Balasore end: O/C & E/F ,Zone-II, R-ph to N ,Fault current IL1-7391 A,IL2-61.48 A,IL3- 133.4 A. At Somanathpur end: Breaker didn't trip at Somanathpur end.
|  | 2023-08-13 | 23:18 | 2023-08-13 | 23:36 | 0.0125 | 0 | 18 | [5 empty] | At Balasore end:- Fault details:O/C, Y-ph,B-ph, fault current Iy-8628A, Ib-7306A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
216 | 132kV Balugaon-Chandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 43.12 | 8760 | 100% | 0 | 377731.2
217 | 132 kv Balugaon-Solari RTSS |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 14.1 | 8760 | 100% | 3.995 | 123516
|  | 2023-09-27 | 05:21 | 2023-09-27 | 05:32 | 0.0076389 | 0 | 11 | [5 empty] | At Balugaon end:- DP relay(SEL-311C) indication:-Dist- 9.63km, Zone-1, Ir=0A, Iy=2342A, Ib=17A, Ig=2360A. hase overcurrent and earth f
|  | 2023-11-10 | 00:40 | 2023-11-10 | 00:46 | 0.0041667 | 0 | 6 | [5 empty] | At Balugaon end: Y-N, Zone 1, Dist- 0.61 km, Iy- 3.032 kA. Y phase O/C & E/F
218 | 132 kv Banki-Nuapatna |  |  |  |  | 0.24306 | 14 | 24 | [7 empty] | 20.61 | 8760 | 99.84% | 296.784 | 180543.6
|  | 2023-12-05 | 11:08 | 2023-12-05 | 11:21 | 0.0090278 | 0 | 28 | [5 empty] | Y Ph O/C. -
|  | 2024-01-05 | 10:56 | 2024-01-05 | 11:08 | 0.0083333 | 0 | 21 | [5 empty] | Tripped from Nuapatna end. 132kV Nuapatna-Banki Feeder tripped from Nuapatna between L/C period of 132kV Atri-Banki Feeder which leads to complete interruption of power of GSS Banki.
|  | 2023-06-17 | 14:54 | 2023-06-17 | 15:08 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on O/C at Banki end , Power supply failed at Nuapatna grid S/S, Ia= 407A, Ib=342A, Ic=350A. Nuapatna and Arati were availing P/S from Banki
|  | 2023-04-12 | 02:41 | 2023-04-12 | 03:22 | 0.028472 | 0 | 41 | [5 empty] | Nuapatna-Banki supply failed from Atri end (Breaker H/T at 02:45 hrs at Nuapatna end). Failed from Atri Grid end due to mal operation of Isolator 89A of 132Kv side Auto-Trf- 1 at Atri grid.
|  | 2023-04-12 | 03:22 | 2023-04-12 | 07:15 | 0.16181 | 0 | 13 | [5 empty] | During closing of Banki line again P/S failed, Total supply to Nuapatna grid failed (Khajuriakata supply failed). Charged through B/C and restored P/S
|  | 2023-06-23 | 10:15 | 2023-06-23 | 10:52 | 0.025694 | 0 | 27 | [5 empty] | Tripped with following indication at Nuapatna : Zone -1, Ir=1.341kA, Iy=1.352kA, ib=18.45A, Dist-2.791km. Touching of tree branch to the conductor.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
219 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
220 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.87 | 8760 | 100% | 0 | 25141.2
221 | 132 kV Katapalli-Thuapalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.5 | 8760 | 100% | 0 | 293460
222 | 132 kV Thuapalli-Bargarh |  |  |  |  | 0.052083 | 1 | 15 | [7 empty] | 43.9 | 8760 | 99.99% | 54.875 | 384564
|  | 2023-05-27 | 20:11 | 2023-05-27 | 21:26 | 0.052083 | 1 | 15 | [5 empty] | D=10.8 Km , IR=0.313KA, IY=3246A, IB=103A, Zone-2, Y-E fault Thuapali end - D=32.9 Km, IR=0.31KA, IY=1690A, IB=0.10KA, Zone-1, Y-E fault. Weather-Cloudy and windy
223 | 132 kV Bargarh New-Ghens Ckt -I |  |  |  |  | 0.49583 | 16 | 26 | [7 empty] | 29.13 | 8760 | 99.81% | 478.703 | 255178.8
|  | 2023-04-15 | 19:34 | 2023-04-15 | 19:45 | 0.0076389 | 0 | 11 | [5 empty] | Back up operation operated.
|  | 2023-09-20 | 00:34 | 2023-09-20 | 09:37 | 0.37708 | 1 | 35 | [5 empty] | Z-1,Loc:-25.2km,Ia-2.1KA. Heavy Rain & Lighting
|  | 2023-07-25 | 08:04 | 2023-07-25 | 10:44 | 0.11111 | 2 | 40 | [5 empty] | Source failure.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
224 | 132 kV Bargarh New-Ghens Ckt -II |  |  |  |  | 0.37708 | 1 | 35 | [7 empty] | 29.13 | 8760 | 99.98% | 46.1225 | 255178.8
|  | 2023-09-20 | 00:34 | 2023-09-20 | 09:37 | 0.37708 | 1 | 35 | [5 empty] | Z-1,Loc:-25.2km,Ia-2.1KA. Heavy Rain & Lighting
225 | 132 kV Bargarh New- Bhatli Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 40.225 | 6756 | 100% | 0 | 271760.1
226 | 132 kV Bargarh New- Bhatli Ckt -II |  |  |  |  | 0.031944 | 0 | 46 | [7 empty] | 40.225 | 6756 | 99.99% | 30.8392 | 271760.1
|  | 2023-09-29 | 21:09 | 2023-09-29 | 21:55 | 0.031944 | 0 | 46 | [5 empty] | A-G, Z-1,Loc:-14.3km. Heavy Rain & Lighting
227 | 132kV Baripada-Kuchei PG |  |  |  |  | 0.040972 | 12 | 59 | [7 empty] | 3.1 | 8760 | 99.85% | 40.2483 | 27156
|  | 2023-06-13 | 16:03 | 2023-06-13 | 16:07 | 0.0027778 | 0 | 4 | [5 empty] | At Baripada end:- No relay operated At PGCIL end:- Backup relay operated:- Directional L3 pickup, Directional O/C trip(B-phase), IL3=0.7kA, time delay=1492ms. CB was trip from PGCIL (KUCHEI) & Balasore grid end .Weather Condition- Rain & lightening..
|  | 2023-09-29 | 20:23 | 2023-09-29 | 20:57 | 0.023611 | 0 | 34 | [5 empty] | At PGCIL grid end:- Back up relay O/C operated, Directional O/C P/U, Directional L1 P/U, Directional Earth P/U, IL1=2.52kA, IL2=1.69kA, IL3=0.13kA, DP Main-I(Only P/U), Zone-III, Distance-17 km. P/S to all the 33 kv area Fdr interuppted at Baripada grid S/S.
|  | 2024-02-21 | 08:33 | 2024-02-21 | 08:54 | 0.014583 | 0 | 21 | [5 empty] | At Kuchei end: B/C Relay- Ir- 0.38kA, Iy- 0.26kA, Ib- 0.25kA. The Line tripped from PGCIL end only due to overdrawal.. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
228 | 132kV Berhampur-Digapahandi |  |  |  |  | 0.065972 | 13 | 16 | [7 empty] | 31.48 | 8760 | 99.85% | 417.6347 | 275764.8
|  | 2023-09-05 | 14:23 | 2023-09-05 | 15:29 | 0.045833 | 0 | 47 | [5 empty] | At Aska end:- Zone-2, A-N, Dist-9.58km, IA-1.485kA, IB- 244.7A, IC-251.8A At Aska New end:- Zone-4, IR-1.486kA, Dist-434.4m.
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:13 | 0.0069444 | 0 | 10 | [5 empty] | B/U relay: Ir-1.36 kA, Iy- 1.49 kA, Ib- 1.37 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
|  | 2023-05-24 | 13:58 | 2023-05-24 | 14:10 | 0.0083333 | 0 | 12 | [5 empty] | Digapahandi end. DP relay optd. Zone -1, AGT, Dist.-4.0KM, Fault current- Ia=302A, Ib-204A, Ic- 355A, Ig=857A Berhampur end-Distance relay optd. Rph to N trip. Distance- 22.10km, Ir=2.732kamp . MR optd.. Weather condition cloudy
|  | 2023-05-30 | 17:30 | 2023-05-30 | 17:37 | 0.0048611 | 0 | 7 | [5 empty] | Digapahandi end. DP relay optd. Zone - 1,AGT, Dist.-2.82KM, Fault current- Ia=476A, Ib-300A, Ic-526A, Ig=1292A. Rain & heavy thunderstoms at Digapahandi end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
229 | 132kV Bhadrak-FACOR |  |  |  |  | 0.90347 | 33 | 41 | [7 empty] | 4.564 | 8760 | 99.62% | 153.7307 | 39980.64
|  | 2023-04-22 | 02:51 | 2023-04-22 | 23:58 | 0.87986 | 21 | 7 | [5 empty] | Zone-I, Active group-I, Started Phase A,B,N, Triped Phase A,B,C IA=6.25KA, IB=5.950kA, IC=63.29A, Dist-4.25km.
|  | 02.10.22 | 00:35 | 02.10.22 | 00:49 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on B phase O/C and E/F , Active group 1, Fault Location 83.22km, Ia=109.4A, Ib=142.8A, Ic=200.9A
|  | 2023-01-13 | 09:05 | 2023-01-13 | 09:25 | 0.013889 | 0 | 20 | [5 empty] | At Bhadrak end:- Tripped on Y- PH O/C, IA= 124.9A, IB= 123.2A, IC= 199.6A, VAB=130kV, VBC=130kV, VCA=128kV
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
230 | 132kV Bhadrak-Dhamara Port |  |  |  |  | 0.06875 | 1 | 39 | [7 empty] | 63.9 | 8760 | 99.98% | 105.435 | 559764
|  | 2023-04-18 | 13:06 | 2023-04-18 | 13:27 | 0.014583 | 0 | 21 | [5 empty] | Started Phase AN, Tripped phase ABC, Zone-I, Dist-21.62km, IA=2.398kA, IB=104.1A, IC=157.9A.
|  | 2023-07-10 | 06:53 | 2023-07-10 | 08:11 | 0.054167 | 1 | 18 | [5 empty] | Triped on active group-I, Tripped phase-ABC, Ia=1.03kA, Ib=1.13kA, Ic=919.5A, In=76.22A, Vab=11.6kV, Vbc=116.1kV, Vca=112.6kV, Vn=0.23V.
231 | 132kV Bhadrak-Dhamara Port Traction |  |  |  |  | 0 | 0 | 0 | [7 empty] | 35.3 | 8760 | 100% | 0 | 309228
232 | 132kV Bhadrak-Bhadrak Traction |  |  |  |  | 0.043056 | 13 | 2 | [7 empty] | 8.086 | 8760 | 99.85% | 105.3875 | 70833.36
|  | 2023-04-11 | 14:32 | 2023-04-11 | 14:38 | 0.0041667 | 0 | 6 | [5 empty] | Y phase B phase O/C, IL2=0.29kA, IL3=0.29kA.
|  | 2023-04-26 | 18:34 | 2023-04-26 | 18:36 | 0.0013889 | 0 | 2 | [5 empty] | Y phase B phase O/C, IL2=0.29kA, IL3=0.28kA.
|  | 2023-05-12 | 14:34 | 2023-05-12 | 14:37 | 0.0020833 | 0 | 3 | [5 empty] | Tripped on O/C Y & B phase,IL1=0.00KA,IL2=0.28KA,IL3=0.28KA.
|  | 2023-05-28 | 09:43 | 2023-05-28 | 09:51 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on O/C Y & B phase,IL1=0.00KA,IL2=0.27KA,IL3=0.27KA.
|  | 2023-07-15 | 11:13 | 2023-07-15 | 11:24 | 0.0076389 | 0 | 11 | [5 empty] | Tripped on backup relay, 86 optd, Y ph p/u, E/F p/u, IL1=0.00kA, IL2=7.15kA, IL3=0.01kA, DP relay operated, Started phase=BN, Tripped phase=ABC, Zone-I, Fault duration=70.06ms, Relay trip time=80.07ms, Fault location = 3.188km, Ia=0.0A, Ib=7.448kA, Ic=31.70A, source fail from Karanjia end.
|  | 2023-07-15 | 12:13 | 2023-07-15 | 12:21 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on backup relay, 86 optd, Y ph p/u, E/F p/u, IL1=0.00kA, IL2=7.15kA, IL3=0.01kA, DP relay operated, Started phase=BN, Tripped phase=ABC, Zone-I, Fault duration=70.06ms, Relay trip time=80.07ms, Fault location = 3.188km, Ia=0.0A, Ib=7.448kA, Ic=31.70A, source fail from Karanjia end.
|  | 2023-12-06 | 09:24 | 2023-12-06 | 09:40 | 0.011111 | 0 | 16 | [5 empty] | O/C, Y & B Ph, Iy- 0.3 kA, Ib- 0.3 kA. -
|  | 2023-12-27 | 14:38 | 2023-12-27 | 14:40 | 0.0013889 | 0 | 2 | [5 empty] | O/C Y & B Ph, Iy- 0.26 kA, Ib- 0.25 kA. -
|  | 2024-02-21 | 09:31 | 2024-02-21 | 09:37 | 0.0041667 | 0 | 6 | [5 empty] | Y-B, directional O/C, If- 0.27kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
233 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0.073611 | 1 | 46 | [7 empty] | 40.12 | 8760 | 99.98% | 70.8787 | 351451.2
|  | 2023-06-06 | 15:58 | 2023-06-06 | 17:00 | 0.043056 | 1 | 2 | [5 empty] | Tripped on B phase O/C &E/F, Started phase CN,Zone-I, Fault location 1.344KM,Ia=128.8A,Ib=262.0A,Ic=8.75KA [Heavy rainfall, lightning]. Heavy rainfall, lightning
|  | 2023-04-04 | 15:32 | 2023-04-04 | 16:16 | 0.030556 | 0 | 44 | [5 empty] | B Phase E/F, Zone-I, Distance-1.35km, IL1=70.45A, IL2=151.7A, IL3=8.570kA.
234 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.32 | 8760 | 100% | 0 | 291883.2
235 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
236 | 132kV Bhanjanagar- G. Udaygiri |  |  |  |  | 1899-12-31 06:27 | 42 | 27 | [7 empty] | 53.4 | 8760 | 99.52% | 2266.83 | 467784
|  | 2023-12-17 | 07:09 | 2023-12-17 | 16:04 | 0.37153 | 8 | 55 | [5 empty] | At Bhanjanagar end: Y-B-N, Zone 1, Dist- 3.601 km, Ir- 0.205 kA, Iy- 7.908 kA, Ib- 7.86 kA Jumper Snapped at Loc No. 13 of 132kV Bhanjanagar-G.Udaygiri Line. Annual maintenanace on dt. 17-12- 23 from 8:00 to 16:04 Hrs
|  | 2023-04-13 | 11:49 | 2023-04-13 | 13:17 | 0.061111 | 1 | 28 | [5 empty] | At Bhanjanagar end:- CN, Zone-1, Dist-4.23km, IC=5.92kA. Line Charged after pattroling
|  | 2023-06-14 | 18:04 | 15.06.23 | 12:23 | 0.76319 | 18 | 19 | [5 empty] | At Bhanjanagar end:- BN, Zone-1, Dist-38.37km, IB=2.429kA At G Udayagiri end:- BN, Zone-1, Dist-12.4km, IB= 0.31kA. L/C TAKEN BY GSS G UDAYGIRI FOR B/D
|  | 2023-09-04 | 09:29 | 2023-09-04 | 11:14 | 0.072917 | 1 | 45 | [5 empty] | At Bhanjanagar end:- BCN, Zone-1, Dist=16.45km, IA=132.8A, IB=230.5A, IC=3.525kA. 132KV Bhanjanagar- G.Udayagiri Ckt tripped at Bhanjanagar end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
237 | 132KV G. Udaygiri -Phulbani |  |  |  |  | 0.925 | 34 | 12 | [7 empty] | 54.5 | 8760 | 99.61% | 1863.9 | 477420
|  | 2023-04-13 | 11:49 | 2023-04-13 | 13:17 | 0.061111 | 1 | 28 | [5 empty] | At Bhanjanagar end:- CN, Zone-1, Dist-4.23km, IC=5.92kA. Line Charged after pattroling
|  | 2023-06-14 | 18:04 | 15.06.23 | 12:23 | 0.76319 | 18 | 19 | [5 empty] | At Bhanjanagar end:- BN, Zone-1, Dist-38.37km, IB=2.429kA At G Udayagiri end:- BN, Zone-1, Dist-12.4km, IB= 0.31kA. L/C TAKEN BY GSS G UDAYGIRI FOR B/D
|  | 2023-09-04 | 09:29 | 2023-09-04 | 11:14 | 0.072917 | 1 | 45 | [5 empty] | At Bhanjanagar end:- BCN, Zone-1, Dist=16.45km, IA=132.8A, IB=230.5A, IC=3.525kA. 132KV Bhanjanagar- G.Udayagiri Ckt tripped at Bhanjanagar end
|  | 2023-05-31 | 20:10 | 2023-05-31 | 20:50 | 0.027778 | 0 | 40 | [5 empty] | Bph & E/F, zone-1, 1.1Km, If=1.91kA. Charged after field patrolling and verification of the line & stood ok.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
238 | 132kV Pratapsasan -Badagada (Kesura) |  |  |  |  | 0.35556 | 0 | 35 | [7 empty] | 11.108 | 8760 | 99.99% | 6.4797 | 97306.08
|  | 2024-03-05 | 17:19 | 2024-03-05 | 19:28 | 0.089583 | 0 | 29 | [5 empty] | Tripped due to flashover at (R,Y-Ph) breaker limb of 33kV TRF II at Badagada end
|  | 2023-04-23 | 01:18 | 2023-04-23 | 07:41 | 0.26597 | 0 | 6 | [5 empty] | Over Voltage trip. Supply failed from Pratapsasan end but immediately availed supply from Ranasinghpur end within 6 mins.
239 | 132kV Pratapsasan -Nimapara |  |  |  |  | 0.77569 | 1 | 20 | [7 empty] | 35.083 | 8760 | 99.98% | 46.7773 | 307327.08
|  | 2023-06-07 | 18:10 | 08.06.23 | 12:47 | 0.77569 | 1 | 20 | [5 empty] | At Nimapara end:-No relay indication At Pratapsasan end:- SOTF, Z1, BN, Ia=316A, Ib=5.18KA, Ic=0.15KA, D=9.5KM (132KV Pratapsasan -Samangara feeder was in T-connection at Nimapara grid) [conductor snapped at loc. No.121]. A/R not operated.conductor snapped at loc. No.121
|  | 2023-06-02 | 16:42 | 2023-06-02 | 17:30 | 0.033333 | 0 | 48 | [5 empty] | R Phase to Earth fault ,Zone 3 OPTD, Ir=2.1KA, Iy=0.51KA, Ib=1.02KA. 132 KV Pratapsan supply was extended to Samangara through Nimapara reserve bus. The feeder test charged but didn't stand. Jumper snapped of 132kV Samangara-Nimapara feeder. Station Supply availed from 132kV Puri. A/R not operated at Prapsasan.
240 | 132kV Pratapsasan -Phulnakhara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.64 | 8760 | 100% | 0 | 128246.4
241 | 132kV Pratapsasan -Phulnakhara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.64 | 8760 | 100% | 0 | 128246.4
242 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 0.059722 | 0 | 14 | [7 empty] | 22.74 | 8760 | 100% | 5.306 | 199202.4
| ` | 2023-09-02 | 14:41 | 2023-09-02 | 16:07 | 0.059722 | 0 | 14 | [5 empty] | At Mancheswar end: DP, Zone-1, Ir=3.088kA, Iy=5.7A, Ib=1.52kA, Dist=1.32km At Phulnakhara end: DP relay operated in Zone-1, Y-ph (Top Conductor) to E/F , Dist= 15.77km, Ir= 64.31A, Iy= 3.048kA, Ib=102.8A. Tripped due to thunderstrom.
243 | 132kV Bhubaneswar-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.18 | 8760 | 100% | 0 | 45376.8
244 | 132kV Chandaka-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.8 | 8760 | 100% | 0 | 94608
245 | 132kV Bidanasi-Brajabiahripur |  |  |  |  | 0.12847 | 0 | 21 | [7 empty] | 10.1 | 8760 | 100% | 3.535 | 88476
|  | 2023-06-17 | 14:48 | 2023-06-17 | 17:53 | 0.12847 | 0 | 21 | [5 empty] | At Brajabiharipur end:- Dist-5.5km, L3-E/F PICKUP. IL1=IL2=0.36kA, IL3=2.69kA. B- PH SI to main bus jumper snapped
246 | 132kV Brajabiharipur-BPPL-Chandaka |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.1 | 8760 | 100% | 0 | 289956
247 | 132 kV Bargarh- Barpali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20 | 8760 | 100% | 0 | 175200
248 | 132 kV Bargarh- Bargarh New |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.6 | 8760 | 100% | 0 | 233016
249 | 132 kV Bargarh New -Barpalli |  |  |  |  | 0.0027778 | 0 | 4 | [7 empty] | 10.6 | 8760 | 100% | 0.70667 | 92856
|  | 2023-09-01 | 07:35 | 2023-09-01 | 07:39 | 0.0027778 | 0 | 4 | [5 empty] | O/C Trip, Ia-5.26KA, IB-0.24KA & Ic-0.30KA.
250 | 132 kV Barpalli- New Bolangir |  |  |  |  | 0.029861 | 0 | 43 | [7 empty] | 59.2 | 8760 | 99.99% | 42.4267 | 518592
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:17 | 0.017361 | 0 | 25 | [5 empty] | Source failure
|  | 2023-08-14 | 10:44 | 2023-08-14 | 11:02 | 0.0125 | 0 | 18 | [5 empty] | Tripped on operation of Differential Protection relay. Relay details:- IA=10.8A, IB=1.697kA, IC=13.16A, Distance=36.08km. -
251 | 132 kV Barpalli-Dunguripalli RTSS |  |  |  |  | 0.0020833 | 0 | 3 | [7 empty] | 12.8 | 8760 | 100% | 0.64 | 112128
|  | 2024-02-04 | 19:31 | 2024-02-04 | 19:34 | 0.0020833 | 0 | 3 | [5 empty] | O/C. -
252 | 132 kV New Bolangir - Sonepur |  |  |  |  | 0.37431 | 20 | 59 | [7 empty] | 52.85 | 8760 | 99.76% | 1108.9692 | 462966
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:03 | 0.0076389 | 0 | 11 | [5 empty] | Source failure
|  | 2023-10-19 | 15:47 | 2023-10-19 | 15:52 | 0.0034722 | 0 | 5 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 08:20 | 2023-10-04 | 08:53 | 0.022917 | 0 | 33 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 14:36 | 2023-10-04 | 14:43 | 0.0048611 | 0 | 7 | [5 empty] | Incomer Source Failure. -
|  | 2023-09-09 | 10:46 | 2023-09-09 | 11:01 | 0.010417 | 0 | 15 | [5 empty] | Incomer Source Failure.
|  | 2023-09-26 | 11:04 | 2023-09-26 | 12:27 | 0.057639 | 1 | 23 | [5 empty] | Incomer Source Failured. emergency s/d by gss sonepur
|  | 2024-03-07 | 15:05 | 2024-03-07 | 15:37 | 0.022222 | 0 | 32 | [5 empty] | Incoming supply failure. L/C at GSS Sonepur for tree trimming
|  | 2023-08-18 | 15:06 | 2023-08-18 | 16:34 | 0.061111 | 1 | 28 | [5 empty] | Source failure. -
|  | 2023-10-06 | 08:10 | 2023-10-06 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Failed from Source. -
|  | 2023-04-07 | 07:00 | 2023-04-07 | 10:26 | 0.14306 | 3 | 26 | [5 empty] | L/C OPTCL for tree cutting under 132 KV Balangir new- Sonepur CKT- 1 line.
|  | 2023-04-13 | 17:30 | 2023-04-13 | 17:40 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Balangir-new end on Distance protection (Zone-1).
|  | 2023-04-25 | 11:06 | 2023-04-25 | 11:19 | 0.0090278 | 0 | 13 | [5 empty] | Failure from source.
|  | 2023-04-27 | 11:22 | 2023-04-27 | 11:42 | 0.013889 | 0 | 20 | [5 empty] | Failure from source.
|  | 2023-06-17 | 18:36 | 2023-06-17 | 18:44 | 0.0055556 | 0 | 8 | [5 empty] | AC Supply failed from Bolangir (New).
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
253 | 132 kV Sonepur - Boudh |  |  |  |  | 0.44167 | 22 | 36 | [7 empty] | 50.25 | 8760 | 99.74% | 1135.65 | 440190
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:06 | 0.0097222 | 0 | 14 | [5 empty] | Source failure
|  | 2023-10-19 | 15:47 | 2023-10-19 | 15:52 | 0.0034722 | 0 | 5 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 08:20 | 2023-10-04 | 08:53 | 0.022917 | 0 | 33 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 14:36 | 2023-10-04 | 14:43 | 0.0048611 | 0 | 7 | [5 empty] | Incomer Source Failure. -
|  | 2023-09-09 | 10:46 | 2023-09-09 | 11:01 | 0.010417 | 0 | 15 | [5 empty] | Incomer Source Failure.
|  | 2023-09-26 | 11:04 | 2023-09-26 | 12:27 | 0.057639 | 1 | 23 | [5 empty] | Incomer Source Failured. emergency s/d by gss sonepur
|  | 2024-03-07 | 15:05 | 2024-03-07 | 15:37 | 0.022222 | 0 | 32 | [5 empty] | Incoming supply failure. L/C at GSS Sonepur for tree trimming
|  | 2023-08-18 | 15:06 | 2023-08-18 | 16:34 | 0.061111 | 1 | 28 | [5 empty] | Source failure. -
|  | 2023-10-06 | 08:10 | 2023-10-06 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Failed from Source. -
|  | 2023-04-07 | 07:00 | 2023-04-07 | 10:26 | 0.14306 | 3 | 26 | [5 empty] | L/C OPTCL for tree cutting under 132 KV Balangir new- Sonepur CKT- 1 line.
|  | 2023-04-13 | 17:30 | 2023-04-13 | 17:40 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Balangir-new end on Distance protection (Zone-1).
|  | 2023-04-25 | 11:06 | 2023-04-25 | 11:19 | 0.0090278 | 0 | 13 | [5 empty] | Failure from source.
|  | 2023-04-27 | 11:22 | 2023-04-27 | 11:42 | 0.013889 | 0 | 20 | [5 empty] | Failure from source.
|  | 2023-06-17 | 18:36 | 2023-06-17 | 18:44 | 0.0055556 | 0 | 8 | [5 empty] | AC Supply failed from Bolangir (New).
|  | 2023-08-02 | 15:09 | 2023-08-02 | 15:37 | 0.019444 | 0 | 28 | [5 empty] | O/C in B-ph. feeder charged but could not stand at first try.
|  | 2023-09-11 | 11:38 | 2023-09-11 | 11:55 | 0.011806 | 0 | 17 | [5 empty] | Tripped due to O/C in Y & B phase. Ia-27.37 A, Ib- 1.93 KA, Ic- 1.96 KA.
|  | 2023-09-14 | 13:48 | 2023-09-14 | 14:04 | 0.011111 | 0 | 16 | [5 empty] | Tripped due to O/C in R phase. Ia-2.055 KA, Ib-96.35 A, Ic- 84.25 A, Zone-1(2.77 Km).
|  | 2023-10-18 | 12:14 | 2023-10-18 | 12:23 | 0.00625 | 0 | 9 | [5 empty] | E/F. -
|  | 2024-03-15 | 12:58 | 2024-03-15 | 13:05 | 0.0048611 | 0 | 7 | [5 empty] | At Sonepur end: Zone 1, Dist- 29.1km, Iy- 1.58kA, Ib- 1.62kA. -
|  | 2024-03-16 | 12:40 | 2024-03-16 | 12:57 | 0.011806 | 0 | 17 | [5 empty] | E/F. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
254 | 132 kV Sonepur - Birmaharajpur |  |  |  |  | 0.42639 | 22 | 14 | [7 empty] | 24.774 | 8760 | 99.75% | 550.8086 | 217020.24
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:03 | 0.0076389 | 0 | 11 | [5 empty] | Source failure
|  | 2023-10-19 | 15:47 | 2023-10-19 | 15:52 | 0.0034722 | 0 | 5 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 08:20 | 2023-10-04 | 08:53 | 0.022917 | 0 | 33 | [5 empty] | Incomer Source Failure. -
|  | 2023-10-04 | 14:36 | 2023-10-04 | 14:43 | 0.0048611 | 0 | 7 | [5 empty] | Incomer Source Failure. -
|  | 2023-09-09 | 10:46 | 2023-09-09 | 11:01 | 0.010417 | 0 | 15 | [5 empty] | Incomer Source Failure.
|  | 2023-09-26 | 11:04 | 2023-09-26 | 12:27 | 0.057639 | 1 | 23 | [5 empty] | Incomer Source Failured. emergency s/d by gss sonepur
|  | 2024-03-07 | 15:05 | 2024-03-07 | 15:37 | 0.022222 | 0 | 32 | [5 empty] | Incoming supply failure. L/C at GSS Sonepur for tree trimming
|  | 2024-03-11 | 20:37 | 2024-03-11 | 20:58 | 0.014583 | 0 | 21 | [5 empty] | At Sonepur end: B-N, Zone 1, Dist- 12.44km, Ib- 1.726kA At Birmaharajpur end: B-N, Zone 1. -
|  | 2024-03-13 | 05:35 | 2024-03-13 | 05:40 | 0.0034722 | 0 | 5 | [5 empty] | At Sonepur end: B-N, Zone 1, Dist- 20.03km At Birmaharajpur end: B-N, Zone 1. -
|  | 2023-08-18 | 15:06 | 2023-08-18 | 16:34 | 0.061111 | 1 | 28 | [5 empty] | Source failure. -
|  | 2023-10-06 | 08:10 | 2023-10-06 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Failed from Source. -
|  | 2023-04-07 | 07:00 | 2023-04-07 | 10:26 | 0.14306 | 3 | 26 | [5 empty] | L/C OPTCL for tree cutting under 132 KV Balangir new- Sonepur CKT- 1 line.
|  | 2023-04-13 | 17:30 | 2023-04-13 | 17:40 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Balangir-new end on Distance protection (Zone-1).
|  | 2023-04-25 | 11:06 | 2023-04-25 | 11:19 | 0.0090278 | 0 | 13 | [5 empty] | Failure from source.
|  | 2023-04-27 | 11:22 | 2023-04-27 | 11:42 | 0.013889 | 0 | 20 | [5 empty] | Failure from source.
|  | 2023-06-17 | 18:36 | 2023-06-17 | 18:44 | 0.0055556 | 0 | 8 | [5 empty] | AC Supply failed from Bolangir (New).
|  | 2023-10-27 | 12:58 | 2023-10-27 | 13:08 | 0.0069444 | 0 | 10 | [5 empty] | E/F. -
|  | 2023-10-27 | 02:12 | 2023-10-27 | 02:27 | 0.010417 | 0 | 15 | [5 empty] | Distance protection, Zone 1. -
|  | 2024-02-23 | 21:06 | 2024-02-23 | 21:25 | 0.013194 | 0 | 19 | [5 empty] | At Sonepur end: B-Ph, Zone 1, Dist- 12.65km. -
|  | 2024-03-12 | 12:25 | 2024-03-12 | 12:30 | 0.0034722 | 0 | 5 | [5 empty] | E/F. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
255 | 132 kV New Bolangir - Bolangir Ckt - II |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 3.008 | 8760 | 100% | 0.65173 | 26350.08
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:31 | 0.0090278 | 0 | 13 | [5 empty] | Failed from source. -
256 | 132kV New Bolangir-Patnagarh Ckt - I |  |  |  |  | 0.08125 | 13 | 55 | [7 empty] | 39.41 | 8760 | 99.84% | 548.4558 | 345231.6
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:00 | 0.0055556 | 0 | 8 | [5 empty] | Source Failure
|  | 2023-09-13 | 18:35 | 2023-09-13 | 18:58 | 0.015972 | 0 | 21 | [5 empty] | TRIPPED on operation of Distance Protection relay. Relay details:Zone 1, IA=1.494KA, IB=2.398KA, IC=237.1A Fault Distance= 16.18km. From 18:56hrs, 132KV Bolangir New- Patnagarh ckt -II was in service o meet the load demand of GSS Patnagarh.
|  | 2023-09-20 | 16:08 | 2023-09-20 | 16:20 | 0.0083333 | 0 | 12 | [5 empty] | TRIPPED on operation of Distance Protection relay. Relay details: Zone 1, IA=4062.98A, IB=110.42A, IC=326.09A Fault Distance= 26.24km.
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure from 220/132KV GSS Sadeipali.
|  | 2023-09-20 | 16:07 | 2023-09-20 | 16:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-10-11 | 10:00 | 2023-10-11 | 10:05 | 0.0034722 | 0 | 5 | [5 empty] | Supply failed from Source end(Bolangir New). -
|  | 2023-10-08 | 09:08 | 2023-10-08 | 09:19 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2023-10-08 | 14:16 | 2023-10-08 | 14:27 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
257 | 132kV New Bolangir-Patnagarh Ckt - II |  |  |  |  | 0.065972 | 13 | 44 | [7 empty] | 39.41 | 8760 | 99.84% | 541.2307 | 345231.6
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:00 | 0.0055556 | 0 | 8 | [5 empty] | Source Failure
|  | 2023-09-20 | 16:08 | 2023-09-20 | 16:22 | 00:14 | 0 | 12 | [5 empty] | TRIPPED on operation of Distance Protection relay. Relay details: Zone 1, IA=3.061KA, IB=70.98KA, IC=236A Fault Distance= 17.66km Fault resistance= 4.663ohm.
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure from 220/132KV GSS Sadeipali.
|  | 2023-09-20 | 16:07 | 2023-09-20 | 16:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-10-11 | 10:00 | 2023-10-11 | 10:05 | 0.0034722 | 0 | 5 | [5 empty] | Supply failed from Source end(Bolangir New). -
|  | 2023-10-08 | 09:08 | 2023-10-08 | 09:19 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2023-10-08 | 14:16 | 2023-10-08 | 14:27 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2024-03-12 | 16:59 | 2024-03-12 | 17:12 | 0.0090278 | 0 | 10 | [5 empty] | At Bolangir New end: Zone 1, Dist- 28.68km, Ir-0.191kA, Iy-0.361kA, Ib- 1.95kA At Patnagarh end: Zone 1, Dist- 7.69km, Ir-0.191kA, Iy-0.366kA, Ib- 1.652kA. 132kV Balangir New-Patnagarh CKT I was in service to meet the load demand of GSS Patnagarh
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
258 | 132kV Duburi- BRPL |  |  |  |  | 1899-12-31 00:41 | 0 | 47 | [7 empty] | 7.632 | 8760 | 99.99% | 5.9784 | 66856.32
|  | 2024-02-27 | 00:31 | 2024-02-27 | 15:16 | 0.61458 | 0 | 39 | [5 empty] | Zone 1, If- 13.7kA. -
|  | 2024-03-31 | 05:52 | 2024-03-31 | 15:48 | 0.41389 | 0 | 8 | [5 empty] | Y-N, Zone 1, Dist- 1.071km, Iy- 13.78kA. -
259 | 132kV BRPL-Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.436 | 8760 | 100% | 0 | 38859.36
260 | 132kV Lapanga-Jharsuguda |  |  |  |  | 0.14306 | 13 | 1 | [7 empty] | 10.4 | 8760 | 99.85% | 135.3733 | 91104
|  | 2023-07-29 | 19:25 | 2023-07-29 | 21:02 | 0.067361 | 0 | 42 | [5 empty] | Ia=370.5A, Ib=204.6A, Ic=3.556kA, In=923.3A, In derived=924.3A. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2023-08-22 | 7:43 | 2023-08-22 | 9:17 | 0.065278 | 0 | 4 | [5 empty] | O/C, E/F IR-0.521KA, IY-0.192KA, IC-3.569 KA. -
|  | 2024-02-16 | 16:46 | 2024-02-16 | 17:01 | 0.010417 | 0 | 15 | [5 empty] | At Jharsuguda end: Y-Ph, E/F, O/C, Ir- 0.343kA, Iy- 1.542kA, Ib- 0.367kA No tripping at Lapanga end. Tripped due to Y phase conductor snapped at Aryan switchyard.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
261 | 132kV Budhipadar-Jharsuguda Ckt-I |  |  |  |  | 0.8625 | 13 | 10 | [7 empty] | 7 | 8760 | 99.85% | 92.1667 | 61320
|  | 2023-06-25 | 03:39 | 2023-06-25 | 04:36 | 0.039583 | 0 | 40 | [5 empty] | At Jharsuguda end:- B/U operated, E/F, Ir-592A, Ib-168A, Ic-137A. Weather:-Lightning & Rainy.
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
|  | 2023-06-04 | 16:07 | 2023-06-04 | 16:12 | 0.0034722 | 0 | 5 | [5 empty] | O/C E fault, Ia= 709.4 A, Ib= 208 A, Ic= 252 A.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
262 | 132kV Budhipadar-Jharsuguda Ckt-II |  |  |  |  | 0.81944 | 0 | 25 | [7 empty] | 4.5 | 8760 | 100% | 1.875 | 39420
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
263 | 132kV Budhipadar- Bamra |  |  |  |  | 0 | 0 | 0 | [7 empty] | 53 | 8760 | 100% | 0 | 464280
264 | 132kV Bamra-Rajgangpur |  |  |  |  | 0.031944 | 0 | 46 | [7 empty] | 44.2 | 8760 | 99.99% | 33.8867 | 387192
|  | 2023-08-17 | 9:33 | 2023-08-17 | 10:19 | 0.031944 | 0 | 46 | [5 empty] | Master Trip, R-PH O/C, IA=2.672kA, IB=196.6A, IC=84 A, Zone-1, Fault Duration=71.72ms, Fault Resistance=6.530Ω, Dist=28.65km. -
265 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 0.92917 | 15 | 2 | [7 empty] | 31.21 | 8760 | 99.83% | 469.1903 | 273399.6
|  | 2024-02-05 | 09:01 | 2024-02-05 | 09:17 | 0.011111 | 0 | 15 | [5 empty] | R-Y-N, Dist- 0.35km, Ir- 4.59kA, Iy- 4.94kA, Ib- 4.64kA. Snake Fault
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
|  | 2023-09-24 | 00:54 | 2023-09-24 | 01:50 | 0.038889 | 0 | 56 | [5 empty] | E/F, R-ph, Ir-0.28 KA, Iy-0.28 KA, Ib-0.28 KA.
|  | 2023-10-07 | 23:20 | 2023-10-07 | 23:45 | 0.017361 | 0 | 25 | [5 empty] | At Sundargarh end: R Ph- E/F, Zone 2, Dist- 26.41 km, Ir-376 A At Budhipadar end: B/U, E/F, R ph, Ir- 3.7 kA. -
|  | 2023-10-09 | 05:36 | 2023-10-09 | 06:00 | 0.016667 | 0 | 24 | [5 empty] | At Sundargarh end: E/F, B-N, Zone 2, Dist- 26.12 km, Ib- 410 A At Budhipadar end: B/U, O/C, B Ph, Ib- 3.8 kA. -
|  | 2023-10-09 | 02:45 | 2023-10-09 | 03:22 | 0.025694 | 0 | 37 | [5 empty] | At Sundargarh end: E/F, R-N, Zone 2, Dist-25.98 km, Ir-385 A At Budhipadar end: B/U, E/F, R-N, Ir- 3.8 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
266 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 0.87222 | 13 | 36 | [7 empty] | 31.21 | 8760 | 99.84% | 424.456 | 273399.6
|  | 2024-02-05 | 09:01 | 2024-02-05 | 09:17 | 0.011111 | 0 | 15 | [5 empty] | R-Y-B-N, Zone 4. Snake Fault
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
|  | 2023-09-24 | 00:54 | 2023-09-24 | 01:54 | 0.041667 | 0 | 56 | [5 empty] | DP,E/F,R-phase,Zone-1, Dist.6.12 Km, Ir-573 A, Iy-145 A, Ib- 148 A, In-863 A.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
267 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 0.32986 | 17 | 13 | [7 empty] | 22.6 | 8760 | 99.8% | 389.0967 | 197976
|  | 2023-07-29 | 19:16 | 2023-07-29 | 19:59 | 00:43 | 0 | 42 | [5 empty] | At Budhipadar end:- D/P operated (makeALSTOM Micom P444): R ph to E fault loop, Zone-1, Dist-12.88km, IL1=5.279kA, IL2=4.987A, IL3-4.188A, Fault Duration=68.56ms At MCL end:- CB did not trip. The feeder (Idle charged) tripped at Brajrajnagar end only. Weather: Heavy Lightning and rain weather-lightening and rain weather-lightening and rain (delay in charging due to CB spring charge problem and rain)
|  | 2023-06-04 | 15:53 | 2023-06-04 | 16:42 | 0.034028 | 0 | 48 | [5 empty] | D/P relay operated, zone-2, fault loop=R ph-E, Fault dist.=19.95KM, Ia=2.867kA, B/U relay:-R-ph, E/F,IL1=2.85kA. Line was Idle charged from budhipadar end. Weather:- thunderstorm & rain.
|  | 2023-08-16 | 17:11 | 2023-08-16 | 22:01 | 0.20139 | 1 | 35 | [5 empty] | At Budhipadar end:- D/P operated :F.L- R-N, ZONE 1, Fault duration- 76.67ms, Dist- 14.28km, IL1-4.452KA, IL2-4.31A, IL3-4.448A. Heavy Lightning and rain
|  | 2023-11-05 | 11:26 | 2023-11-05 | 12:27 | 0.042361 | 1 | 0 | [5 empty] | B-N, Zone 1, Dist- 1.72 km, Ib- 3.833 kA. Tripping was due to truck movement by MSP plant under this Line.
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 1 | 8 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
268 | 132kV Budhipadar-MCL(Jorbaga)-II |  |  |  |  | 0.033333 | 0 | 48 | [7 empty] | 22.6 | 1980 | 99.96% | 18.08 | 44748
|  | 2023-06-04 | 15:53 | 2023-06-04 | 16:41 | 0.033333 | 0 | 48 | [5 empty] | D/P relay operated, zone-2, fault loop=R ph-E, Fault dist.=19.95KM, Ia=2.867kA, B/U relay:-R-ph, E/F,IL1=2.85kA. Line was Idle charged from budhipadar end. Weather:- thunderstorm & rain.
269 | 132kV Budhipadar-Lakhanpur |  |  |  |  | 0.29583 | 15 | 15 | [7 empty] | 29.524 | 6780 | 99.78% | 450.241 | 200172.72
|  | 2023-08-16 | 17:11 | 2023-08-16 | 22:01 | 0.20139 | 1 | 35 | [5 empty] | At Budhipadar end:- D/P operated :F.L- R-N, ZONE 1, Fault duration- 76.67ms, Dist- 14.28km, IL1-4.452KA, IL2-4.31A, IL3-4.448A. Heavy Lightning and rain
|  | 2023-11-05 | 11:26 | 2023-11-05 | 12:27 | 0.042361 | 1 | 0 | [5 empty] | B-N, Zone 1, Dist- 1.72 km, Ib- 3.833 kA. Tripping was due to truck movement by MSP plant under this Line.
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 40 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
270 | 132kV Lakhanpur- Brajrajnagar (Remja) |  |  |  |  | 0.45833 | 17 | 49 | [7 empty] | 20.109 | 8076 | 99.78% | 358.2754 | 162400.284
|  | 2023-06-04 | 16:06 | 2023-06-04 | 17:01 | 0.038194 | 0 | 55 | [5 empty] | FFS, D/P operated at Budhipadar end: Rph to E trip, Zone 2 trip, Dist = 11.89km, Ia= 5.882kA. The132kV Budhipadar- Brajrajnagar I/C tripped at Budhipadar end. Weather:- Thunderstorm and rain.
|  | 2023-06-20 | 22:36 | 2023-06-20 | 23:44 | 0.047222 | 0 | 33 | [5 empty] | Failure From Source. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-06-25 | 03:17 | 2023-06-25 | 04:17 | 0.041667 | 0 | 18 | [5 empty] | B/U relay operated at Lakhanpur end: M/T operated and R ph pick up.. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only and 132kV Brajrajnagar Lakhanpur feeder tripped at Lakhanpur end along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-06-28 | 08:05 | 2023-06-28 | 08:28 | 0.015972 | 0 | 23 | [5 empty] | FFS. The feeder had failed simultaneously at Budhipadar end when 132 Budhipadar Brajrajnagar feeder was H/T
|  | 2023-06-30 | 12:52 | 2023-06-30 | 13:01 | 0.00625 | 0 | 9 | [5 empty] | FFS. 132 kV Lakhanpur Brajrajnagar feeder failed from GSS Lakhanpur on E/F due to 33 kV OCPL feeder's fault while 132 kV Budhipadar-Brajrajnagar feeder was under L/C
|  | 2023-07-29 | 19:17 | 2023-07-29 | 19:59 | 0.029167 | 0 | 42 | [5 empty] | D/P operated, Rph-E, Zone 1,FD=23.6km, IL1=2.77kA, IL2=0.28kA, IL3=2.89kA. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2023-08-16 | 17:11 | 2023-08-16 | 22:01 | 0.20139 | 1 | 35 | [5 empty] | At Budhipadar end:- D/P operated :F.L- R-N, ZONE 1, Fault duration- 76.67ms, Dist- 14.28km, IL1-4.452KA, IL2-4.31A, IL3-4.448A. Heavy Lightning and rain
|  | 2023-11-05 | 11:26 | 2023-11-05 | 12:27 | 0.042361 | 1 | 0 | [5 empty] | B-N, Zone 1, Dist- 1.72 km, Ib- 3.833 kA. Tripping was due to truck movement by MSP plant under this Line.
|  | 2023-07-09 | 20:51 | 2023-07-09 | 21:43 | 0.036111 | 0 | 14 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
271 | 132kV Brajrajnagar (Remja)- MCL(Jorbaga) |  |  |  |  | 0.95139 | 17 | 0 | [7 empty] | 24.855 | 6780 | 99.75% | 422.535 | 168516.9
|  | 2023-06-25 | 03:17 | 2023-06-25 | 03:35 | 0.0125 | 0 | 18 | [5 empty] | FFS. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only and 132kV Brajrajnagar Lakhanpur feeder tripped at Lakhanpur end along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-06-28 | 08:05 | 2023-06-28 | 08:52 | 0.032639 | 0 | 23 | [5 empty] | FFS. The feeder had failed simultaneously at Budhipadar end when 132 Budhipadar Brajrajnagar feeder was H/T
|  | 2023-06-30 | 12:52 | 2023-06-30 | 13:10 | 0.0125 | 0 | 10 | [5 empty] | FFS. 132 kV Lakhanpur Brajrajnagar feeder failed from GSS Lakhanpur on E/F due to 33 kV OCPL feeder's fault while 132 kV Budhipadar-Brajrajnagar feeder was under L/C
|  | 2023-07-29 | 19:10 | 2023-07-29 | 20:36 | 0.059722 | 0 | 42 | [5 empty] | D/P operated, Rph-E, Zone 1,FD=23.6km, IL1=2.77kA, IL2=0.28kA, IL3=2.89kA. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2023-08-02 | 23:15 | 2023-08-02 | 23:34 | 0.013194 | 0 | 19 | [5 empty] | At Brajrajnagar end:- D/P relay operated- Fault loop=L2-L3, IL1=0.06kA, IL2=9.08kA, IL3= 9.03kA, Fault Distance=3.1km, Fault resistance=0.38ohm Fault duration=100ms. Weather - Heavy lightning and rain at both ends.The said feeder tripped at Brajrajnagar end only. The feeder chaged after weather clear at our end and stood ok.
|  | 2023-08-03 | 0:13 | 2023-08-03 | 13:15 | 0.54306 | 0 | 19 | [5 empty] | At Brajrajnagar end:- D/P relay operated- Fault loop=L2-L3, Zone 1, IL1=0kA, IL2=7.53kA, IL3= 7.59kA, Fault Distance=3.2km, Fault resistance=0.41ohm Fault duration=100ms. The feeder tripped again at Brajrajnagar end only. After line patrolling, no fault was found and said feeder charged and stood ok. Main reason of tripping was due to lightning at that location.
|  | 2023-08-16 | 17:11 | 2023-08-16 | 22:01 | 0.20139 | 1 | 35 | [5 empty] | At Budhipadar end:- D/P operated :F.L- R-N, ZONE 1, Fault duration- 76.67ms, Dist- 14.28km, IL1-4.452KA, IL2-4.31A, IL3-4.448A. Heavy Lightning and rain
|  | 2023-11-05 | 11:26 | 2023-11-05 | 12:27 | 0.042361 | 1 | 0 | [5 empty] | B-N, Zone 1, Dist- 1.72 km, Ib- 3.833 kA. Tripping was due to truck movement by MSP plant under this Line.
|  | 2023-07-09 | 20:51 | 2023-07-09 | 21:40 | 0.034028 | 0 | 14 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
272 | 132kV Budhipadar-MSP |  |  |  |  | 0.15556 | 14 | 39 | [7 empty] | 0.592 | 8760 | 99.83% | 8.6728 | 5185.92
|  | 2023-06-28 | 00:07 | 2023-06-28 | 02:01 | 0.079167 | 1 | 54 | [5 empty] | B/U relay operated: O/C, Rph, Yph, Bph trip, IL1=7.1kA, IL2= 4.8kA, IL3=4.8kA.
|  | 2023-06-28 | 02:37 | 2023-06-28 | 03:00 | 0.015972 | 0 | 23 | [5 empty] | B/U relay operated: O/C, Rph, Yph, Bph trip, IL1=399A, IL2= 0 A, IL3=0 A.
|  | 2023-06-28 | 02:23 | 2023-06-28 | 02:35 | 0.0083333 | 0 | 12 | [5 empty] | E/F, IL1= 399.2A, IL2= 399.2A, IL3= 399A.
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 0 | 10 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
273 | 132kV Budhipadar-Brajrajnagar (Remja) |  |  |  |  | 0.23958 | 17 | 28 | [7 empty] | 11.75 | 8760 | 99.8% | 205.2333 | 102930
|  | 2023-04-21 | 07:54 | 2023-04-21 | 09:25 | 0.063194 | 1 | 31 | [5 empty] | FFS. 132kV Budhipadar- Brajrajnagar incomer tripped at Budhipadar end only. After line patrolling, the said line was charged and stood ok.
|  | 2023-06-04 | 16:06 | 2023-06-04 | 17:01 | 0.038194 | 0 | 55 | [5 empty] | FFS, D/P operated at Budhipadar end: Rph to E trip, Zone 2 trip, Dist = 11.89km, Ia= 5.882kA. The132kV Budhipadar- Brajrajnagar I/C tripped at Budhipadar end. Weather:- Thunderstorm and rain.
|  | 2023-06-20 | 22:36 | 2023-06-20 | 23:44 | 0.047222 | 0 | 33 | [5 empty] | Failure From Source. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-06-25 | 03:17 | 2023-06-25 | 03:35 | 0.0125 | 0 | 18 | [5 empty] | B/U relay operated at Budhipadar end: E/F, Ir=0.07kA, Iy=0.06kA, Ib=0.006kA. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only and 132kV Brajrajnagar Lakhanpur feeder tripped at Lakhanpur end along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-07-29 | 19:16 | 2023-07-29 | 19:59 | 00:43 | 0 | 42 | [5 empty] | At Budhipadar end:- D/P operated (makeALSTOM Micom P444): R ph to E fault loop, Zone-1, Dist-12.88km, IL1=5.279kA, IL2=4.987A, IL3-4.188A, Fault Duration=68.56ms At MCL end:- CB did not trip. The feeder (Idle charged) tripped at Brajrajnagar end only. Weather: Heavy Lightning and rain weather-lightening and rain weather-lightening and rain (delay in charging due to CB spring charge problem and rain)
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 1 | 15 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
|  | 2023-07-09 | 20:51 | 2023-07-09 | 21:29 | 0.026389 | 0 | 14 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
274 | 132kV Brajrajnagar- RTSS Kecchobahal |  |  |  |  | 0.48194 | 22 | 1 | [7 empty] | 11.75 | 8760 | 99.75% | 258.6958 | 102930
|  | 2023-10-06 | 10:13 | 2023-10-06 | 11:15 | 0.043056 | 1 | 2 | [5 empty] | B/U relay, B-N, Ib- 0.17 kA. -
|  | 2023-04-21 | 07:54 | 2023-04-21 | 09:25 | 0.063194 | 1 | 31 | [5 empty] | FFS. 132kV Budhipadar- Brajrajnagar incomer tripped at Budhipadar end only. After line patrolling, the said line was charged and stood ok.
|  | 2023-06-04 | 16:06 | 2023-06-04 | 17:01 | 0.038194 | 0 | 55 | [5 empty] | FFS, D/P operated at Budhipadar end: Rph to E trip, Zone 2 trip, Dist = 11.89km, Ia= 5.882kA. The132kV Budhipadar- Brajrajnagar I/C tripped at Budhipadar end. Weather:- Thunderstorm and rain.
|  | 2023-06-20 | 22:36 | 2023-06-20 | 23:44 | 0.047222 | 1 | 8 | [5 empty] | Failure From Source. 132kV Budhipadar Brajrajnagar tripped at Budhipadar end only along with 132kV RTSS Kechhobahal feeder.Weather condition: Heavy Lightning and rain.
|  | 2023-06-25 | 03:17 | 2023-06-25 | 05:44 | 0.10208 | 2 | 27 | [5 empty] | D/P operated: DIRI_A, RDI_A, DIRI_B, RDI_B, DIRI_C, RDI_C,PU_TOC_ A1, TRIP_TOC_A1, PU_TOC_ N1, TRIP_TOC_N1, Ia=27.548A, Ic=27.215A. Weather condition: Heavy Lightning and rain. After weather cleared from both side, the said feeder chaged and stood ok.
|  | 2023-06-28 | 08:05 | 2023-06-28 | 08:39 | 0.023611 | 0 | 34 | [5 empty] | FFS. The feeder had failed simultaneously at Budhipadar end when 132 Budhipadar Brajrajnagar feeder was H/T
|  | 2023-06-30 | 12:52 | 2023-06-30 | 13:09 | 0.011806 | 0 | 17 | [5 empty] | FFS. 132 kV Lakhanpur Brajrajnagar feeder failed from GSS Lakhanpur on E/F due to 33 kV OCPL feeder's fault while 132 kV Budhipadar-Brajrajnagar feeder was under L/C
|  | 2023-07-29 | 19:17 | 2023-07-29 | 20:59 | 0.070833 | 0 | 42 | [5 empty] | Incoming supply fail. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2024-03-09 | 14:06 | 2024-03-09 | 15:21 | 0.052083 | 1 | 11 | [5 empty] | Failure From Source. Tripped due to B-phase conductor snapped at Loc no.144
|  | 2023-07-09 | 20:51 | 2023-07-09 | 21:34 | 0.029861 | 0 | 14 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
275 | 132kV Brajrajnagar- RTSS Belpahar Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.293 | 5292 | 100% | 0 | 59762.556
276 | 132kV Brajrajnagar- RTSS Belpahar Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.293 | 5292 | 100% | 0 | 59762.556
277 | 132kV Budhipadar - Kalunga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 99 | 8760 | 100% | 0 | 867240
278 | 132kV Burla PH-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.5 | 8760 | 100% | 0 | 170820
279 | 132kV Burla PH-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
280 | 132kV Burla PH-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
281 | 132kV Burla PH-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 100% | 0 | 61320
282 | 132kV Burla PH-Katapali Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.26 | 8760 | 100% | 0 | 194997.6
283 | 132kV Burla-Hirakud |  |  |  |  | 1899-12-31 06:45 | 1 | 35 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 6.2 | 8760 | 99.98% | 9.8167 | 54312
|  | 2023-07-29 | 19:29 | 2023-07-30 | 15:46 | 0.84514 | 1 | 24 | [5 empty] | E/F At Lapanga end:- B/U, Rph, O/C, E/F, IR=2.12kA, IY=IB=0.01kA. Tripped due Tree falling between Location No.105 &106 of 132KV Lapanga- Hirakud-Burla PH Line. Charged after clearance of fault.
|  | 2023-08-18 | 23:55 | 2023-08-19 | 10:23 | 0.43611 | 0 | 11 | [5 empty] | At Lapanga end:- Fault:O/C & E/F on Y-B, Zone-1 Distance:8KM. -
284 | 132kV Hirakud-Lapanga |  |  |  |  | 1900-01-01 00:48 | 13 | 57 | [7 empty] | 38.2 | 8760 | 99.84% | 532.89 | 334632
|  | 2023-07-29 | 19:29 | 2023-07-30 | 15:46 | 0.84514 | 0 | 42 | [5 empty] | E/F At Lapanga end:- B/U, Rph, O/C, E/F, IR=2.12kA, IY=IB=0.01kA. Tripped due Tree falling between Location No.105 &106 of 132KV Lapanga- Hirakud-Burla PH Line. Charged after clearance of fault.
|  | 2023-08-18 | 23:55 | 2023-08-19 | 10:23 | 0.43611 | 0 | 11 | [5 empty] | At Lapanga end:- Fault:O/C & E/F on Y-B, Zone-1 Distance:8KM. -
|  | 2023-08-22 | 7:33 | 2023-08-22 | 7:42 | 0.00625 | 0 | 4 | [5 empty] | Fault: E/F on B-N, Zone-2 Distance:39.97KM. -
|  | 2023-09-15 | 17:14 | 2023-09-15 | 17:25 | 0.0076389 | 0 | 11 | [5 empty] | Fault:- O/C on Y-B Phase , Zone -None. E/F
|  | 2024-03-19 | 21:11 | 2024-03-20 | 14:54 | 0.73819 | 0 | 49 | [5 empty] | B-N, Ib- 4.67kA, Dist- 33.3km. Tripped due to earthwire snapped and fell on live wire
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
285 | 132kV Burla-Lapanga |  |  |  |  | 1899-12-31 04:11 | 1 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 43.6 | 8760 | 99.99% | 43.6 | 381936
|  | 2023-08-18 | 23:55 | 2023-08-19 | 10:23 | 0.43611 | 0 | 11 | [5 empty] | At Lapanga end:- Fault:O/C & E/F on Y-B, Zone-1 Distance:8KM. -
|  | 2024-03-19 | 21:11 | 2024-03-20 | 14:54 | 0.73819 | 0 | 49 | [5 empty] | B-N, Ib- 4.67kA, Dist- 33.3km. Tripped due to earthwire snapped and fell on live wire
286 | 132kV Lapanga-Budhipadar |  |  |  |  | 0.42778 | 15 | 25 | [7 empty] | 16 | 8760 | 99.82% | 246.6667 | 140160
|  | 2023-07-29 | 19:16 | 2023-07-29 | 21:19 | 0.085417 | 0 | 42 | [5 empty] | At Budhipadar end:- D/P operated (makeSiemens 7SA52): B ph to E fault loop, Dist-13.8km, IL1=0.35kA, IL2=0.29kA, IL3-4.6kA At Lapanga end:- B/U, O/C & E/F, SOTF, IL1=0kA, IL2=0kA, IL3=6.4kA. The feeder (Idle charged) tripped at Brajrajnagar end only. Weather: Heavy Lightning and rain weather-lightening and rain weather-lightening and rain (delay in charging due to CB spring charge problem and rain)
|  | 2023-08-16 | 16:55 | 2023-08-16 | 19:43 | 0.11667 | 1 | 35 | [5 empty] | At Budhipadar end:- D/P operated: F.L-L2-E, IL1-0.31KA, IL2-5.95KA, IL3-0.15KA, Zone 1 At Lapanga end:- D/P operated: Zone 2, Dist- 20km, IL1-0A, IL2- 6.56KA, IL3-6.55KA. Heavy Lightning and rain
|  | 2024-03-09 | 14:01 | 2024-03-09 | 19:26 | 0.22569 | 1 | 8 | [5 empty] | At Lapanga end: Y-B, Zone 1, Dist- 6.8km, Iy- 7.08kA, Ib- 7.84kA, B/C relay- Y-B, O/C. Tripped due to B-phase conductor snapped at Loc no.144
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
287 | 132kV Burla PH-Sambalpur |  |  |  |  | 0.054167 | 1 | 24 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.5 | 8760 | 99.98% | 27.3 | 170820
|  | 2023-07-29 | 19:48 | 2023-07-29 | 21:06 | 0.054167 | 1 | 24 | [5 empty] | At Sambalpur end:- Tripped on Yph E/F, Z4, Ia= 337.148A, Ib=1962.09A, Ic=212.926A, Ig=1413.675A, VA= 94kV, VB=107kV, VC=77kV, Vn=64kV, Fault dist.=2.76km At Katapali end:- Tripped on Z1, Fault dist.=11.7km. Transient fault
288 | 132kV Chainpal-Angul |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 14.93 | 8760 | 99.99% | 6.7185 | 130786.8
|  | 2023-05-29 | 15:25 | 2023-05-29 | 15:52 | 0.01875 | 0 | 27 | [5 empty] | Tripped at both Chainpal & Angul end on Distance Proection Relay. Relay indication at Chainpal end Z1, IA=6.2kA, Distance=9.64Km. Relay indication at Angul end Z1, IA=3.4kA, Distance=5.387Km.. Heavy rain and severe lighting
289 | 132kV Chainpal-Global-TFL |  |  |  |  | 0.12917 | 15 | 6 | [7 empty] | 11.6 | 8760 | 99.83% | 175.16 | 101616
|  | 2023-06-04 | 19:01 | 2023-06-04 | 19:58 | 0.039583 | 0 | 57 | [5 empty] | Tripped at Chainpal end on Directional Over Current B phase & E/F. IA=0.31kA, IB=10kA, IC=9.56kA..
|  | 2023-06-11 | 06:45 | 2023-06-11 | 08:25 | 0.069444 | 1 | 40 | [5 empty] | Tripped at Chainpal end on Directional Over Current Y phase & E/F. IA=0.503kA, IB=9.12kA, IC=8.25kA.. Fault due to Bird Nest at GLOBAL end.Line charged after clearing the nest.
|  | 2023-11-04 | 14:25 | 2023-11-04 | 14:54 | 0.020139 | 0 | 29 | [5 empty] | At Chainpal end: Zone 1, Dist- 5.25 km, Ir- 8.29 kA No Tripping at Global end. Tripping due to lightning
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
290 | 132kV Chainpal-TFL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7 | 8760 | 100% | 0 | 61320
291 | 132kV Chainpal-Talcher Traction |  |  |  |  | 0.020139 | 0 | 29 | [7 empty] | 0.448 | 8760 | 99.99% | 0.21653 | 3924.48
|  | 2023-11-04 | 14:25 | 2023-11-04 | 14:54 | 0.020139 | 0 | 29 | [5 empty] | At Chainpal end: Zone 1, Dist- 5.25 km, Ir- 8.29 kA No Tripping at Global end. Tripping due to lightning
292 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.5 | 8760 | 100% | 0 | 48180
293 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.5 | 8760 | 100% | 0 | 48180
294 | 132kV Chandaka-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.1 | 8760 | 100% | 0 | 158556
295 | 132kV Chandaka-Nimapara |  |  |  |  | 0.49444 | 0 | 50 | [7 empty] | 65 | 8760 | 99.99% | 54.1667 | 569400
|  | 2023-05-05 | 14:16 | 2023-05-05 | 16:28 | 0.091667 | 0 | 6 | [5 empty] | Local End:-Z1,Ia=1.136KA,Ib=1.346KA, Ic=1.174KA,D=44.82KM Remote End:-Z1,Ia=5.69KA,Ib=8.7KA, Ic=5.84KA,D=9.15KM. P/S availed from GSS,Kesura at 14:23 Hrs
|  | 2023-09-02 | 14:39 | 2023-09-02 | 15:55 | 0.052778 | 0 | 14 | [5 empty] | At Nimapara end:- Zone-1 , ABCN, Dist-43.92km, Ia=1.26kA, Ib=1.4kA, Ic=1.35kA At Chandaka end:- Zone-1, ABCN, Dist 9.584km, Ia=4.71kA, Ib=4.96kA, Ic=4.60kA. Tripped due to thunderstrom.
|  | 2023-06-08 | 17:21 | 09.06.23 | 1:25 | 0.35 | 0 | 30 | [5 empty] | At Nimapara end:-Z1, AN, Ia=2.503KA, Ib=0A, Ic=3.99A, D=19.28KM, A/R successful At Chandaka end:-Z1, AN, Ia=3.046KA, Ib= 276.3A, Ic=351.7A, D=31.86KM, A/R blocked [conductor snapped at loc. No.121]. conductor snapped at loc. No.121
296 | 132kV Chandaka-Ranasinghpur |  |  |  |  | 0.39028 | 13 | 29 | [7 empty] | 27.85 | 8760 | 99.85% | 375.5108 | 243966
|  | 2023-05-05 | 14:17 | 2023-05-05 | 16:06 | 0.075694 | 0 | 6 | [5 empty] | DP Relay operated at Z1,Distance-34.48 Km,IR-122.0 A,IY-196.8 A,IB-161.7 A. P/S availed from GSS,Kesura at 14:23 Hrs
|  | 2023-09-02 | 14:41 | 2023-09-02 | 15:48 | 0.046528 | 0 | 14 | [5 empty] | Relay operated at CDK end IR = 4.717KA, IY = 4.967KA, IB = 4.607KA at CDK end. Tripped due to thunderstrom.
|  | 2023-07-31 | 15:20 | 2023-07-31 | 21:46 | 0.26806 | 1 | 9 | [5 empty] | DP, Zone-1, Dist-956.4m, IR=582.1A, IY=551.1A, IB=589.3A. R-Ph CVT of 132kV Chandaka - Ranasinghpur feeder burst
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
297 | 132kV Chandaka- Mancheswar-B Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 8760 | 100% | 0 | 98112
298 | 132kV Chandaka B-Unit-8 |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.4 | 8760 | 100% | 0 | 99864
299 | 132kV Chandpur - Atri |  |  |  |  | 0.045139 | 0 | 31 | [7 empty] | 43.03 | 8760 | 99.99% | 22.2322 | 376942.8
|  | 2023-04-12 | 02:41 | 2023-04-12 | 03:46 | 0.045139 | 0 | 31 | [5 empty] | At Atri end:- Due to mal operation of Isolator 89A of 132kV side Auto- Trf-1 at Atri Grid. At Chandpur end:- no breaker operated.. Failed from Atri Grid end due to mal operation of Isolator 89A of 132Kv side Auto-Trf- 1 at Atri grid.
300 | 132kV Atri - Khurdha Ckt-II |  |  |  |  | 0.04375 | 0 | 44 | [7 empty] | 10.29 | 8760 | 99.99% | 7.546 | 90140.4
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:44 | 0.04375 | 0 | 44 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE
301 | 132kV Atri - Khurdha Ckt-I |  |  |  |  | 0.04375 | 0 | 44 | [7 empty] | 10.24 | 8760 | 99.99% | 7.5093 | 89702.4
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:44 | 0.04375 | 0 | 44 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE
302 | 132kV Atri-Shamuka |  |  |  |  | 0.057639 | 0 | 34 | [7 empty] | 68.94 | 8760 | 99.99% | 39.066 | 603914.4
|  | 2023-04-12 | 02:40 | 2023-04-12 | 04:03 | 0.057639 | 0 | 34 | [5 empty] | Breaker didn't trip at Shamuka end At Atri-Fault occurs at atri grid premises.
303 | 132kV Atri - Argul Ckt-I |  |  |  |  | 0.12083 | 14 | 54 | [7 empty] | 19.4 | 8760 | 99.83% | 289.06 | 169944
|  | 2023-06-04 | 21:35 | 2023-06-04 | 21:38 | 0.0020833 | 0 | 3 | [5 empty] | Incoming failure from Atri end
|  | 2023-06-16 | 19:24 | 2023-06-16 | 19:26 | 0.0013889 | 0 | 2 | [5 empty] | Incoming failure from Atri end
|  | 2023-06-16 | 10:42 | 2023-06-16 | 11:15 | 0.022917 | 0 | 33 | [5 empty] | Incoming failure from Atri end
|  | 2023-07-03 | 14:15 | 2023-07-03 | 14:30 | 0.010417 | 0 | 15 | [5 empty] | No relay indication
|  | 2023-09-03 | 18:50 | 2023-09-03 | 20:12 | 0.056944 | 1 | 22 | [5 empty] | B-ph to E, FAULT CURRENTS Ia=0kA, Ib=0kA, Ic=3.47kA, Zone-1, Dist-17.7 km
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:19 | 0.026389 | 0 | 38 | [5 empty] | Incomer failed
|  | 2023-06-16 | 19:24 | 2023-06-16 | 19:25 | 0.00069444 | 0 | 1 | [5 empty] | Incoming failure from Atri end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
304 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0.054167 | 13 | 18 | [7 empty] | 19.4 | 8760 | 99.85% | 258.02 | 169944
|  | 2023-06-16 | 10:42 | 2023-06-16 | 11:15 | 0.022917 | 0 | 33 | [5 empty] | Incoming failure from Atri end
|  | 2023-06-16 | 19:24 | 2023-06-16 | 19:26 | 0.0013889 | 0 | 2 | [5 empty] | Incoming failure from Atri end
|  | 2023-07-03 | 14:15 | 2023-07-03 | 14:30 | 0.010417 | 0 | 15 | [5 empty] | No relay indication
|  | 2023-09-03 | 18:50 | 2023-09-03 | 19:17 | 0.01875 | 0 | 27 | [5 empty] | B-ph to E, FAULT CURRENTS Ia=0.07kA, Ib=0.15kA, Ic=3.37kA, Zone-1, Dist-36.8km
|  | 2023-06-16 | 19:24 | 2023-06-16 | 19:25 | 0.00069444 | 0 | 1 | [5 empty] | Incoming failure from Atri end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
305 | 132kV Atri - Banki |  |  |  |  | 0.11319 | 14 | 9 | [7 empty] | 20.5 | 8760 | 99.84% | 290.075 | 179580
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:44 | 0.04375 | 1 | 3 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE
|  | 2023-06-16 | 10:41 | 2023-06-16 | 11:15 | 0.023611 | 0 | 34 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE. 132KV NUAPATNA WAS AVAILING POWER FROM BANKI END.HENCE POWER COULD NOT BE AVAILED FROM NUAPTNA END AND BANKI GRID WAS UNDER COMPLETE POWER FAILURE DURINGTHIS PERIOD.
|  | 2023-06-16 | 19:24 | 2023-06-16 | 19:25 | 0.00069444 | 0 | 1 | [5 empty] | Incoming failure from Atri end
|  | 2023-04-12 | 02:41 | 2023-04-12 | 03:46 | 0.045139 | 0 | 31 | [5 empty] | At Atri end:- Due to mal operation of Isolator 89A of 132kV side Auto- Trf-1 at Atri Grid. At Chandpur end:- no breaker operated.. Failed from Atri Grid end due to mal operation of Isolator 89A of 132Kv side Auto-Trf- 1 at Atri grid.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
306 | 132kV Khurdha-Kaipadar RTSS |  |  |  |  | 0.082639 | 13 | 40 | [7 empty] | 11.26 | 8760 | 99.84% | 153.8867 | 98637.6
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:44 | 0.04375 | 0 | 44 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE
|  | 2023-06-18 | 22:55 | 2023-06-18 | 23:02 | 0.0048611 | 0 | 7 | [5 empty] | S/F 40. Bad Weather. M/S failed from MSAL end
|  | 2023-06-19 | 00:17 | 2023-06-19 | 00:46 | 0.020139 | 0 | 29 | [5 empty] | Source Failure. Bad Weather. M/S failed from Mendhasal end
|  | 2023-11-15 | 09:10 | 2023-11-15 | 09:30 | 0.013889 | 0 | 20 | [5 empty] | At Atri end: CKT I: R-N, Zone 2, Dist- 12.7 km, Ir- 3.266 kA; CKT II: R-N, Zone 2, Dist-9.334 km, Ir- 3.419 kA. Grid pulled out due to bursting of 132kV LA in R-Ph of TRF I
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
307 | 132kV Chandikhol-Kendrapada |  |  |  |  | 0.069444 | 13 | 3 | [7 empty] | 31.2 | 8760 | 99.85% | 407.16 | 273312
|  | 2023-06-22 | 13:23 | 2023-06-22 | 14:07 | 0.030556 | 0 | 16 | [5 empty] | At Kendrapara end:- TRIPPED ON B/U E/F WITH M/R, Ir=2.525KA, Iy=8.677A, Ib=7.987A At Chandikhol end:-No tripping. LINE WAS IDLE CHARGED FROM CHANDIKHOLE END.
|  | 2023-11-23 | 17:13 | 2023-11-23 | 17:45 | 0.022222 | 0 | 23 | [5 empty] | At Kendrapara end: Zone 1, Dist- 17.37 km, Ir- 264.7A, Iy- 2.6kA, Ib- 126.9A No Tripping at Chandikhol end.. Incomer power supply was availed from Jajpur Road end at 17:36 Hrs
|  | 2023-04-20 | 12:52 | 2023-04-20 | 13:16 | 0.016667 | 0 | 24 | [5 empty] | KENDRAPARA End TRIPPED ON DP, ZONE-1, DIST.=17.95KM, Ir=151A, Iy=212.1A, Ib=2.384KA, No tripping at Chandikhole end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
308 | 132kV Chatrapur-Balugaon |  |  |  |  | 0.19583 | 12 | 55 | [7 empty] | 53.79 | 8760 | 99.85% | 694.7875 | 471200.4
|  | 2023-04-29 | 14:24 | 2023-04-29 | 14:28 | 0.0027778 | 0 | 4 | [5 empty] | At Chhatrapur end:- Back-up relay operated with indication: R-ph O/C, E/F, IR=0.56kA, IY=0.05kA, IB=0.09kA At Balugaon end:- breaker H/T. I/C P/S failure from chhatrapur
|  | 2023-04-29 | 14:33 | 2023-04-29 | 18:29 | 0.16389 | 0 | 9 | [5 empty] | At Chhatrapur end:- Zone-1, Dist-37.58km, O/C, IR=2.176kA, IY=184A, IB=413.1A At Balugaon end:- DP relay operated with Zone-I indication, IR=3A,IY=3A,IB=4A. Balugaon Availed power suppy from Chandpur end at 14:42Hrs
|  | 2023-06-16 | 10:41 | 2023-06-16 | 10:53 | 0.0083333 | 0 | 12 | [5 empty] | I/C P/S failure due to Under voltage..
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:33 | 0.020833 | 0 | 30 | [5 empty] | At Chatrapur end. Zone 4, Dist- 0.354m, Y-N, Iy- 795.3A No tripping at Balugaon end.. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
309 | 132kV Chatrapur-Ganjam |  |  |  |  | 0.072917 | 13 | 33 | [7 empty] | 12.6 | 8760 | 99.85% | 170.73 | 110376
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:27 | 0.016667 | 0 | 24 | [5 empty] | . Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:26 | 0.015972 | 0 | 11 | [5 empty] | Auto TRF II: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 2.14 kA, Iy- 2.18 kA, Ib- 2.12 kA Auto TRF III: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 0.80 kA, Iy- 0.83 kA, Ib- 0.81 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
|  | 2023-11-06 | 22:28 | 2023-11-06 | 23:10 | 0.029167 | 0 | 42 | [5 empty] | At Chhatrapur end: B-N, Zone 1, Dist- 9.5 km, Ib- 4.571 kA No tripping at Ganjam end.. Weather condition: Heavy rainfall and lightening
|  | 2023-04-22 | 00:55 | 22.04.2023 | 1:06 | 0.0076389 | 0 | 11 | [5 empty] | Z-1 R-G DIST -1.1 KM TRIPPED AT CHATRAPUR END. WEATHER CONDITION- RAIN AND WIND STORM
|  | 2023-06-16 | 10:42 | 2023-06-16 | 10:47 | 0.0034722 | 0 | 5 | [5 empty] | Source failure.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
310 | 132kV Chatrapur-IRE-I |  |  |  |  | 0.017361 | 0 | 25 | [7 empty] | 5.8 | 8760 | 100% | 2.4167 | 50808
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:28 | 0.017361 | 0 | 25 | [5 empty] | Tripped due to incoming failure at 132/33KV GSS Chatrapur. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
311 | 132kV Chatrapur-IRE-II |  |  |  |  | 0.017361 | 0 | 25 | [7 empty] | 5.8 | 8760 | 100% | 2.4167 | 50808
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:28 | 0.017361 | 0 | 25 | [5 empty] | Tripped due to incoming failure at 132/33KV GSS Chatrapur. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
312 | 132kV Chatrapur-Rambha RTSS |  |  |  |  | 0.47708 | 23 | 27 | [7 empty] | 28.5 | 8760 | 99.73% | 668.325 | 249660
|  | 2023-07-11 | 10:59 | 2023-07-11 | 11:09 | 0.0069444 | 0 | 10 | [5 empty] | (AG-T), Zone-1, Dist-22.54km, IA=2585A, IB=35A, IG=2618A. Weather Condition-Very heavy rain,lightening and thunderstrom.
|  | 2023-04-01 | 12:26 | 2023-04-01 | 23:18 | 0.45278 | 10 | 52 | [5 empty] | Tripped on Y-G, Z-1,Dist- 18.48KM,Ir=6A,Iy=3.08KA,Ig=3.081KA.[Earthwire snapped from location no-82 to 86 Weather condition; Heavy rain fall,lightening and Thunderstorm.].
|  | 2023-06-29 | 09:10 | 2023-06-29 | 09:12 | 0.0013889 | 0 | 2 | [5 empty] | Tripped on O/C(R,Y-Ph)with M/R,Ir=0.95KA,Iy=0.95ka.
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:26 | 0.015972 | 0 | 23 | [5 empty] | . Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
313 | 132kV Chhend-Adhunik Metalics |  |  |  |  | 0.048611 | 1 | 9 | [7 empty] | 24.04 | 8760 | 99.99% | 27.646 | 210590.4
|  | 2023-08-16 | 14:49 | 2023-08-16 | 15:16 | 0.01875 | 0 | 27 | [5 empty] | At Chhend end:- In DP-Zone-2, Loc-13.58km, IL1-304.2A, IL2-341.3A, IL3-4.610kA. Heavy Lightening ,Windy, Rain
|  | 2023-10-12 | 19:00 | 2023-10-12 | 19:43 | 0.029861 | 0 | 42 | [5 empty] | Zone 2, Dist- 16.43 km, Ir- 5.153 kA, Iy- 3.960A, Ib- 5.027 kA. Heavy Spark observed at their end. L/C issued from 20:03 hrs to 23:49 hrs
314 | 132kV Chhend-Nuagaon RTSS |  |  |  |  | 0.14653 | 15 | 31 | [7 empty] | 34.6 | 8760 | 99.82% | 536.8767 | 303096
|  | 2023-07-28 | 14:13 | 2023-07-28 | 17:32 | 0.13819 | 3 | 19 | [5 empty] | At Chhend end:- Tripped on O/C, IL1=0.22kA, IL2=0.22kA. Heavy spark obseved at Rph CT stud clamp.
|  | 2023-08-16 | 14:44 | 2023-08-16 | 14:53 | 0.00625 | 0 | 9 | [5 empty] | At Chhend end:- In DP-Zone-1, Loc-13.87km, IL1-26A, IL2-4414A, IN- 4.420kA. Heavy Lightening ,Windy, Rain
|  | 2023-10-09 | 04:46 | 2023-10-09 | 04:49 | 0.0020833 | 0 | 3 | [5 empty] | Zone 2, Dist-34.10 km, Ir-2.338 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
315 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
316 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
317 | 132kV Choudwar-Bidanasi |  |  |  |  | 0.13889 | 12 | 45 | [7 empty] | 15.41 | 8760 | 99.85% | 196.4775 | 134991.6
|  | 2023-06-17 | 14:50 | 2023-06-17 | 17:46 | 0.12222 | 0 | 21 | [5 empty] | Power supply failed at Choudwar GSS. B- PH SI to main bus jumper snapped
|  | 2023-10-25 | 05:28 | 2023-10-25 | 05:34 | 0.0041667 | 0 | 6 | [5 empty] | Zone 1, Dist- 5.8 km, Ir-7.07 kA. -
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:29 | 0.0076389 | 0 | 11 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
318 | 132kV Choudwar-Kendrapara Road Traction |  |  |  |  | 0.024306 | 12 | 34 | [7 empty] | 4.6 | 8760 | 99.86% | 57.8067 | 40296
|  | 2023-06-17 | 14:50 | 2023-06-17 | 15:00 | 0.0069444 | 0 | 10 | [5 empty] | Power supply failed at Choudwar GSS. B- PH SI to main bus jumper snapped
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:29 | 0.0076389 | 0 | 11 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
|  | 2023-12-05 | 11:07 | 2023-12-05 | 11:14 | 0.0048611 | 0 | 6 | [5 empty] | Incomer failure from source end. No tripping at Salipur end.. Due to tripping of 132kV Choudwar- Bidanasi Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
319 | 132kV Cuttack-Jagatsinghpur |  |  |  |  | 1899-12-31 03:00 | 14 | 9 | [7 empty] | 34.71 | 8760 | 99.84% | 491.1465 | 304059.6
|  | 2023-08-16 | 22:40 | 2023-08-16 | 23:36 | 0.038889 | 0 | 9 | [5 empty] | Zone-1, dist- 6.408km, Ia=525A, Ib=6.304kA, Ic= 264.1A. Weather: Heavy Rain fall and lightning
|  | 2023-10-15 | 21:18 | 2023-10-15 | 21:41 | 0.015972 | 0 | 23 | [5 empty] | At Cuttack end: O/C in Y-Phase & E/F (B/C Relay), Iy- 1.9 kA, Ic = 336A( DP Not Opearted) TRF I: O/C in Y Ph, Iy- 0.42 kA TRF II: O/C in RYB Ph, Ir- 1.01 kA, Iy- 0.69 kA, Ib- 0.96 kA No relay operated at Jagatsinghpur end.. At 21:40Hrs Jagatsinghpur GSS availed 132kV P/S from Cuttack end. At 21:45 Hrs 33kV side of TRF-I was charged & At 23:15 Hrs 132kV Side of TRF II was charged & At 23:17 Hrs 33kV Side of TRF II was charged
|  | 2023-11-10 | 22:52 | 2023-11-10 | 23:20 | 0.019444 | 0 | 22 | [5 empty] | No Tripping at Jagatsinghpur end. At Cuttack end: O/C & B/C, Ir- 0.43 kA, Ib- 1.98kA, Ic- 0.26kA DP:- Dist- 52.4 km, Ir-527A, Iy- 1.979 kA, Ib- 341A, Zone 3. At 23:00Hrs Jagatsinghpur GSS availed 132kV P/S from Tirtol end keeping Cuttack-Jagatsinghpur breaker in off condition. At 23:20Hrs 132kV Cuttack-JagatsinghpurLine charged from Cuttack end.
|  | 2023-10-20 | 17:54 | 21.10.23 | 13:54 | 0.83333 | 0 | 5 | [5 empty] | At Cuttack end: R-N, Zone 1, Dist- 26.48 km, Ir- 3.188 kA At Jagasinghpur end: Ir- 0.46 kA, Iy- 0.72 kA, Ib- 0.58 kA, Dist- 5.5 km, Zone 1 At 18:23 Hrs the said Line charged from Cuttack end, but again tripped. At Cuttack end: SOTF, Zone 1, Dist- 25.49 km, Ir- 2.833 kA. At 18:00 Hrs Jagatsinghpur availed 132kV P/S from Tirtol end. At 13:54 Hrs 132kV Cuttack-Jagatsinghpur Line Charged. At 13:57 Hrs Jagatsinghpur availed 132kV P/S from Cuttack end & 132kV Tirtol- Jagatsinghpur Line was H/T from Jagatsinghpur end.
|  | 2023-10-29 | 03:55 | 2023-10-29 | 04:23 | 0.019444 | 0 | 8 | [5 empty] | At Cuttack end: O/C & B/C, Ir- 0.44 kA, Iy- 2.02 kA, Ib- 0.27 kA, Dist- 51.99 km, Zone 3 20 MVA TRF-I:- O/C in RYB phase, Ir- 0.46 kA, Iy- 0.46 kA, Ib- 0.46 kA 20 MVA TRF-II:- O/C in RYB phase, Ir- 0.96 kA, Iy- 0.96 kA, Ib- 0.96 kA. At 04:02 Hrs Jagatsinghpur GSS availed 132kV P/S from Tirtol end. At 04:05 Hrs 20 MVA TRF-I & 20 MVA TRF-II were charged one after another.At 04:23 Hrs 132kV Cuttack- Jagatsinghpur Line charged & stood ok.
|  | 2023-05-03 | 16:35 | 2023-05-03 | 18:52 | 0.095139 | 0 | 30 | [5 empty] | 132kV Ctc-Jspur Line tripped on DP relay from both end with following relay indication:- Relay Indication at JSPUR GSS Zone-1, Ia= 8A, Ib = 7A,Ic= 1318.4 A Distance = 13.418KM, Fault Time = 88ms Relay Indication at CTC GSS Active Group 1, Zone-1, Started Phase :- BN, Tripped Phase:- ABC Ia= 565.1A, Ib = 4.748kA, Ic= 392.2 A Distance = 13.46KM, Fault Duration = 73.38ms, Relay trip time = 80ms. Jagatsinghpur Gss was availing 132kV P/S from Tirtol end at 16:45Hrs.
|  | 2023-06-04 | 20:01 | 2023-06-04 | 20:24 | 0.015972 | 0 | 23 | [5 empty] | 132kV p/s failed from both Cuttack & Tirtol GSS with heavy spark inside Jagatsinghpur GSS. No Breaker tripped at Jagatsinghpur end. At Cuttack end:- Zone-2, Tripped on RYB, Ia= 543.5A, Ib = 2.306kA, Ic= 350.2 A, Dist-42.08km. Jagatsinghpur GSS availed 132kV P/S from Cuttack end at 20:24 .
|  | 2023-07-31 | 17:29 | 2023-07-31 | 19:34 | 0.086806 | 0 | 9 | [5 empty] | At Jagatsinghpur end:- DP Rlay operated. Zone-1, Distance-1Km, Ia-0.71kA, Ib-0.66kA, Ic-0.68kA At Cuttack end:- Zone-2, Tripped on RYB, Ia= 3.20kA, Ib = 0.695kA, Ic= 3.167kA, Distance=37.47km. Weather- Heavy rainfall & Lightening. 132kV Power supply failed from Cuttack end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
320 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.26 | 8760 | 100% | 0 | 177477.6
321 | 132kV Dhenkanal-Khuntuni-Grid Steel -ICCL |  |  |  |  | 0.35625 | 14 | 9 | [7 empty] | 39.18 | 8760 | 99.84% | 554.397 | 343216.8
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
|  | 2023-06-04 | 20:24 | 2023-06-04 | 20:47 | 0.015972 | 0 | 23 | [5 empty] | Source failure. LC taken by MRDL grid to attend the B/D. 132KV DKL-MRDL line was B/D. So no power supply to the station. Fault occured at Meramundali grid ,Power failure from 132KV DKL fdr . As the said period the 132 kV ICCL Fdr was in H/T condition at ICCL end, At 20:47 hrs 132KV supply availed from ICCL end.
|  | 2023-06-12 | 12:20 | 2023-06-12 | 12:36 | 0.011111 | 0 | 16 | [5 empty] | At Dhenkanal end:- B/U relay operated, Ia=432.7A, Ib=462.4A, Ic=431.1A. The line test charged & it stood OK.
|  | 2023-06-20 | 8:53 | 2023-06-20 | 09:03 | 0.0069444 | 0 | 10 | [5 empty] | At Dhenkanal end:-B/U relay operated, Ia=87.99A, Ib=109.1A, Ic=775.1A, In=604.1A. The line test charged & it tripped immediately.The concerned authority was informed for line patrolling.
|  | 2023-06-20 | 09:03 | 2023-06-20 | 12:16 | 0.13403 | 0 | 10 | [5 empty] | At Dhenkanal end:- B/U relay operated, Ia=93A, Ib=101A, Ic=982A, In=791A. After thorough patrolling by the concerned authority the line charged & it stood OK.
|  | 2023-06-22 | 11:59 | 2023-06-22 | 12:55 | 0.038889 | 0 | 10 | [5 empty] | At Dhenkanal end:- DP relay operated, Z-2 Dist.=21.10km, Ia=3.118KA, Ib=301.2A, Ic=3.2KA At Khuntuni end:- DP relay operated, Z-1, Ia=300A, Ib=300A, Ic=300A. The line test charged after getting confirmation from concerned authority & it stood OK.
|  | 2023-10-03 | 16:40 | 2023-10-03 | 17:25 | 0.03125 | 0 | 12 | [5 empty] | Power supply fail. P/S failure as 132kV Dhenkanal- Meramundali & 132kV Dhenkanal- Khajuriakata-Nuapatna Line tripped
|  | 2023-10-26 | 16:44 | 2023-10-26 | 16:51 | 0.0048611 | 0 | 7 | [5 empty] | E/F and 86 A & 86 B Operated.
|  | 2023-10-27 | 23:57 | 28.10.23 | 0:09 | 0.0083333 | 0 | 12 | [5 empty] | At Khuntuni end:- E/F and 86 A & 86 B Operated
|  | 2023-12-11 | 13:21 | 2023-12-11 | 13:32 | 0.0076389 | 0 | 11 | [5 empty] | DP operated, Zone-1
|  | 2023-06-12 | 11:42 | 2023-06-12 | 13:55 | 0.092361 | 0 | 11 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 11:53
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
322 | 132kV Khuntuni- Shree Cement |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.45 | 8760 | 100% | 0 | 56502
323 | 132kV Dhenkanal-Joranda RTSS |  |  |  |  | 1899-12-31 01:02 | 20 | 22 | [7 empty] | 19.35 | 8760 | 99.77% | 394.095 | 169506
|  | 2023-04-04 | 16:06 | 2023-04-04 | 16:28 | 0.015278 | 0 | 22 | [5 empty] | DP relay operated with indication: B_N,Z_2,Ib=2.36 kA,dist=17.29 kM (weather condition was not good). Line test charged after weather condition was normal & it stood OK.
|  | 2023-05-19 | 17:38 | 2023-05-19 | 17:46 | 0.0055556 | 0 | 8 | [5 empty] | DP Relay operated with indication: Z-1, Dist- 11.58kM, IA=31.65A, IC=2.673KA. The line test charged after weather condition is good & it stood OK.
|  | 2023-06-04 | 20:24 | 2023-06-04 | 20:39 | 0.010417 | 0 | 15 | [5 empty] | Power supply failure. LC taken by MRDL grid to attend the B/D. 132KV DKL-MRDL line was B/D. So no power supply to the station. Fault occured at Meramundali grid ,Power failure from 132KV DKL fdr . As the said period the 132 kV ICCL Fdr was in H/T condition at ICCL end, At 20:47 hrs 132KV supply availed from ICCL end.
|  | 2023-06-05 | 12:33 | 2023-06-05 | 12:42 | 0.00625 | 0 | 9 | [5 empty] | Power supply failure. 132KV DKL-MRDL line was B/D. So no power supply to the station.
|  | 2023-06-05 | 14:54 | 2023-06-05 | 15:04 | 0.0069444 | 0 | 10 | [5 empty] | Power supply failure. 132KV DKL-MRDL line was B/D. So no power supply to the station.
|  | 2023-06-18 | 23:01 | 2023-06-18 | 23:23 | 0.015278 | 0 | 22 | [5 empty] | DP relay operated, Z-2, Dist.=17.57km, Ic=2.7KA. Line test charged & stood OK
|  | 2023-06-29 | 17:20 | 2023-06-29 | 18:38 | 0.054167 | 1 | 18 | [5 empty] | DP relay operated, Z-2, Dist.=16.97km, Ic=2.87KA [one insulator disc punctured]. After thorough patrolling one insulator disc punctured found. The line charged & it stood OK.
|  | 2023-06-29 | 14:40 | 2023-06-29 | 14:52 | 0.0083333 | 0 | 12 | [5 empty] | DP relay operated, Z-2, Dist.=17.35km, Ic=2.827KA. Line test charged & stood OK
|  | 2023-10-03 | 16:40 | 2023-10-03 | 16:43 | 0.69653 | 0 | 3 | [5 empty] | Power supply fail. P/S failure as 132kV Dhenkanal- Meramundali & 132kV Dhenkanal- Khajuriakata-Nuapatna Line tripped
|  | 2023-10-16 | 07:56 | 2023-10-16 | 13:01 | 0.21181 | 5 | 5 | [5 empty] | E/F. Earth wire snapped between Loc No. 46 to 50
|  | 02.11.2023 | 09:15 | 02.11.2023 | 09:21 | 0.0041667 | 0 | 6 | [5 empty] | Zone 1, Dist- 4.467 km, Ib- 3.84 kA. -
|  | 2024-03-25 | 23:11 | 2024-03-25 | 23:23 | 0.0083333 | 0 | 12 | [5 empty] | Zone 2, Dist- 16.01km, Ir- 2.838kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
324 | 132kV Digapahandi-Chikiti ckt - I |  |  |  |  | 0.020833 | 12 | 30 | [7 empty] | 29.1 | 8760 | 99.86% | 363.75 | 254916
|  | 2023-09-05 | 14:23 | 2023-09-05 | 14:28 | 0.0034722 | 0 | 5 | [5 empty] | Source failure from Digapahandi end.
|  | 2024-03-31 | 08:20 | 2024-03-31 | 08:26 | 0.0041667 | 0 | 6 | [5 empty] | Supply failure from Digapahandi end. -
|  | 2023-05-24 | 13:58 | 2023-05-24 | 14:10 | 0.0083333 | 0 | 12 | [5 empty] | Digapahandi end. DP relay optd. Zone -1, AGT, Dist.-4.0KM, Fault current- Ia=302A, Ib-204A, Ic- 355A, Ig=857A Berhampur end-Distance relay optd. Rph to N trip. Distance- 22.10km, Ir=2.732kamp . MR optd.. Weather condition cloudy
|  | 2023-05-30 | 17:30 | 2023-05-30 | 17:37 | 0.0048611 | 0 | 7 | [5 empty] | Digapahandi end. DP relay optd. Zone - 1,AGT, Dist.-2.82KM, Fault current- Ia=476A, Ib-300A, Ic-526A, Ig=1292A. Rain & heavy thunderstoms at Digapahandi end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
325 | 132kV Digapahandi-Chikiti ckt - II |  |  |  |  | 0.020833 | 12 | 30 | [7 empty] | 29.1 | 8760 | 99.86% | 363.75 | 254916
|  | 2023-09-05 | 14:23 | 2023-09-05 | 14:28 | 0.0034722 | 0 | 5 | [5 empty] | Source failure from Digapahandi end.
|  | 2024-03-31 | 08:20 | 2024-03-31 | 08:26 | 0.0041667 | 0 | 6 | [5 empty] | Supply failure from Digapahandi end. -
|  | 2023-05-24 | 13:58 | 2023-05-24 | 14:10 | 0.0083333 | 0 | 12 | [5 empty] | Digapahandi end. DP relay optd. Zone -1, AGT, Dist.-4.0KM, Fault current- Ia=302A, Ib-204A, Ic- 355A, Ig=857A Berhampur end-Distance relay optd. Rph to N trip. Distance- 22.10km, Ir=2.732kamp . MR optd.. Weather condition cloudy
|  | 2023-05-30 | 17:30 | 2023-05-30 | 17:37 | 0.0048611 | 0 | 7 | [5 empty] | Digapahandi end. DP relay optd. Zone - 1,AGT, Dist.-2.82KM, Fault current- Ia=476A, Ib-300A, Ic-526A, Ig=1292A. Rain & heavy thunderstoms at Digapahandi end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
326 | 132kV Duburi-BC Mohanty |  |  |  |  | 0.36806 | 20 | 50 | [7 empty] | 11.97 | 8760 | 99.76% | 249.375 | 104857.2
|  | 2023-09-23 | 17:13 | 2023-09-23 | 17:21 | 0.0055556 | 0 | 8 | [5 empty] | B/U. Due to tripping of 132KV Bamnipal fdr with high
|  | 2023-08-08 | 13:42 | 2023-08-08 | 13:55 | 0.0090278 | 0 | 13 | [5 empty] | DP operated. Puncture of 132kV LA at Daitari GSS
|  | 2024-03-30 | 14:15 | 2024-03-30 | 22:44 | 0.35347 | 8 | 29 | [5 empty] | At Duburi end: B-N, Zone 1, Dist- 40.15m, Ib- 12.88kA No tripping at B C Mohanty end. B phase insulator failure at Tower Loc. No. 1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
327 | 132kV BCMohanty-Daitari |  |  |  |  | 0.39653 | 21 | 31 | [7 empty] | 21.224 | 8760 | 99.75% | 456.6697 | 185922.24
|  | 2023-09-23 | 17:13 | 2023-09-23 | 17:21 | 0.0055556 | 0 | 8 | [5 empty] | B/U. Due to tripping of 132KV Bamnipal fdr with high
|  | 2024-03-29 | 11:22 | 2024-03-29 | 12:03 | 0.028472 | 0 | 41 | [5 empty] | Ir- 0.581kA, Iy- 0.470kA, Ib- 2.99kA. B-ph LA of 132kV Daitari-Bamnipal Feeder punctured-
|  | 2023-08-08 | 13:42 | 2023-08-08 | 13:55 | 0.0090278 | 0 | 13 | [5 empty] | DP operated. Puncture of 132kV LA at Daitari GSS
|  | 2024-03-30 | 14:15 | 2024-03-30 | 22:44 | 0.35347 | 8 | 29 | [5 empty] | At Duburi end: B-N, Zone 1, Dist- 40.15m, Ib- 12.88kA No tripping at B C Mohanty end. B phase insulator failure at Tower Loc. No. 1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
328 | 132kV BCMohanty-Tomka (T) |  |  |  |  | 0.43194 | 28 | 22 | [7 empty] | 11.46 | 8760 | 99.68% | 325.082 | 100389.6
|  | 2023-11-15 | 09:55 | 2023-11-15 | 10:00 | 0.0034722 | 0 | 5 | [5 empty] | O/C
|  | 2023-12-13 | 11:40 | 2023-12-13 | 11:45 | 0.0034722 | 6 | 5 | [5 empty] | O/C
|  | 2023-06-07 | 13:20 | 2023-06-07 | 13:42 | 0.015278 | 0 | 22 | [5 empty] | O/C.
|  | 2023-06-30 | 20:22 | 2023-06-30 | 20:49 | 0.01875 | 0 | 27 | [5 empty] | E/F.
|  | 2024-03-29 | 11:22 | 2024-03-29 | 12:03 | 0.028472 | 0 | 41 | [5 empty] | Ir- 0.581kA, Iy- 0.470kA, Ib- 2.99kA. B-ph LA of 132kV Daitari-Bamnipal Feeder punctured-
|  | 2023-08-08 | 13:42 | 2023-08-08 | 13:55 | 0.0090278 | 0 | 13 | [5 empty] | DP operated. Puncture of 132kV LA at Daitari GSS
|  | 2024-03-30 | 14:15 | 2024-03-30 | 22:44 | 0.35347 | 8 | 29 | [5 empty] | At Duburi end: B-N, Zone 1, Dist- 40.15m, Ib- 12.88kA No tripping at B C Mohanty end. B phase insulator failure at Tower Loc. No. 1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
329 | 132kV Daitari-Bamnipal(Tisco) |  |  |  |  | 0.65417 | 27 | 42 | [7 empty] | 10.227 | 8760 | 99.68% | 283.2879 | 89588.52
|  | 2024-03-29 | 11:22 | 2024-03-29 | 18:22 | 0.29167 | 7 | 0 | [5 empty] | Ir- 0.429kA, Iy- 0.53kA, Ib- 3.05kA. B-ph LA of 132kV Daitari-Bamnipal Feeder punctured-
|  | 2023-08-08 | 13:42 | 2023-08-08 | 13:55 | 0.0090278 | 0 | 13 | [5 empty] | DP operated. Puncture of 132kV LA at Daitari GSS
|  | 2024-03-30 | 14:15 | 2024-03-30 | 22:44 | 0.35347 | 8 | 29 | [5 empty] | At Duburi end: B-N, Zone 1, Dist- 40.15m, Ib- 12.88kA No tripping at B C Mohanty end. B phase insulator failure at Tower Loc. No. 1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
330 | 132kV Duburi-Jajpur Road Ckt-I |  |  |  |  | 0.04375 | 12 | 55 | [7 empty] | 13.2 | 8760 | 99.85% | 170.5 | 115632
|  | 2023-09-25 | 11:37 | 2023-09-25 | 11:46 | 0.00625 | 0 | 9 | [5 empty] | Source failure from Duburi end
|  | 2023-07-17 | 13:56 | 2023-07-17 | 14:10 | 0.0097222 | 0 | 6 | [5 empty] | Tripped on Backup relay.
|  | 2023-04-22 | 22:23 | 2023-04-22 | 22:33 | 0.0069444 | 0 | 10 | [5 empty] | At Jajpur Road end: DP RELAY OPERATED, FAULT CURRENT: IA=3.668KA,IB=206.3A,IC=122.2A;F. VOLTAGE: VAN=122.2KV,VBN=191.6KV,VCN=67.4KV; F. ZONE-IV; FAULT RESISTANCE=33.85Ω; FAULT LOCATION=9.127 KM, No tripping at Duburi end.
|  | 2023-06-07 | 09:58 | 2023-06-07 | 10:28 | 0.020833 | 0 | 30 | [5 empty] | DP RELAY OPERATED, FAULT CURRENT: IA=3.710KA,IB=246.8A,IC=591.5KA;F. VOLTAGE: VAN=123.2KV,VBN=189.5KV,VCN=70.43KV; F. ZONE-IV; FAULT RESISTANCE=34.18mΩ; FAULT LOCATION=11.03KM. After getting clerance from SI of GSS the line was charged
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
331 | 132kV Duburi-Jajpur Road Ckt-II |  |  |  |  | 0.038194 | 12 | 55 | [7 empty] | 13.2 | 8760 | 99.85% | 170.5 | 115632
|  | 2023-09-25 | 11:37 | 2023-09-25 | 11:46 | 0.00625 | 0 | 9 | [5 empty] | Source failure from Duburi end
|  | 2023-07-17 | 13:56 | 2023-07-17 | 14:02 | 0.0041667 | 0 | 6 | [5 empty] | Tripped on Backup relay.
|  | 2023-04-22 | 22:23 | 2023-04-22 | 22:33 | 0.0069444 | 0 | 10 | [5 empty] | At Jajpur Road end: DP RELAY OPERATED, FAULT CURRENT: IA=3.668KA,IB=206.3A,IC=122.2A;F. VOLTAGE: VAN=122.2KV,VBN=191.6KV,VCN=67.4KV; F. ZONE-IV; FAULT RESISTANCE=33.85Ω; FAULT LOCATION=9.127 KM, No tripping at Duburi end.
|  | 2023-06-07 | 09:58 | 2023-06-07 | 10:28 | 0.020833 | 0 | 30 | [5 empty] | DP RELAY OPERATED, FAULT CURRENT: IA=3.710KA,IB=246.8A,IC=591.5KA;F. VOLTAGE: VAN=123.2KV,VBN=189.5KV,VCN=70.43KV; F. ZONE-IV; FAULT RESISTANCE=34.18mΩ; FAULT LOCATION=11.03KM. After getting clerance from SI of GSS the line was charged
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
332 | 132kV Duburi-Jakhapura RTSS |  |  |  |  | 0.11389 | 14 | 44 | [7 empty] | 12.45 | 8760 | 99.83% | 183.43 | 109062
|  | 2023-07-09 | 07:47 | 2023-07-09 | 07:56 | 0.00625 | 0 | 9 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
|  | 2023-07-09 | 16:39 | 2023-07-09 | 16:53 | 0.0097222 | 0 | 14 | [5 empty] | Tripped on Backup relay. 33kV Sargipali feeder tripped at 20:51 hrs. 33kV side of 132/33kV TRF-I tripped on E/F & M/T operated due to 33kV Sargipali feeder's fault. Si3mkVultsaidneeouf s1ly3,2d/3u3ektVo Simultaneously, there was a heavy spark at 132kV S/Y. Therefore, the said feeeders H/T. After physical inspection of S/Y and isolating the faulty
|  | 2023-07-11 | 09:45 | 2023-07-11 | 09:53 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on Backup relay.
|  | 2023-08-08 | 13:42 | 2023-08-08 | 13:55 | 0.0090278 | 0 | 13 | [5 empty] | At Duburi end:- DIRECTIONAL OC/EF RELAY, Start Phase -A B C N, Tripped Phase-N, IA=3.128kA, IB=427A, IC=712.2A, VAB=118.4KV, VBC=134.5KV, VCA=120.7KV, VAN=63.27KV, VBN=76.05KV, VCN=76.14KV, FAULT DURATION=430ms, CB Operated Time=5ms, Relay Trip Time=420ms. Puncture of 132kV LA at Daitari GSS
|  | 2023-08-22 | 18:41 | 2023-08-22 | 19:50 | 0.047917 | 1 | 9 | [5 empty] | At Duburi end:- DISTANCE RELAY, Start Phase -A B C N, Tripped Phase-A B C, ZONE-1, FAULT LOCATION=9.043KM, IA=4.519KA, IB=4.903KA, IC=4.710KA, VAN=19.87KV, VBN=19.79KV, VCN=21.04KV At RTSS end:- DISTANCE RELAY, Start Phase -A B C N, Tripped Phase-A B C, ZONE-1, FAULT RESISTANCE =28.32KM, IA=2.39KA, IB=2.47KA, IC=2.43KA. -
|  | 2023-09-27 | 12:31 | 2023-09-27 | 12:43 | 0.0083333 | 0 | 12 | [5 empty] | At Duburi end:- Directional O/C & E/F Protection, Start Phase - A B, Tripped Phase-A, Active grp-1, IA=299.7A, IB=297A, VAB=132.7kV, VBN=133.7kV, VCA=135kV, VAN=77.35kV, VBN=76.54kV, VCN=77.87kV.
|  | 2024-03-19 | 02:03 | 2024-03-19 | 02:42 | 0.027083 | 0 | 39 | [5 empty] | R-N, Zone 1, Dist- 5.271km, Ir- 9.253kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
333 | 132kV JSWCL- Mesco |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.464 | 8760 | 100% | 0 | 47864.64
334 | 132kV Duburi-JSWCL |  |  |  |  | 0.021528 | 0 | 31 | [7 empty] | 9.26 | 8760 | 99.99% | 4.7843 | 81117.6
|  | 2024-03-19 | 02:12 | 2024-03-19 | 02:43 | 0.021528 | 0 | 31 | [5 empty] | B-N, Zone 1, Dist- 4.2km. -
335 | 132kV ICCL-Choudwar |  |  |  |  | 0.24375 | 13 | 8 | [7 empty] | 0.5 | 8760 | 99.85% | 6.5667 | 4380
|  | 2023-06-17 | 15:02 | 2023-06-17 | 17:52 | 0.11806 | 0 | 42 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 15:09 (Only station supply aviled till 15:46 load limited to 20MW)
|  | 2023-06-30 | 18:18 | 2023-06-30 | 19:42 | 0.058333 | 0 | 7 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
|  | 2023-09-13 | 14:56 | 2023-09-13 | 16:19 | 0.057639 | 0 | 6 | [5 empty] | No indication, Incoming failed from ICCL end.. Supply availed from Kendrapara Grid at 15:02Hrs
|  | 2023-12-05 | 11:07 | 2023-12-05 | 11:14 | 0.0048611 | 0 | 6 | [5 empty] | Incomer failure from source end. No tripping at Salipur end.. Due to tripping of 132kV Choudwar- Bidanasi Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
336 | 132kV Jabamayee FAlloys-Duburi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12 | 8760 | 100% | 0 | 105120
337 | 132kV Jabamayee FAlloys-Sukinda RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.87 | 8760 | 100% | 0 | 33901.2
338 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0.071528 | 13 | 18 | [7 empty] | 29.6 | 8760 | 99.85% | 393.68 | 259296
|  | 2023-08-18 | 14:41 | 2023-08-18 | 14:53 | 0.0083333 | 0 | 12 | [5 empty] | The line was charged after consultation with Line incharge. At Anandapur end:- Zone-1, Dist-3km, Ia-0.285kA, Ib-0.231kA, Ic- 2.353kA, Va-84kV, Vb-66kV, Vc-91kV At Jajpur Road end:- Zone-2, Fault type-CG, Dist-33.53km, Ia-0.289kA, Ib-0.238kA, Ic-2.34kA, Van-94.41kV, Vbn-43.48kV, Vcn-77.19kV
|  | 2023-09-25 | 11:37 | 2023-09-25 | 11:46 | 0.00625 | 0 | 9 | [5 empty] | Source failure from Duburi end
|  | 2023-07-17 | 13:55 | 2023-07-17 | 14:55 | 0.041667 | 0 | 35 | [5 empty] | At Anandapur end:- DP, Zone-4, Fault location-0.5Km, Ia-1.68kA, Ib-0.11kA, Ic-0.1kA, Va-2.5kV, Vb-92.6kV, Vc-91.91kV
|  | 2023-12-02 | 00:07 | 2023-12-02 | 00:29 | 0.015278 | 0 | 22 | [5 empty] | At Jajpur Road end: Zone 2, Dist- 33.3 km, Ir- 0.278 kA, Iy- 0.296 kA, Ib- 2.377 kA At Anandpur end: Zone 1, Dist- 3.2 km, Ir- 0.290 kA, Iy- 0.303 kA, Ib- 2.304 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
339 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0.070139 | 13 | 16 | [7 empty] | 29.6 | 8760 | 99.85% | 392.6933 | 259296
|  | 2023-08-18 | 14:41 | 2023-08-18 | 14:53 | 0.0083333 | 0 | 12 | [5 empty] | At Jajpur Road end:- DP, Fault Current: IA=1.856kA, IB=297.4A, IC=296A, VAN=81.87kV, VBN=98.32kV, VCN=37.83kV, Zone-III, Fault Resistance=17.21Ω, Dist=45.36km
|  | 2023-09-25 | 11:37 | 2023-09-25 | 11:46 | 0.00625 | 0 | 9 | [5 empty] | Source failure from Duburi end
|  | 2023-07-17 | 13:55 | 2023-07-17 | 14:55 | 0.041667 | 0 | 35 | [5 empty] | At Anandapur end:- DP, Zone-4, Fault location-0.5Km, Ia-1.68kA, Ib-0.11kA, Ic-0.1kA, Va-2.5kV, Vb-92.6kV, Vc-91.91kV
|  | 2023-12-02 | 00:07 | 2023-12-02 | 00:27 | 0.013889 | 0 | 20 | [5 empty] | At Jajpur Road end: Zone 2, Dist- 33.3 km, Ir- 0.278 kA, Iy- 0.296 kA, Ib- 2.377 kA At Anandpur end: Zone 1, Dist- 3.2 km, Ir- 0.290 kA, Iy- 0.303 kA, Ib- 2.304 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
340 | 132kV Bhadrak-Agarpada |  |  |  |  | 0.027083 | 0 | 23 | [7 empty] | 28.07 | 8760 | 100% | 10.7602 | 245893.2
|  | 2023-07-31 | 17:39 | 2023-07-31 | 18:18 | 0.027083 | 0 | 23 | [5 empty] | Transient fault, Weather- Heavy rain and lightening At Anandapur end:- DP, Zone-2, Fault type-CG, Fault location- 40.06Km, Ia-0.09kA, Ib-0.14kA, Ic-1.7kA, Va-80.67kV, Vb- 81.62kV, Vc-48.66kV At Agarpada end:- Zone-1, Fault type-CG, Fault location-4.5Km, Ia-0.12kA, Ib-0.15kA, Ic-0.14kA
341 | 132kV Agarpada-Anandpur |  |  |  |  | 0.14444 | 13 | 58 | [7 empty] | 41 | 8760 | 99.84% | 572.6333 | 359160
|  | 2023-08-16 | 13:59 | 2023-08-16 | 14:57 | 0.040278 | 0 | 25 | [5 empty] | At Agarpada end:- Gr A/B optd. DP relay optd. Ia=0.12kA, Ib=0.12kA, Ic=0.12kA At Anandapur end:- zone- Z1, DP relay optd. Ia=0.112kA, Ib=0.117kA, Ic=2.16kA, distance- 28.41km
|  | 2023-07-31 | 17:39 | 2023-07-31 | 18:18 | 0.027083 | 0 | 23 | [5 empty] | Transient fault, Weather- Heavy rain and lightening At Anandapur end:- DP, Zone-2, Fault type-CG, Fault location- 40.06Km, Ia-0.09kA, Ib-0.14kA, Ic-1.7kA, Va-80.67kV, Vb- 81.62kV, Vc-48.66kV At Agarpada end:- Zone-1, Fault type-CG, Fault location-4.5Km, Ia-0.12kA, Ib-0.15kA, Ic-0.14kA
|  | 2023-07-31 | 17:40 | 2023-07-31 | 18:03 | 0.015972 | 0 | 23 | [5 empty] | Tripped due to lightening Started phase-CN, Tripped phase-ABC, Zone-I, Distance=22.85km, Ia=6.786A, Ib=6.126A, Ic=2.975kA, Van=75.77, Vbn=76.71, Vcn=54.16
|  | 2023-08-18 | 14:41 | 2023-08-18 | 14:53 | 0.0083333 | 0 | 12 | [5 empty] | The line was charged after consultation with Line incharge. At Anandapur end:- Zone-1, Dist-3km, Ia-0.285kA, Ib-0.231kA, Ic- 2.353kA, Va-84kV, Vb-66kV, Vc-91kV At Jajpur Road end:- Zone-2, Fault type-CG, Dist-33.53km, Ia-0.289kA, Ib-0.238kA, Ic-2.34kA, Van-94.41kV, Vbn-43.48kV, Vcn-77.19kV
|  | 2024-03-27 | 16:59 | 2024-03-27 | 17:17 | 0.0125 | 0 | 7 | [5 empty] | At Anandpur end: Zone-1 , B-Phase ,distance-28-39km,Ia-203-5A,Ib-260- 7A, Ic-375-4A
|  | 2023-07-17 | 13:55 | 2023-07-17 | 14:31 | 0.025 | 0 | 6 | [5 empty] | 132kV Jajapur Road feeder tripped wthout any relay indication at.
|  | 2023-12-02 | 00:07 | 2023-12-02 | 00:29 | 0.015278 | 0 | 22 | [5 empty] | At Jajpur Road end: Zone 2, Dist- 33.3 km, Ir- 0.278 kA, Iy- 0.296 kA, Ib- 2.377 kA At Anandpur end: Zone 1, Dist- 3.2 km, Ir- 0.290 kA, Iy- 0.303 kA, Ib- 2.304 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
342 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0.63819 | 13 | 0 | [7 empty] | 34.31 | 8760 | 99.85% | 446.03 | 300555.6
|  | 2023-09-25 | 11:36 | 2023-09-25 | 13:55 | 0.096528 | 0 | 10 | [5 empty] | Tripped from Duburi end with no relay indication at Chandikhol end. 132kV I/C P/S was availed from Kendrapara end at 11:46 Hrs.
|  | 2023-08-18 | 16:40 | 2023-08-18 | 18:04 | 0.058333 | 0 | 11 | [5 empty] | At Jajpur Road end:- DP, Zone-1, Distance-8.782km, Fault Current in Y- Phase: 5.755 kA. 132kV I/C P/S was availed from Kendrapara end at 16:50 Hrs
|  | 2023-07-17 | 13:55 | 2023-07-17 | 14:14 | 0.013194 | 0 | 6 | [5 empty] | chandikhol end. Area interruption period = 07 min as 132kV I/C.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:32 | 0.022917 | 0 | 30 | [5 empty] | Tripped on E/F & O/C R,Y & B-Phase due to bird fault on 132kV Main Bus. I/C Power Supply was availed from kendrapara end at 10:14 .
|  | 2023-10-16 | 11:22 | 2023-10-16 | 22:06 | 0.44722 | 0 | 3 | [5 empty] | At Jajpur Road end: Zone 2, Dist- 29.94 km, Iy- 2.599 kA At Chandikhol end: No tripping. Chandikhol availed P/S from Kendrapara end at 11:25 Hrs. Conductor snapping at Loc no. 102
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
343 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.05 | 8760 | 100% | 0 | 219438
344 | 132kVJajpur Road-RAMCO |  |  |  |  | 0.125 | 1 | 3 | [7 empty] | 29.13 | 8760 | 99.99% | 30.5865 | 255178.8
|  | 2023-07-28 | 10:08 | 2023-07-28 | 10:47 | 0.027083 | 0 | 39 | [5 empty] | At Jajpur Road end:- DP Relay operated, Fault Current:- IA=248.5A, IB=214.6A, IC=2.546kA, Fault Voltage:- VAN=97.80kV, VBN=38.53kV, VCN=80.17kV, Zone-I, Fault Resistance=12.09Ω, Dist=23.6km At RAMCO end:- No tripping. trolling done but no fault fou
|  | 2023-09-17 | 12:05 | 2023-09-17 | 14:26 | 0.097917 | 0 | 24 | [5 empty] | At Jajpur Road end:- DP, FAULT CURRENT: IA=55.95A, IB=4.519kA, IC=4.464kA, F. VOLTAGE: VAN=76.24kV, VBN=53.24kV, VCN=47.23kV; F. Zone-I; FAULT RESISTANCE=876.8mΩ, Dist=15.79km.
345 | 132kV RAMCO- Kendrapara |  |  |  |  | 0.32708 | 14 | 7 | [7 empty] | 41.43 | 8760 | 99.84% | 584.8535 | 362926.8
|  | 2023-06-22 | 13:23 | 2023-06-22 | 14:07 | 0.030556 | 0 | 16 | [5 empty] | At Kendrapara end:- TRIPPED ON B/U E/F WITH M/R, Ir=2.525KA, Iy=8.677A, Ib=7.987A At Chandikhol end:-No tripping. LINE WAS IDLE CHARGED FROM CHANDIKHOLE END.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 11:02 | 0.04375 | 0 | 16 | [5 empty] | At Kendrapara end:- TRIPPED ON B/U E/F WITH M/R, Ir=165.7A, Iy=134.5A, Ib=324.3A At RAMCO end:- TRIPPED ON B/U E/F WITH M/R, Ir=102.5A, Iy=42.68 A, Ib=36.84 A. PATTAMUNDAI GRID WAS AVAILING P/S FROM RAMCO END THROUGH KENDRAPARA RESERVE BUS.
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2024-03-25 | 21:45 | 2024-03-25 | 22:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end: O/C, Zone 1, Dist- 14.41km, Ir- 1.992kA, Iy- 1.888kA, Ib- 1.382kA No tripping at RAMCO end. -
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
346 | 132kV Kuchei PG- Jaleswar |  |  |  |  | 0.093056 | 14 | 14 | [7 empty] | 78.88 | 8760 | 99.84% | 1122.7253 | 690988.8
|  | 2024-02-21 | 08:33 | 2024-02-21 | 08:41 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on O/C from Jaleswar end only(Back-up relay).. -
|  | 2023-06-15 | 18:21 | 2023-06-15 | 18:51 | 0.020833 | 0 | 30 | [5 empty] | Tripped from Kuchei end only.. 131 KV Kuchei-Jaleswar, Kuchei- Bhograi Line tripped from Kuchei end only & 132 KV Basta- Jaleswar Fdr priciously H/T from Basta end.
|  | 2024-03-11 | 06:55 | 2024-03-11 | 08:31 | 0.066667 | 1 | 36 | [5 empty] | Tripped from Jaleswar end on DP relay.. Fire breakdown at TRF III
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
347 | 132kV Kuchei PG- Bhogarai |  |  |  |  | 0.056944 | 1 | 22 | [7 empty] | 100.91 | 8760 | 99.98% | 137.9103 | 883971.6
|  | 2023-08-11 | 21:44 | 2023-08-11 | 22:33 | 0.034028 | 0 | 49 | [5 empty] | At Bhograi end:- DP, Bph-E, Zone-2, Dist-1.1km, IR-235.1A, IY- 265.1A, IB-241.7A At Kuchei end:- DP, Bph-E, Zone-1, Dist-104.2km, IB-0.952kA. Patrolling done but no fault found
|  | 2023-06-15 | 18:23 | 2023-06-15 | 18:56 | 0.022917 | 0 | 33 | [5 empty] | At Kuchei end:- DP operated, Zone-1, Bph to E, Dist- 16.07km, IB-2.794kA. 131 KV Kuchei-Jaleswar, Kuchei- Bhograi Line tripped from Kuchei end only & 132 KV Basta- Jaleswar Fdr priciously H/T from Basta end.
348 | 132kV Jaleswar-Bhogarai |  |  |  |  | 0.16319 | 15 | 44 | [7 empty] | 57.13 | 8760 | 99.82% | 898.8453 | 500458.8
|  | 2023-08-11 | 21:44 | 2023-08-11 | 22:06 | 0.015278 | 0 | 22 | [5 empty] | At Bhograi end:- DP, Bph-E, Zone-1, Dist-7.3km, IR-9.3A, IY-0A, IB- 195.8A At Jaleswar end:- DP, Bph-E, Zone-1. Patrolling done but no fault found
|  | 2023-06-15 | 18:21 | 2023-06-15 | 18:53 | 0.022222 | 0 | 30 | [5 empty] | Source failure. 131 KV Kuchei-Jaleswar, Kuchei- Bhograi Line tripped from Kuchei end only & 132 KV Basta- Jaleswar Fdr priciously H/T from Basta end.
|  | 2024-03-11 | 06:55 | 2024-03-11 | 08:52 | 0.08125 | 1 | 52 | [5 empty] | At Bhograi end: Y-B, Zone 2, Dist- 34.9km, Iy-1.109kA, Ib-1.083kA At Jaleswar end: O/C, E/F. Fire breakdown at TRF III
|  | 2024-03-18 | 08:01 | 2024-03-18 | 09:05 | 0.044444 | 1 | 0 | [5 empty] | At Bhograi end: Y-N, Zone 1, Dist- 10.5km, Iy- 1.046kA At Jaleswar end:Y-N, Zone 1, Dist- 14.8km, Iy- 0.172kA. Disc insulator string punctured at Loc no-141 of Basta-Jaleswar Line. Weather- Heavy lightning and thunderstorm.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
349 | 132kVJaleswar-Jaleswar RTSS |  |  |  |  | 0.0875 | 14 | 6 | [7 empty] | 2.34 | 8760 | 99.84% | 32.994 | 20498.4
|  | 2024-02-21 | 08:33 | 2024-02-21 | 08:41 | 0.0055556 | 0 | 8 | [5 empty] | Tripped on O/C from Jaleswar end only(Back-up relay).. -
|  | 2023-06-15 | 18:21 | 2023-06-15 | 18:32 | 0.0076389 | 0 | 11 | [5 empty] | Source failure. 131 KV Kuchei-Jaleswar, Kuchei- Bhograi Line tripped from Kuchei end only & 132 KV Basta- Jaleswar Fdr priciously H/T from Basta end.
|  | 2024-03-11 | 06:55 | 2024-03-11 | 08:35 | 0.069444 | 1 | 40 | [5 empty] | Handtripped as TRF III caught fire.. Fire breakdown at TRF III
|  | 2024-03-12 | 16:17 | 2024-03-12 | 16:24 | 0.0048611 | 0 | 7 | [5 empty] | O/C. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
350 | 132 kV Jaleswar-Basta |  |  |  |  | 0.76528 | 15 | 52 | [7 empty] | 23.41 | 8760 | 99.82% | 371.4387 | 205071.6
|  | 2023-08-11 | 21:35 | 2023-08-12 | 7:30 | 0.41319 | 0 | 49 | [5 empty] | At Basta end:- Zone-1, B ph-Gnd, Distance-12.87km, Ia-124.8A, Ib- 2.175kA, Ic-193.7A At Jaleswar end:- Zone-1, B ph-Gnd, Dist-8.58km, Ib-2.028kA. After patrolling of Basta- Jaleswar feeder, no fault was found
|  | 2023-06-15 | 18:21 | 2023-06-15 | 18:32 | 0.0076389 | 0 | 11 | [5 empty] | Source failure. 131 KV Kuchei-Jaleswar, Kuchei- Bhograi Line tripped from Kuchei end only & 132 KV Basta- Jaleswar Fdr priciously H/T from Basta end.
|  | 2024-03-11 | 06:55 | 2024-03-11 | 09:00 | 0.086806 | 1 | 52 | [5 empty] | Handtripped as TRF III caught fire.. Fire breakdown at TRF III
|  | 2024-03-18 | 08:01 | 2024-03-18 | 14:12 | 0.25764 | 1 | 0 | [5 empty] | At Basta end: R-N, Zone 1, Dist- 9.5km, Ir- 2.198kA At Jaleswar end: R-N, Zone 1, Dist- 12.904km, Ir- 1.715kA. Disc insulator string punctured at Loc no-141 of Basta-Jaleswar Line. Weather- Heavy lightning and thunderstorm.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
351 | 132kVJayanagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.87 | 8760 | 100% | 0 | 393061.2
352 | 132kVJayanagar-Jayanagar RTSS |  |  |  |  | 0.97847 | 25 | 3 | [7 empty] | 39.6 | 8760 | 99.71% | 991.98 | 346896
|  | 2023-04-06 | 23:28 | 2023-04-06 | 23:33 | 0.0034722 | 0 | 5 | [5 empty] | A-N,Z-1,Dist-24KM,If=1.3KA.
|  | 2023-04-25 | 17:11 | 2023-04-25 | 17:32 | 0.014583 | 0 | 21 | [5 empty] | A-N, Z-1, Dist=1.55KM,If=8.6KA.
|  | 2023-04-25 | 18:32 | 2023-04-25 | 18:50 | 0.0125 | 0 | 18 | [5 empty] | B-N, Z-1, Dist=47.62KM,If=1.72KA.
|  | 2023-04-26 | 10:33 | 2023-04-26 | 14:06 | 0.14792 | 3 | 33 | [5 empty] | A-B-C-N,Z-1, Dist=6.69KM,Ia=7.43KA,Ib=7.22KA,Ic=7.17KA.
|  | 2023-04-28 | 15:25 | 2023-04-28 | 15:32 | 0.0048611 | 0 | 7 | [5 empty] | A-N, Z-1, Dist=66.99KM,If=1.66KA.
|  | 2023-05-08 | 15:37 | 2023-05-08 | 15:47 | 0.0069444 | 0 | 10 | [5 empty] | .
|  | 2023-05-13 | 13:13 | 2023-05-13 | 13:34 | 0.014583 | 0 | 21 | [5 empty] | B-N,Z1,Dist-3.64Km,IF-6.31KA. CHARGED BUT TRIPPED IMMEDIATELY
|  | 2023-05-13 | 13:34 | 2023-05-13 | 15:18 | 0.072222 | 1 | 44 | [5 empty] | B-N,Z1,3.14KM,If-6.43KA. CHARGED BUT TRIPPED IMMEDIATELY
|  | 2023-05-14 | 12:18 | 2023-05-15 | 1:17 | 0.49931 | 1 | 35 | [5 empty] | Y-B-N,Z1,23.54KM,If-3.6KA. CHARGED BUT TRIPPED IMMEDIATELY
|  | 2023-05-14 | 12:07 | 2023-05-14 | 12:18 | 0.0076389 | 0 | 11 | [5 empty] | B-N,Z1,Dist-22.03Km,IF-3.03KA. CHARGED BUT TRIPPED IMMEDIATELY
|  | 2023-05-21 | 15:34 | 2023-05-21 | 17:55 | 0.097917 | 2 | 21 | [5 empty] | R-N,Z1,Dist-1.524Km,If-8.98KA….Trail Charge done at 15:53Hrs but tripped with fault details-R-N,Z1,Dist-1.48Km,If-8.66KA. CHARGED BUT TRIPPED IMMEDIATELY
|  | 2023-06-19 | 02:04 | 2023-06-19 | 02:10 | 0.0041667 | 0 | 6 | [5 empty] | B-N,Z-1,Dist-41Km,If-1.8KA.
|  | 2023-09-26 | 14:36 | 2023-09-26 | 14:51 | 0.010417 | 0 | 15 | [5 empty] | Z-1,B-G,Dist-41.08Km,If-1.91KA.
|  | 2023-10-02 | 02:21 | 2023-10-02 | 02:27 | 0.0041667 | 0 | 6 | [5 empty] | Zone 1, R-Y-B-G, Dist- 62 km, If- 2.2 kA. -
|  | 2023-10-04 | 10:58 | 2023-10-04 | 11:08 | 0.0069444 | 0 | 10 | [5 empty] | B-N, Zone 1, Dist- 9.49 km, If- 3.96 kA. -
|  | 2023-10-25 | 05:50 | 2023-10-25 | 06:37 | 0.032639 | 0 | 45 | [5 empty] | Zone 1, Y-B-N, Dist- 2.895 km, If- 8.3 kA. -
|  | 2024-01-05 | 15:05 | 2024-01-05 | 15:17 | 0.0083333 | 0 | 12 | [5 empty] | B-N, Zone 1, Dist- 4.96km, Ib- 4.65kA. -
|  | 2024-02-12 | 12:08 | 2024-02-12 | 12:51 | 0.029861 | 0 | 43 | [5 empty] | Zone 1, B-N, Dist- 22.56km, If- 2.74kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
353 | 132kVJayanagar-Podagada |  |  |  |  | 0.015278 | 0 | 22 | [7 empty] | 38.0419 | 8760 | 100% | 13.9487 | 333247.044
|  | 2023-06-19 | 01:33 | 2023-06-19 | 01:50 | 0.011806 | 0 | 17 | [5 empty] | Incoming failure.
|  | 2023-08-31 | 15:13 | 2023-08-31 | 15:18 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on General trip, Dist= 52.3km. All 132kV feeders were interrupted
354 | 132kV Podagada-Rayagada |  |  |  |  | 1899-12-31 05:11 | 13 | 52 | [7 empty] | 72.1572 | 8760 | 99.84% | 1000.5798 | 632097.072
|  | 2023-08-05 | 9:57 | 2023-08-05 | 10:12 | 0:15 | 0 | 15 | [5 empty] | Ia=140a, Ib=530a,Ic=110a, LOC=75.1km.
|  | 2023-08-12 | 19:26 | 2023-08-12 | 19:30 | 0:04 | 0 | 4 | [5 empty] | Ia=130a, Ib=260a,Ic=600a, LOC=131.3km., Zone=3, B-phase.
|  | 2023-06-19 | 01:33 | 2023-06-19 | 01:50 | 0.011806 | 0 | 17 | [5 empty] | Incoming failure.
|  | 2023-08-03 | 11:32 | 2023-08-03 | 11:39 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Machhkund end. -
|  | 2023-08-03 | 11:42 | 2023-08-03 | 12:45 | 0.04375 | 0 | 25 | [5 empty] | AutoTripped on General trip, E/F PU, IL1= 0.17kA, IL2= 0.62kA, IL3= 0.11kA 1614mS, Rsec= 94ohm, Xsec= 9.34ohm, Rpri= 282.01ohm, Xpri= 28.02 ohm, Dist= 71.8KM.. the line was declared faulty.Akhusingh gss availed load from Gunupur
|  | 2023-08-03 | 12:45 | 04.08.23 | 16:05 | 1899-12-31 03:20 | 0 | 20 | [5 empty] | AutoTripped on General trip, E/F PU, L2-E, Dir. O/C & E/F relay optd.IL1= 0.02kA, IL2= 0.36kA, IL3= 0.02kA 1614mS, Rsec= 44.96ohm, Xsec= 13.80ohm, Rpri= 134.88 Ohm, Xpri= 41.41 ohm, Dist= 98.6 KM.. Yph insulator puncture at Loc 4,10 & 428
|  | 2023-06-07 | 15:04 | 2023-06-07 | 15:13 | 0.00625 | 0 | 9 | [5 empty] | Incoming failure. Charged after getting confirmation from Rayagada GSS.
|  | 2023-06-12 | 14:24 | 2023-06-12 | 14:39 | 0.010417 | 0 | 15 | [5 empty] | Incoming failure.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
355 | 132kV Podagada-Patangi |  |  |  |  | 1899-12-31 01:05 | 13 | 46 | [7 empty] | 52 | 8760 | 99.84% | 715.8667 | 455520
|  | 2023-06-19 | 01:22 | 20.06.23 | 0:54 | 0.99444 | 0 | 33 | [5 empty] | Tripped on GR-A/B,A/R UNSUCCESSFUL, Trip Relay Optd,Distance Protection relay Optd , R-Ph fault , zone=1, PUT=81.67 ms,Trip time 80.01 ms, Dist= 23.03 KM, IL1= 1.069 KA, IL2= 52.98 A, IL3=66.79 A. Heavy Rain with Thunder. Charged after getting confirmation from Potangi GSS.
|  | 2023-08-17 | 09:43 | 2023-08-17 | 10:08 | 0.017361 | 0 | 25 | [5 empty] | Power supply failed from Podagada end. -
|  | 2023-08-17 | 12:14 | 2023-08-17 | 12:19 | 0.0034722 | 0 | 5 | [5 empty] | Power supply failed from Podagada end. -
|  | 2023-08-31 | 15:13 | 2023-08-31 | 15:18 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on General trip, Dist= 52.3km. All 132kV feeders were interrupted
|  | 2023-08-31 | 15:52 | 2023-08-31 | 16:25 | 0.022917 | 0 | 33 | [5 empty] | Power supply failed from Podagada end. -
|  | 2023-08-31 | 18:54 | 2023-08-31 | 18:59 | 0.0034722 | 0 | 5 | [5 empty] | Power supply failed from Podagada end. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
356 | 132kVJaynagar-Tentulikhunti |  |  |  |  | 0.09375 | 13 | 50 | [7 empty] | 55.6 | 8760 | 99.84% | 769.1333 | 487056
|  | 2023-04-23 | 16:18 | 2023-04-23 | 16:38 | 0.013889 | 0 | 20 | [5 empty] | Source end failure.
|  | 2023-06-26 | 14:20 | 2023-06-26 | 14:38 | 0.0125 | 0 | 18 | [5 empty] | Y-B fault.
|  | 2023-06-27 | 17:56 | 2023-06-27 | 18:41 | 0.03125 | 0 | 45 | [5 empty] | Y-B fault. Line patrolling was done and no fault found.
|  | 2023-05-12 | 06:13 | 2023-05-12 | 07:05 | 0.036111 | 0 | 27 | [5 empty] | Supply Fail.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
357 | 132kVJayanagar-Nabarangpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.24 | 564 | 100% | 0 | 41307.36
358 | 132kVJayanagar-Borigumma |  |  |  |  | 0.027083 | 0 | 27 | [7 empty] | 39.3 | 8196 | 99.99% | 17.685 | 322102.8
|  | 2023-05-12 | 06:13 | 2023-05-12 | 06:52 | 0.027083 | 0 | 27 | [5 empty] | Supply Fail.
359 | 132kV Borigumma-Nabarangpur |  |  |  |  | 0.027083 | 0 | 27 | [7 empty] | 66 | 8196 | 99.99% | 29.7 | 540936
|  | 2023-05-12 | 06:13 | 2023-05-12 | 06:52 | 0.027083 | 0 | 27 | [5 empty] | Supply Fail.
360 | 132kV Nabarangpur-Tentulikhunti |  |  |  |  | 0.084722 | 13 | 50 | [7 empty] | 26.4 | 8760 | 99.84% | 365.2 | 231264
|  | 2023-04-23 | 16:18 | 2023-04-23 | 16:38 | 0.013889 | 0 | 20 | [5 empty] | Source end failure.
|  | 2023-06-26 | 14:20 | 2023-06-26 | 14:38 | 0.0125 | 0 | 18 | [5 empty] | Y-B fault.
|  | 2023-06-27 | 17:56 | 2023-06-27 | 18:41 | 0.03125 | 0 | 45 | [5 empty] | Y-B fault. Line patrolling was done and no fault found.
|  | 2023-05-12 | 06:13 | 2023-05-12 | 06:52 | 0.027083 | 0 | 27 | [5 empty] | Supply Fail.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
361 | 132kVJharsuguda-Jharsuguda RTSS |  |  |  |  | 0.90903 | 14 | 34 | [7 empty] | 0.15 | 8760 | 99.83% | 2.185 | 1314
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
|  | 2023-05-20 | 18:00 | 2023-05-20 | 18:08 | 0.0055556 | 0 | 8 | [5 empty] | Zone 1, Ia= 1.771 kA, Ib= 1.772 kA. At Railway end- Ir= 16.35 A, Iy= 16.33 A
|  | 2023-06-27 | 01:49 | 2023-06-27 | 01:59 | 0.0069444 | 0 | 10 | [5 empty] | O/C Ryph, Ia=1.7 kA, Ib=1.7 kA.
|  | 2023-08-02 | 0:05 | 2023-08-02 | 0:26 | 0.014583 | 0 | 21 | [5 empty] | O/C, Ir=1.928 kA, Iy= 1.929 kA, Ic= 0 kA,. -
|  | 2023-08-02 | 0:27 | 2023-08-02 | 0:58 | 0.021528 | 0 | 31 | [5 empty] | O/C, Ir=1.928 kA, Iy= 1.929 kA, Ic= 0 kA,. -
|  | 2023-08-02 | 1:26 | 2023-08-02 | 1:56 | 0.020833 | 0 | 30 | [5 empty] | O/C, Ir=1.928 kA, Iy= 1.929 kA, Ic= 0 kA,. -
|  | 2023-09-27 | 22:23 | 2023-09-27 | 22:39 | 0.011111 | 0 | 16 | [5 empty] | At Jharsuguda end:- RY Phase, Ir-1.6kA, Iy-1.6kA, Fault duration -270.0ms, Micom P141. Capacitor bank burst at Railway swtichyard
|  | 2023-09-28 | 09:00 | 2023-09-28 | 09:13 | 0.0090278 | 0 | 13 | [5 empty] | At Jharsuguda end:- RY Phase, Ir-1.6kA, Iy-1.6kA, Fault duration -48.33 ms, Micom P141. Capacitor bank burst at Railway swtichyard
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
362 | 132kVJharsuguda-Ultratech |  |  |  |  | 0.05625 | 1 | 21 | [7 empty] | 31 | 8760 | 99.98% | 41.85 | 271560
|  | 2023-07-29 | 13:51 | 2023-07-29 | 15:12 | 0.05625 | 1 | 21 | [5 empty] | Zone-1, Fault Loc= 8.411km, Fault duration=1.659 ms, Ia= 130.9A, Ib= 6.883kA, Ic= 82.43kA, In= 6.83kA. No Fault found after line patrolling
363 | 132kV Joda- Banaspani RTSS |  |  |  |  | 0.75417 | 30 | 0 | [7 empty] | 2.99 | 8760 | 99.66% | 89.7 | 26192.4
|  | 2023-04-11 | 12:14 | 2023-04-11 | 02:52 | 0.60972 | 14 | 38 | [5 empty] | Tripped at Joda end with following relay At Joda end: B/Y relay: O/C trip,Fault Current: IL1=0.25KA,IL2=0.25KA,IL3=0.
|  | 2023-07-04 | 03:55 | 2023-07-04 | 04:10 | 0.010417 | 0 | 15 | [5 empty] | At Joda end:- B/U relay:- O/C, FL: L1-L2, Fault Current:- Ia=0.27kA, Ib=0.26kA, Ic=0.00kA At Palasponga end:- DP relay:- Zone-I, CGT, Dist=1.43km, Fa. Incoming power supply failed from Atri end.
|  | 2023-07-27 | 11:28 | 2023-07-27 | 11:36 | 0.0055556 | 0 | 8 | [5 empty] | At Joda end:- B/U relay:- O/C, Fault Current: Ia=0.27kA, Ib=0.26kA, Ic=0.00kA.
|  | 2023-08-14 | 8:47 | 2023-08-14 | 9:03 | 0.011111 | 0 | 16 | [5 empty] | At Joda end:- B/U relay: Direction O/C trip, Dist=147.9KM,Fault Current: IL1=0.25KA,IL2=0.25KA. O/C Tripped
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:23 | 0.0125 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-09-05 | 19:29 | 2023-09-05 | 19:33 | 0.0027778 | 0 | 4 | [5 empty] | At Joda end:- B/U relay: O/C tripped, Fault current: IL1=0.27kA, IL2=0.26kA. Tripped on B/U relay at Joda end
|  | 2023-10-04 | 20:37 | 2023-10-04 | 20:44 | 0.0048611 | 0 | 7 | [5 empty] | At Joda end: B/U relay: Dir-O/C, R-Y Ph, Ir- 0.27 kA, Iy-0.27 kA. Tripped on B/U relay
|  | 2023-11-25 | 10:10 | 2023-11-25 | 10:19 | 0.00625 | 0 | 9 | [5 empty] | At Joda end: B/U relay- O/C, Ir- 0.25 kA, Iy- 0.25 kA. -
|  | 2023-12-04 | 22:16 | 2023-12-04 | 22:22 | 0.0041667 | 0 | 6 | [5 empty] | B/U Relay: Dir.O/C, Ir- 0.26 kA, Iy- 0.26 kA. -
|  | 2023-12-11 | 09:09 | 2023-12-11 | 09:19 | 0.0069444 | 0 | 10 | [5 empty] | B/U Relay: Dir.O/C, Ir- 0.26kA, Iy- 0.26kA. -
|  | 2023-12-18 | 08:16 | 2023-12-18 | 08:24 | 0.0055556 | 0 | 8 | [5 empty] | B/U Relay: Dir.O/C, If- 0.27 kA. -
|  | 2023-12-19 | 20:24 | 2023-12-19 | 20:29 | 0.0034722 | 0 | 5 | [5 empty] | B/U Relay: Dir.O/C, If- 0.28 kA. No physical fault found
|  | 2023-12-31 | 21:04 | 2023-12-31 | 21:12 | 0.0055556 | 0 | 8 | [5 empty] | B/U Relay: Dir.O/C, If- 0.27 kA. -
|  | 2024-01-06 | 19:27 | 2024-01-06 | 19:36 | 0.00625 | 0 | 9 | [5 empty] | At Joda end: B/U relay- Dir. O/C, If- 0.27kA. -
|  | 2024-01-13 | 17:28 | 2024-01-13 | 17:32 | 0.0027778 | 0 | 4 | [5 empty] | At Joda end: B/U relay: Dir.O/C tripped, If- 0.27 kA. -
|  | 2024-01-13 | 17:40 | 2024-01-13 | 17:42 | 0.0013889 | 0 | 2 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.27 kA. -
|  | 2024-01-16 | 09:50 | 2024-01-16 | 09:55 | 0.0034722 | 0 | 5 | [5 empty] | At Joda end: B/U relay- Dir.O/C, If- 0.27 kA. -
|  | 2024-01-22 | 23:52 | 23.01.24 | 0:01 | 0.00625 | 0 | 9 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.27 kA. -
|  | 2024-02-07 | 17:37 | 2024-02-07 | 17:44 | 0.0048611 | 0 | 7 | [5 empty] | At Joda end: B/U relay: Dir. O/C, If- 0.27kA. -
|  | 2024-02-08 | 04:10 | 2024-02-08 | 04:20 | 0.0069444 | 0 | 10 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.26kA. -
|  | 2024-02-11 | 15:57 | 2024-02-11 | 16:01 | 0.0027778 | 0 | 4 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.27kA. -
|  | 2024-02-23 | 09:24 | 2024-02-23 | 09:31 | 0.0048611 | 0 | 7 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.27kA. -
|  | 2024-02-23 | 10:30 | 2024-02-23 | 10:37 | 0.0048611 | 0 | 7 | [5 empty] | At Joda end: B/U relay: Dir.O/C,If- 0.27kA. -
|  | 2024-02-27 | 08:32 | 2024-02-27 | 08:38 | 0.0041667 | 0 | 6 | [5 empty] | At Joda end: B/U relay: Dir.O/C, If- 0.25kA. -
|  | 2024-03-02 | 17:12 | 2024-03-02 | 17:24 | 0.0083333 | 0 | 12 | [5 empty] | At Joda end: B/U relay-Dir-O/C, If- 0.26kA. -
|  | 2024-03-03 | 08:08 | 2024-03-03 | 08:16 | 0.0055556 | 0 | 8 | [5 empty] | At Joda end: B/U relay-Dir-O/C, If- 0.28kA. -
|  | 2024-03-14 | 00:21 | 2024-03-14 | 00:25 | 0.0027778 | 0 | 4 | [5 empty] | At Joda end: Dir. O/C, If-0.27kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
364 | 132kV Joda-FAP |  |  |  |  | 0.013889 | 0 | 12 | [7 empty] | 1.03 | 8760 | 100% | 0.206 | 9022.8
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:25 | 0.013889 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
365 | 132kV Joda-Kenduposi |  |  |  |  | 0.014583 | 0 | 20 | [7 empty] | 49.42 | 8760 | 100% | 16.4733 | 432919.2
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:26 | 0.014583 | 0 | 20 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
366 | 132kV Joda-Palasponga |  |  |  |  | 1900-01-02 08:50 | 16 | 21 | [7 empty] | 41.6 | 8760 | 99.81% | 680.16 | 364416
|  | 2023-04-08 | 15:58 | 2023-04-08 | 16:06 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end with following relay indication. Relay at Joda end: B/U relay: Direction O/C trip, Fault Current: Ia=0.27KA,Ib=0.84KA,Ic=0.24KA, At Palasponga end : Not tripped.
|  | 2023-05-19 | 19:28 | 2023-05-19 | 19:58 | 0.020833 | 0 | 30 | [5 empty] | Tripped at both end with following relay indication: At Joda end: DP relay: FL=L2-N,Zone-1,Dist=6.43KM,Fault Current: Ia=235.84A,Ib=6.64KA,Ic=154.94A,In=6.43KA At PPG end: DP relay: BGT,Zone-1,Dist=31.11KM,Fault Current: Ia=245A,Ib=315A,Ic=174A,In=0,Ig=530A.
|  | 2023-05-31 | 14:51 | 2023-05-31 | 16:38 | 0.074306 | 0 | 38 | [5 empty] | Tripped at both end with following relay indication At Joda end:- D.P. Relay:FL: L2-N Zone-1,Dist. =2.2169KM Fault Current: IL1=230.62A, IL2=7754.55A, IL3=113.16A, IN=7521.04A At PPG end:- D.P. Relay,FL: BG T,Zone-1 Dist. =32.9KM Fault Current: Ia=241A, Ib=254A, Ic=128A, Ig=486A.
|  | 2023-07-03 | 11:27 | 2023-07-03 | 16:38 | 0.21597 | 0 | 27 | [5 empty] | At Joda end:- DP relay:- Zone-II, FL: L3-N, FD=46.038km, Fault Current:- Ia=209.25A, Ib=460.24A, Ic=2000.37A At Palasponga end:- DP relay:- Zone-I, CGT, Dist=1.43km, Fault Current:- Ia=231A, Ib=463A, Ic=530A, Ig=1090A,source fail from Karanjia end. B-Ph LA of Joda incomer burst at Palasponga end.
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:21 | 0.011111 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2024-02-06 | 18:50 | 2024-02-08 | 12:14 | 1899-12-31 17:24 | 1 | 15 | [5 empty] | At Joda end: Zone 1, Dist- 1.46km, Iy- 6.831kA. -
|  | 2024-03-19 | 02:33 | 2024-03-19 | 02:52 | 0.013194 | 0 | 19 | [5 empty] | Ir- 0.29kA, Iy- 0.78kA, Ib- 0.26kA. -
|  | 2023-07-15 | 12:14 | 2023-07-16 | 18:45 | 1899-12-31 06:31 | 0 | 8 | [5 empty] | At Karanjia end:- Y ph-G, Zone-1, Dist=53.4km, Ir=0.28kA, Iy=0.24kA, Ib=0.21kA At Palasponga end:- Y ph-G, Zone -1, Dist=46.27km, Ir=282A, Iy=1452A, Ib=205A, Ig=965A. Y-ph insulator punctured at LOC No. 156 of Karanjia- Palaspanga line
|  | 2023-04-14 | 13:38 | 2023-04-14 | 13:46 | 0.0055556 | 0 | 8 | [5 empty] | O/C TRIP ONLY AT PALASPANGA END, IA=507.5A,IB=421.5A,IC=370A, IG=4.0A.
|  | 2024-01-06 | 07:57 | 2024-01-06 | 08:03 | 0.0041667 | 0 | 6 | [5 empty] | O/C, Ir- 0.538kA, Iy- 0.457kA, Ib- 0.295kA. -
|  | 2024-01-10 | 10:17 | 2024-01-10 | 10:20 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.493kA, Iy- 0.395kA, Ib- 0.291kA. -
|  | 2023-12-29 | 07:12 | 2023-12-29 | 07:16 | 0.0027778 | 0 | 4 | [5 empty] | At Palasponga end: B/C Relay, O/C(R- Y), Ir- 0.502 kA, Iy- 0.442 kA, Ib- 0.287 kA. -
|  | 2024-01-09 | 16:54 | 2024-01-09 | 16:58 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 0.507kA, Iy- 0.433kA, Ib- 0.332kA. -
|  | 2024-01-09 | 20:29 | 2024-01-09 | 20:32 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.484kA, Iy- 0.424kA, Ib- 0.314kA. -
|  | 2024-01-10 | 07:51 | 2024-01-10 | 07:53 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir- 0.516kA, Iy- 0.424kA, Ib- 0.314kA. -
|  | 2024-01-16 | 10:02 | 2024-01-16 | 10:06 | 0.0027778 | 0 | 4 | [5 empty] | At Palasponga end: O/C, Ir- 0.496 kA, Iy- 0.433 kA, Ib- 0.276 kA. -
|  | 2024-03-03 | 14:57 | 2024-03-03 | 14:59 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir-0.528kA, Iy-0.416kA, Ib- 0.326kA. -
|  | 2024-03-11 | 08:51 | 2024-03-11 | 08:55 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 0.528kA, Iy- 0.416kA, Ib- 0.326kA. -
|  | 2024-03-16 | 07:53 | 2024-03-16 | 07:57 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 5.283kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
367 | 132kV Palasponga- Keonjhargarh RTSS |  |  |  |  | 0.40208 | 15 | 46 | [7 empty] | 19.43 | 8760 | 99.82% | 306.3463 | 170206.8
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
|  | 2023-04-08 | 15:58 | 2023-04-08 | 16:06 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end with following relay indication. Relay at Joda end: B/U relay: Direction O/C trip, Fault Current: Ia=0.27KA,Ib=0.84KA,Ic=0.24KA, At Palasponga end : Not tripped.
|  | 2023-05-19 | 19:28 | 2023-05-19 | 19:58 | 0.020833 | 0 | 30 | [5 empty] | Tripped at both end with following relay indication: At Joda end: DP relay: FL=L2-N,Zone-1,Dist=6.43KM,Fault Current: Ia=235.84A,Ib=6.64KA,Ic=154.94A,In=6.43KA At PPG end: DP relay: BGT,Zone-1,Dist=31.11KM,Fault Current: Ia=245A,Ib=315A,Ic=174A,In=0,Ig=530A.
|  | 2023-05-31 | 14:51 | 2023-05-31 | 16:38 | 0.074306 | 0 | 38 | [5 empty] | Tripped at both end with following relay indication At Joda end:- D.P. Relay:FL: L2-N Zone-1,Dist. =2.2169KM Fault Current: IL1=230.62A, IL2=7754.55A, IL3=113.16A, IN=7521.04A At PPG end:- D.P. Relay,FL: BG T,Zone-1 Dist. =32.9KM Fault Current: Ia=241A, Ib=254A, Ic=128A, Ig=486A.
|  | 2023-07-03 | 11:27 | 2023-07-03 | 16:38 | 0.21597 | 0 | 27 | [5 empty] | At Joda end:- DP relay:- Zone-II, FL: L3-N, FD=46.038km, Fault Current:- Ia=209.25A, Ib=460.24A, Ic=2000.37A At Palasponga end:- DP relay:- Zone-I, CGT, Dist=1.43km, Fault Current:- Ia=231A, Ib=463A, Ic=530A, Ig=1090A,source fail from Karanjia end. B-Ph LA of Joda incomer burst at Palasponga end.
|  | 2023-04-07 | 16:38 | 2023-04-07 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | O/C TRIP,IA=305.2A,IB=224.9A, IC=103.8A,INM=6.395A,IND=7.035A.
|  | 2023-04-14 | 13:38 | 2023-04-14 | 13:46 | 0.0055556 | 0 | 8 | [5 empty] | O/C TRIP ONLY AT PALASPANGA END, IA=507.5A,IB=421.5A,IC=370A, IG=4.0A.
|  | 2023-04-16 | 08:55 | 2023-04-16 | 08:57 | 0.0013889 | 0 | 2 | [5 empty] | O/C TRIP,IA=304.9A,IB=275.8A,IC=42.79A, INM=6.786A,IND=5.209A.
|  | 2023-04-24 | 06:08 | 2023-04-24 | 06:11 | 0.0020833 | 0 | 3 | [5 empty] | E/F TRIP, DP Relay: Started phase C-N,ZONE-2, D=21.75KM,IA=43.14A,IB=9.857A,IC=2.035KA B/U RELAY:IA=36.05A,IB=9.27A,IC=2.032KA, IND=2.053A.
|  | 2023-05-18 | 08:23 | 2023-05-18 | 08:25 | 0.0013889 | 0 | 2 | [5 empty] | IA=300.1A,IB=275.9A,IC=46.95A, INM=6.3579A,IND=7.2773A. O/C TRIP
|  | 2023-10-19 | 08:57 | 2023-10-19 | 09:00 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.302 kA, Iy- 0.253 kA, Ib- 0.053 kA. -
|  | 2023-06-07 | 12:05 | 2023-06-07 | 12:11 | 0.0041667 | 0 | 6 | [5 empty] | O/C (R-ɸ), BACK UP RELAY ,IA=299.8A,IB=235.1A,IC=90.68A, INM=6.99A,IND=7.4A. O/C TRIP
|  | 2023-06-08 | 18:28 | 2023-06-08 | 18:30 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R-ɸ), BACK UP RELAY ,IA=300.4A,IB=256.4A,IC=53.27A, INM=6.733A,IND=5.263A. O/C TRIP
|  | 2023-07-17 | 13:41 | 2023-07-17 | 13:43 | 0.0013889 | 0 | 2 | [5 empty] | At Palasponga end:- Back up Relay ,O/C (R-ɸ), IA=299.5A, IB=258.12A, IC=46.79A, INM=7.326A, IND=5.843A. O/C trip
|  | 2023-08-11 | 09:22 | 2023-08-11 | 09:24 | 0.0013889 | 0 | 2 | [5 empty] | BACK UP RELAY, O/C (R-ɸ), IA=300.2A, IB=277.3A, IC=39.86A, Inm=5.87A, Ind=4.63A. O/C Trip
|  | 2023-08-18 | 10:11 | 2023-08-18 | 10:14 | 0.0020833 | 0 | 3 | [5 empty] | BACK UP RELAY, O/C (R-ɸ), IA=301.6A, IB=239.5A, IC=67.87A, Inm=7.031A, Ind=4.850A. O/C Trip
|  | 2023-08-23 | 07:13 | 2023-08-23 | 07:16 | 0.0020833 | 0 | 3 | [5 empty] | BACK UP RELAY, O/C (R-ɸ), IA=299.0A, IB=273.3A, IC=42.69A, Inm=6.64A, Ind=3.683A. O/C Trip
|  | 2023-12-15 | 10:35 | 2023-12-15 | 10:37 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R Ph), Ir- 0.299 kA, Iy- 0.277 kA, Ib- 0.038 kA. -
|  | 2023-12-18 | 08:25 | 2023-12-18 | 08:28 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R-Ph), Ir- 0.303 kA, Iy- 0.262 kA, Ib- 0.046 kA. -
|  | 2023-12-29 | 07:12 | 2023-12-29 | 07:16 | 0.0027778 | 0 | 4 | [5 empty] | At Palasponga end: B/C Relay, O/C(R- Y), Ir- 0.502 kA, Iy- 0.442 kA, Ib- 0.287 kA. -
|  | 2024-01-06 | 07:57 | 2024-01-06 | 08:03 | 0.0041667 | 0 | 6 | [5 empty] | O/C, Ir- 0.538kA, Iy- 0.457kA, Ib- 0.295kA. -
|  | 2024-01-09 | 16:54 | 2024-01-09 | 16:58 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 0.507kA, Iy- 0.433kA, Ib- 0.332kA. -
|  | 2024-01-09 | 20:29 | 2024-01-09 | 20:32 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.484kA, Iy- 0.424kA, Ib- 0.314kA. -
|  | 2024-01-10 | 07:51 | 2024-01-10 | 07:53 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir- 0.516kA, Iy- 0.424kA, Ib- 0.314kA. -
|  | 2024-01-10 | 10:17 | 2024-01-10 | 10:20 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.493kA, Iy- 0.395kA, Ib- 0.291kA. -
|  | 2024-01-16 | 10:02 | 2024-01-16 | 10:06 | 0.0027778 | 0 | 4 | [5 empty] | At Palasponga end: O/C, Ir- 0.496 kA, Iy- 0.433 kA, Ib- 0.276 kA. -
|  | 2024-01-17 | 13:48 | 2024-01-17 | 13:51 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.299 kA, Iy- 0.19 kA, Ib- 0.121 kA. -
|  | 2024-01-21 | 14:35 | 2024-01-21 | 14:38 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.3 kA, Iy- 0.252 kA, Ib- 0.059 kA. -
|  | 2024-01-23 | 12:46 | 2024-01-23 | 12:48 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir- 0.307 kA, Iy- 0.259 kA, Ib- 0.053 kA. -
|  | 2024-01-28 | 15:35 | 2024-01-28 | 15:38 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 300.3A, Iy- 233.1A, Ib- 73.01A. -
|  | 2023-11-21 | 15:43 | 2023-11-21 | 15:46 | 0.0020833 | 0 | 3 | [5 empty] | Ir- 300.3A, Iy- 271.4A, Ib- 34.43A. -
|  | 2023-11-23 | 16:41 | 2023-11-23 | 16:43 | 0.0013889 | 0 | 2 | [5 empty] | Ir- 299.2A, Iy- 271.1A, Ib- 35.08A. -
|  | 2023-11-23 | 16:32 | 2023-11-23 | 16:35 | 0.0020833 | 0 | 3 | [5 empty] | Ir- 300.5A, Iy- 2.757 kA, Ib- 50.27A. -
|  | 2024-03-05 | 09:47 | 2024-03-05 | 09:50 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.3kA, Iy- 0.268kA, Ib- 0.037kA. -
|  | 2024-03-03 | 14:57 | 2024-03-03 | 14:59 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir-0.528kA, Iy-0.416kA, Ib- 0.326kA. -
|  | 2024-03-11 | 08:51 | 2024-03-11 | 08:55 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 0.528kA, Iy- 0.416kA, Ib- 0.326kA. -
|  | 2024-03-16 | 07:53 | 2024-03-16 | 07:57 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 5.283kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
368 | 132 kV Palasponga - Essar |  |  |  |  | 0.37014 | 14 | 56 | [7 empty] | 19.093 | 8760 | 99.83% | 285.1221 | 167254.68
|  | 2023-04-08 | 15:58 | 2023-04-08 | 16:06 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end with following relay indication. Relay at Joda end: B/U relay: Direction O/C trip, Fault Current: Ia=0.27KA,Ib=0.84KA,Ic=0.24KA, At Palasponga end : Not tripped.
|  | 2023-05-19 | 19:28 | 2023-05-19 | 19:58 | 0.020833 | 0 | 30 | [5 empty] | Tripped at both end with following relay indication: At Joda end: DP relay: FL=L2-N,Zone-1,Dist=6.43KM,Fault Current: Ia=235.84A,Ib=6.64KA,Ic=154.94A,In=6.43KA At PPG end: DP relay: BGT,Zone-1,Dist=31.11KM,Fault Current: Ia=245A,Ib=315A,Ic=174A,In=0,Ig=530A.
|  | 2023-05-31 | 14:51 | 2023-05-31 | 16:38 | 0.074306 | 0 | 38 | [5 empty] | Tripped at both end with following relay indication At Joda end:- D.P. Relay:FL: L2-N Zone-1,Dist. =2.2169KM Fault Current: IL1=230.62A, IL2=7754.55A, IL3=113.16A, IN=7521.04A At PPG end:- D.P. Relay,FL: BG T,Zone-1 Dist. =32.9KM Fault Current: Ia=241A, Ib=254A, Ic=128A, Ig=486A.
|  | 2023-07-03 | 11:27 | 2023-07-03 | 16:38 | 0.21597 | 0 | 27 | [5 empty] | At Joda end:- DP relay:- Zone-II, FL: L3-N, FD=46.038km, Fault Current:- Ia=209.25A, Ib=460.24A, Ic=2000.37A At Palasponga end:- DP relay:- Zone-I, CGT, Dist=1.43km, Fault Current:- Ia=231A, Ib=463A, Ic=530A, Ig=1090A,source fail from Karanjia end. B-Ph LA of Joda incomer burst at Palasponga end.
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:21 | 0.011111 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
|  | 2023-06-23 | 17:09 | 2023-06-23 | 17:21 | 0.0083333 | 0 | 12 | [5 empty] | Master trip relay, DP Relay: , Loc-22.5km, IL1=20.04KA,A,IL2=2.0KA,IL3=1.86KA,Distance pick up L12,L123-ON,Distance loop L1-2,L2-3,L3-1 ON,Power swing L2 L3 -ON,Distance trip 3P ON.. O/C TRIP
|  | 2023-07-03 | 12:25 | 2023-07-03 | 12:47 | 0.015278 | 0 | 22 | [5 empty] | NIL. Incomer failure
|  | 2023-04-14 | 13:38 | 2023-04-14 | 13:46 | 0.0055556 | 0 | 8 | [5 empty] | O/C TRIP ONLY AT PALASPANGA END, IA=507.5A,IB=421.5A,IC=370A, IG=4.0A.
|  | 2024-01-06 | 07:57 | 2024-01-06 | 08:03 | 0.0041667 | 0 | 6 | [5 empty] | O/C, Ir- 0.538kA, Iy- 0.457kA, Ib- 0.295kA. -
|  | 2024-01-10 | 10:17 | 2024-01-10 | 10:20 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.493kA, Iy- 0.395kA, Ib- 0.291kA. -
|  | 2024-03-03 | 14:57 | 2024-03-03 | 14:59 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Ir-0.528kA, Iy-0.416kA, Ib- 0.326kA. -
|  | 2024-03-11 | 08:51 | 2024-03-11 | 08:55 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 0.528kA, Iy- 0.416kA, Ib- 0.326kA. -
|  | 2024-03-16 | 07:53 | 2024-03-16 | 07:57 | 0.0027778 | 0 | 4 | [5 empty] | O/C, Ir- 5.283kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
369 | 132kV OPCL-Kamakhyanagar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 54.2 | 8760 | 100% | 0 | 474792
370 | 132kV Kamakhyanagar-Goda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 25.551 | 8760 | 100% | 0 | 223826.76
371 | 132kV Goda-Kalarangi |  |  |  |  | 0.1125 | 0 | 19 | [7 empty] | 10.326 | 8760 | 100% | 3.2699 | 90455.76
|  | 2023-10-03 | 14:18 | 2023-10-03 | 17:00 | 0.1125 | 0 | 19 | [5 empty] | At Kalarangi end: Zone 1, B-N, Dist- 7.066 km, Ib- 0.666 kA At Goda end: Zone 2, B-N, Dist- 9.8 km, Ib-4.62 kA. Heavy lightning and thunderstorm
372 | 132kV Kalarangi-Duburi |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 39.7 | 8760 | 100% | 12.5717 | 347772
|  | 2023-10-03 | 14:18 | 2023-10-03 | 14:37 | 0.013194 | 0 | 19 | [5 empty] | At Kalarangi end: Zone 1, B-N, Dist- 7.066 km, Ib- 0.666 kA At Goda end: Zone 2, B-N, Dist- 9.8 km, Ib-4.62 kA. Heavy lightning and thunderstorm
373 | 132kV Kamakhya Nagar - Kamakhya Nagar RTSS |  |  |  |  | 0.18403 | 14 | 0 | [7 empty] | 4.94 | 8760 | 99.84% | 69.16 | 43274.4
|  | 2023-10-01 | 20:51 | 2023-10-01 | 21:18 | 0.01875 | 0 | 27 | [5 empty] | LBB operated, Iy- 4.15 kA, Ib- 4.48 kA. -
|  | 2023-12-04 | 08:28 | 2023-12-04 | 08:33 | 0.0034722 | 0 | 5 | [5 empty] | O/C, Iy- 0.14kA, Ib- 0.14kA. -
|  | 2023-12-04 | 06:39 | 2023-12-04 | 06:48 | 0.00625 | 0 | 9 | [5 empty] | O/C, Iy- 0.15kA, Ib- 0.15kA. -
|  | 2024-01-15 | 11:29 | 2024-01-15 | 14:36 | 0.12986 | 0 | 42 | [5 empty] | No trippping at Kamakhyanagar end. At OPCL end: Ir- 0.13 kA, Iy- 0.13 kA, Ib- 1.74 kA. Grid pull-out as TTPS-OPCL Failed.
|  | 2023-04-10 | 07:21 | 2023-04-10 | 07:51 | 0.020833 | 0 | 30 | [5 empty] | Y,B phase tripped on O/C.
|  | 2023-04-13 | 10:40 | 2023-04-13 | 10:47 | 0.0048611 | 0 | 7 | [5 empty] | Y,B phase tripped on O/C.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
374 | 132kV Katapalli-Sambalpur |  |  |  |  | 0.1125 | 14 | 3 | [7 empty] | 21.85 | 8760 | 99.84% | 306.9925 | 191406
|  | 2023-07-29 | 19:48 | 2023-07-29 | 21:06 | 0.054167 | 0 | 42 | [5 empty] | At Sambalpur end:- Tripped on Yph E/F, Z4, Ia= 337.148A, Ib=1962.09A, Ic=212.926A, Ig=1413.675A, VA= 94kV, VB=107kV, VC=77kV, Vn=64kV, Fault dist.=2.76km At Katapali end:- Tripped on Z1, Fault dist.=11.7km. Transient fault
|  | 2023-10-07 | 17:23 | 2023-10-07 | 17:33 | 0.0069444 | 0 | 7 | [5 empty] | At Katapali end: O/C, Ir- 0.44 kA, Iy- 0.39 kA, Ib- 0.42 kA No tripping at Sambalpur end.. -
|  | 2023-09-19 | 09:39 | 2023-09-19 | 10:05 | 0.018056 | 0 | 26 | [5 empty] | Tripped at Katapali end.. Tripped at Katapali end only at 09:39 Hrs, on O/C E/F, Ia= 0.44KA, Ib=0.28KA,Ic=0.45KA.
|  | 2023-09-30 | 17:07 | 2023-09-30 | 17:55 | 0.033333 | 0 | 48 | [5 empty] | AT Sambalpur end:Tripped on Z1, Y-Bph O/C, Ia=179A, Ib=5297A,Ic=4117A, Ig=3339A, Fault dist.=7.1KM At Katapali end: Tripped with DP optd in zone-1 in Y & B phase, IR=4.639KA, IY=6.3KA, IB=5.8KA, fault distance=15.15km,fault duration=116.7ms , Relay trip time=100msec.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
375 | 132kV Katapalli-RTSS Godhbhaga |  |  |  |  | 0.021528 | 0 | 31 | [7 empty] | 10.66 | 8760 | 99.99% | 5.5077 | 93381.6
|  | 2023-09-01 | 16:59 | 2023-09-01 | 17:30 | 0.021528 | 0 | 31 | [5 empty] | Tripped with DP optd,master trip 86A optd ONLY, general trip, R & B phase, A/R successful in zone-1 , Indication on annunciation facia-GR-A/B trip relay optd, dist protection optd, dist protection optd zone-2/3, multiphase fault. No fault found. Rainy and cloudy condition
376 | 132kV Kendrapada-Marshaghai |  |  |  |  | 0.013889 | 0 | 20 | [7 empty] | 16.2 | 8760 | 100% | 5.4 | 141912
|  | 2024-03-04 | 23:41 | 2024-03-04 | 23:51 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara end: O/C , E/F, Ib- 0.225kA No tripping at Marshaghai end. Flashover due to climbing of a nocturnal animal at feeder breaker
|  | 2024-03-22 | 23:12 | 2024-03-22 | 23:22 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara end: E/F, Ir- 1.613kA, Iy- 1.572kA, Ib- 1.647kA No tripping at Marshaghai end. -
377 | 132kV Marshaghai-Paradeep |  |  |  |  | 0.051389 | 0 | 29 | [7 empty] | 19.61 | 8760 | 99.99% | 9.4782 | 171783.6
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 8 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
378 | 132kV Marshaghai-Kendrapara RTSS |  |  |  |  | 0.051389 | 0 | 30 | [7 empty] | 14.08 | 8760 | 99.99% | 7.04 | 123340.8
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 9 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
379 | 132kV Kendrapada-Paradeep |  |  |  |  | 0.05625 | 12 | 36 | [7 empty] | 15.77 | 8760 | 99.86% | 198.702 | 138145.2
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 8 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
380 | 132kV Kendrapada-Pattamundai |  |  |  |  | 0.61736 | 16 | 26 | [7 empty] | 19.1 | 8760 | 99.81% | 313.8767 | 167316
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-06-22 | 13:22 | 2023-06-22 | 13:38 | 0.011111 | 0 | 16 | [5 empty] | At Pattamundai end:- No tripping At RAMCO end:- DP, Z-1, Dist-23.1km, Ia=1.81kA, Ib=0.14kA, Ic=0.35kA. Supply failed from Jajpur Road. Supply was availed from Paradeep end.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
381 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 0.86181 | 22 | 16 | [7 empty] | 23.94 | 8760 | 99.75% | 533.064 | 209714.4
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:23 | 2023-06-22 | 13:38 | 0.010417 | 0 | 15 | [5 empty] | Incomer failed.. LINE WAS IDLE CHARGED FROM CHANDIKHOLE END.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:53 | 0.0055556 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:17 | 0.052083 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
382 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 1900-01-04 13:13 | 22 | 16 | [7 empty] | 23.94 | 8760 | 99.75% | 533.064 | 209714.4
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:23 | 2023-06-22 | 13:38 | 0.010417 | 0 | 15 | [5 empty] | Incomer failed.. LINE WAS IDLE CHARGED FROM CHANDIKHOLE END.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:53 | 0.0055556 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:17 | 0.052083 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
383 | 132kV Pattamundai-Rajnagar Ckt - I |  |  |  |  | 0.9125 | 23 | 29 | [7 empty] | 22.286 | 8760 | 99.73% | 523.3496 | 195225.36
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:22 | 2023-06-22 | 13:37 | 0.010417 | 0 | 15 | [5 empty] | Source failure. Supply failed from Jajpur Road. Supply was availed from Paradeep end.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:53 | 0.0055556 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:17 | 0.052083 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
|  | 2023-10-08 | 09:20 | 2023-10-08 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | 132kV P/S failed from source. -
|  | 2023-10-08 | 17:27 | 2023-10-08 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | 132kV P/S failed from source. -
|  | 2024-02-05 | 02:49 | 2024-02-05 | 03:49 | 0.041667 | 1 | 0 | [5 empty] | Tripped due to burst of R-Ph CT of 132kV Pattamundai-Rajnagar CKT-II. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
384 | 132kV Pattamundai-Rajnagar Ckt - II |  |  |  |  | 0.9125 | 23 | 29 | [7 empty] | 22.286 | 8760 | 99.73% | 523.3496 | 195225.36
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:22 | 2023-06-22 | 13:37 | 0.010417 | 0 | 15 | [5 empty] | Source failure. Supply failed from Jajpur Road. Supply was availed from Paradeep end.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:53 | 0.0055556 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:17 | 0.052083 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
|  | 2023-10-08 | 09:20 | 2023-10-08 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | 132kV P/S failed from source. -
|  | 2023-10-08 | 17:27 | 2023-10-08 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | 132kV P/S failed from source. -
|  | 2024-02-05 | 02:49 | 2024-02-05 | 03:49 | 0.041667 | 1 | 0 | [5 empty] | Tripped due to burst of R-Ph CT of 132kV Pattamundai-Rajnagar CKT-II. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
385 | 132kV Olavar - Chandabali Ckt - I |  |  |  |  | 1899-12-31 00:56 | 26 | 30 | [7 empty] | 12.5 | 8760 | 99.7% | 331.25 | 109500
|  | 2023-08-21 | 16:14 | 2023-08-21 | 16:41 | 0.01875 | 0 | 27 | [5 empty] | Source failure. -
|  | 2023-09-01 | 17:00 | 2023-09-01 | 18:51 | 0.077083 | 1 | 51 | [5 empty] | Source failure.
|  | 2023-09-04 | 08:37 | 2023-09-04 | 08:45 | 0.0055556 | 0 | 8 | [5 empty] | Source failure.
|  | 2023-09-04 | 19:30 | 2023-09-04 | 19:35 | 0.0034722 | 0 | 5 | [5 empty] | Source failure.
|  | 2023-09-08 | 09:39 | 2023-09-08 | 11:22 | 0.071528 | 1 | 43 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:23 | 2023-06-22 | 13:38 | 0.010417 | 0 | 15 | [5 empty] | Source Fail. PATTAMUNDAI GRID WAS AVAILING P/S FROM RAMCO END THROUGH KENDRAPARA RESERVE BUS.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:51 | 0.0041667 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:20 | 0.054167 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 7 | [5 empty] | B-N, Ib-0.53 kA, Dist- 11.1km. Alternate supply availed through 132kV Marsaghai-Kendrapara Feeder. Pattamundai availed P/S from Salipur end through Kendrapara Main bus.
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
386 | 132kV Olavar - Chandabali Ckt - II |  |  |  |  | 1899-12-31 00:03 | 26 | 23 | [7 empty] | 12.5 | 8760 | 99.7% | 329.7917 | 109500
|  | 2023-08-21 | 16:14 | 2023-08-21 | 16:41 | 0.01875 | 0 | 27 | [5 empty] | Source failure. -
|  | 2023-09-01 | 17:00 | 2023-09-01 | 18:51 | 0.077083 | 1 | 51 | [5 empty] | Source failure.
|  | 2023-09-04 | 08:37 | 2023-09-04 | 08:45 | 0.0055556 | 0 | 8 | [5 empty] | Source failure.
|  | 2023-09-04 | 19:30 | 2023-09-04 | 19:35 | 0.0034722 | 0 | 5 | [5 empty] | Source failure.
|  | 2023-09-08 | 09:39 | 2023-09-08 | 11:22 | 0.071528 | 1 | 43 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source failure. Supply failed from Paradeep end
|  | 2023-10-06 | 09:20 | 2023-10-06 | 09:27 | 0.0048611 | 0 | 7 | [5 empty] | Source failed. -
|  | 2023-10-06 | 17:27 | 2023-10-06 | 17:33 | 0.0041667 | 0 | 6 | [5 empty] | Source failed. -
|  | 2024-01-03 | 08:36 | 2024-01-03 | 12:38 | 0.16806 | 4 | 2 | [5 empty] | Source failure. Shutdown for replacement of 132kV main bus insulator string at Pattamundai GSS.
|  | 2023-06-22 | 13:23 | 2023-06-22 | 13:38 | 0.010417 | 0 | 15 | [5 empty] | Source Fail. PATTAMUNDAI GRID WAS AVAILING P/S FROM RAMCO END THROUGH KENDRAPARA RESERVE BUS.
|  | 2023-07-10 | 09:55 | 2023-07-10 | 09:59 | 0.0027778 | 0 | 4 | [5 empty] | Source failure.
|  | 2023-07-10 | 14:45 | 2023-07-10 | 14:51 | 0.0041667 | 0 | 6 | [5 empty] | Source failure.
|  | 2023-07-11 | 16:02 | 2023-07-11 | 17:20 | 0.054167 | 1 | 15 | [5 empty] | Source failure.
|  | 2023-06-07 | 09:59 | 2023-06-07 | 10:25 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure. Supply failed from Jajpur Road due to tripping of RAMCO feeder. Supply was availed from Paradeep end.
|  | 2023-09-03 | 15:24 | 2023-09-03 | 15:50 | 0.018056 | 0 | 26 | [5 empty] | Source failure.
|  | 2023-09-27 | 11:26 | 2023-09-27 | 11:31 | 0.0034722 | 0 | 5 | [5 empty] | At Kendrapara end:- No Tripping At Paradeep end:- DP, Zone-2, Dist=36km, Ia=279A, Ib=296A, Ic=595A. Supply failed from Paradeep end
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 12:14 | 2023-10-10 | 15:51 | 0.15069 | 0 | 13 | [5 empty] | At RAMCO end: Zone 1, Dist-35.2 km, Ib=1.54 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-10 | 11:50 | 2023-10-10 | 12:02 | 0.0083333 | 0 | 11 | [5 empty] | At RAMCO end: Zone 1,Dist-35.9KM, Ib=1.49 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-06-07 | 08:10 | 2023-06-07 | 08:18 | 0.0055556 | 0 | 8 | [5 empty] | Source Fail.
|  | 2023-06-17 | 12:17 | 2023-06-17 | 12:20 | 0.0020833 | 0 | 3 | [5 empty] | Incomer failed..
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:47 | 0.015972 | 0 | 23 | [5 empty] | Iy- 0.636kA, Ib- 0.631kA. -
|  | 2023-10-13 | 14:14 | 2023-10-13 | 14:25 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed due to tripping at RAMCO end. -
|  | 2023-04-14 | 09:11 | 2023-04-14 | 14:50 | 0.23542 | 0 | 31 | [5 empty] | AT KENDRAPARA End: TRIPPED ON DP RELAY, ZONE-1, DIST=2.77KM, Ir=512.234A, Iy=404.977A, Ib=275.684A, AT RAMCO END:tripped on DP Zone-1, fault loc- 35.8km at RAMCO end. Y-Ph jumper at Loc. No.-205 of 132kV Kendrapara-RAMCO Ckt snapped.. No power supply to Chandabali grid
|  | 2023-06-06 | 16:45 | 2023-06-06 | 17:19 | 0.023611 | 0 | 34 | [5 empty] | At Kendrapara end:- TRIPPED ON DP, ZONE-2, DIST.=21.13 KM,R-PHASE,Ir=4.494 KA,Iy=546.5 A,Ib=635.8 A At Pattamundai end:- DP, ZONE-1, DIST.=10.84 KM, Ir=480.5 A KA, Iy=432 A,Ib=532.5 A. Heavy rain
|  | 2023-06-17 | 11:14 | 2023-06-17 | 11:22 | 0.0055556 | 0 | 8 | [5 empty] | Incomer failed..
|  | 2023-09-10 | 12:17 | 2023-09-10 | 12:44 | 0.01875 | 0 | 27 | [5 empty] | Source Failure.
|  | 2023-09-27 | 11:25 | 2023-09-27 | 11:31 | 0.0041667 | 0 | 6 | [5 empty] | Source Failure. Supply failed from Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
387 | 132kV Dhamara - Chandabali Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.373 | 1140 | 100% | 0 | 31205.22
388 | 132kV Dhamara - Chandabali Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.373 | 1140 | 100% | 0 | 31205.22
389 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 1900-01-01 05:15 | 12 | 51 | [7 empty] | 76.15 | 8760 | 99.85% | 978.5275 | 667074
|  | 2023-08-24 | 11:32 | 2023-08-24 | 11:38 | 0.0041667 | 0 | 6 | [5 empty] | Over load. Over Load
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:23 | 0.089583 | 0 | 15 | [5 empty] | DP Relay, IR = 32A, IY = 17A, IB = 17A Indravati end-Broken conductor indication, IR = 288A, IY = 522A, IB = 443A.. System Failure at Therubali Grid
|  | 2023-12-28 | 12:32 | 30.12.23 | 15:32 | 1900-01-01 03:00 | 0 | 30 | [5 empty] | No tripping at Therubali end. At Muniguda end: B-N, Dist- 27.5 km, Zone 2, Ib- 0.913 kA. System out at Therubali end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
390 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.28 | 8760 | 100% | 0 | 501772.8
391 | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.075694 | 13 | 49 | [7 empty] | 39.81 | 8760 | 99.84% | 550.0415 | 348735.6
|  | 2023-08-05 | 13:11 | 2023-08-05 | 13:35 | 0.016667 | 0 | 24 | [5 empty] | At Bhawanipatna end:- E/F, Y=856.8A, IN=1.3kA At Kesinga end:- O/C, R-Phase. Fault at Kesinga end
|  | 2023-09-20 | 04:08 | 2023-09-20 | 04:18 | 0.0069444 | 0 | 10 | [5 empty] | Source failure. Power supply failed from Kesinga End
|  | 2023-05-28 | 23:22 | 2023-05-28 | 23:42 | 0.013889 | 0 | 20 | [5 empty] | ZONE-1. Samultaneouly 132 KV Incoming Failed from Kesinga
|  | 2023-05-24 | 20:21 | 2023-05-24 | 20:56 | 0.024306 | 0 | 35 | [5 empty] | Master trip.
|  | 2023-10-02 | 03:14 | 2023-10-02 | 03:23 | 0.00625 | 0 | 9 | [5 empty] | O/C. -
|  | 2023-12-06 | 00:54 | 2023-12-06 | 00:59 | 0.0034722 | 0 | 5 | [5 empty] | O/C. -
|  | 2023-08-24 | 11:32 | 2023-08-24 | 11:38 | 0.0041667 | 0 | 6 | [5 empty] | Over load. Over Load
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
392 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 0.03125 | 12 | 45 | [7 empty] | 24.76 | 8760 | 99.85% | 315.69 | 216897.6
|  | 2023-05-22 | 18:20 | 2023-05-22 | 18:37 | 0.011806 | 0 | 17 | [5 empty] | ZONE-1. Simultaneouly 132 KV Incoming Failed from Kesinga
|  | 2023-05-28 | 23:22 | 2023-05-28 | 23:42 | 0.013889 | 0 | 20 | [5 empty] | ZONE-1. Samultaneouly 132 KV Incoming Failed from Kesinga
|  | 2023-08-05 | 13:12 | 2023-08-05 | 13:20 | 0.0055556 | 0 | 8 | [5 empty] | At Junagarh end:- R-Y ph to E. 33kV Charbahal feeder VCB problem found.There was a delay in tripping due to which the TRF were tripped.The problem was rectified by E&Mr,Kesinga
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
393 | 132kV Kesinga-Junagarh |  |  |  |  | 0.00625 | 0 | 9 | [7 empty] | 53.3 | 8760 | 100% | 7.995 | 466908
|  | 2023-10-02 | 03:14 | 2023-10-02 | 03:23 | 0.00625 | 0 | 9 | [5 empty] | O/C. -
394 | 132kV Bhawanipatna- Lanjigarh RTSS |  |  |  |  | 0.71736 | 29 | 15 | [7 empty] | 34.18 | 8760 | 99.67% | 999.765 | 299416.8
|  | 2023-04-12 | 06:46 | 2023-04-12 | 06:49 | 0.0020833 | 0 | 3 | [5 empty] | O/C.
|  | 2023-10-09 | 16:02 | 2023-10-09 | 16:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C. -
|  | 2023-10-12 | 05:30 | 2023-10-12 | 05:32 | 0.0013889 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-10-13 | 21:46 | 2023-10-13 | 21:49 | 0.0020833 | 0 | 3 | [5 empty] | O/C. -
|  | 2023-10-14 | 04:53 | 2023-10-14 | 04:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-12-16 | 19:44 | 2023-12-16 | 19:47 | 0.0020833 | 0 | 3 | [5 empty] | Tripped on O/C. -
|  | 2023-10-02 | 05:06 | 2023-10-02 | 05:08 | 00:02 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-10-05 | 09:18 | 2023-10-05 | 09:21 | 0.0020833 | 0 | 3 | [5 empty] | O/C. -
|  | 2023-10-06 | 08:47 | 2023-10-06 | 08:49 | 0.0013889 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-10-07 | 06:49 | 2023-10-07 | 06:53 | 0.0027778 | 0 | 4 | [5 empty] | O/C. -
|  | 2023-11-04 | 12:29 | 2023-11-04 | 12:32 | 0.0020833 | 0 | 3 | [5 empty] | O/C. -
|  | 2023-11-15 | 21:08 | 2023-11-15 | 21:09 | 0.00069444 | 0 | 1 | [5 empty] | O/C. -
|  | 2023-12-19 | 23:35 | 2023-12-19 | 23:37 | 0.0013889 | 0 | 2 | [5 empty] | Tripped on O/C. -
|  | 2023-12-28 | 12:41 | 2023-12-28 | 12:46 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on O/C. -
|  | 2024-01-10 | 16:21 | 2024-01-10 | 16:23 | 0.0013889 | 0 | 2 | [5 empty] | O/C. -
|  | 2024-01-16 | 19:25 | 2024-01-16 | 19:26 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on O/C. -
|  | 2024-01-21 | 19:00 | 2024-01-21 | 19:02 | 0.0013889 | 0 | 2 | [5 empty] | Tripprd on O/C. -
|  | 2024-01-29 | 05:39 | 2024-01-29 | 05:40 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on O/C. -
|  | 2024-03-03 | 06:02 | 2024-03-03 | 06:04 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 0.273kA, Ib- 0.268kA. -
|  | 2024-03-09 | 14:17 | 2024-03-09 | 14:19 | 0.0013889 | 0 | 2 | [5 empty] | O/C, E/F, Iy- 660mA, Ib- 648mA. -
|  | 2024-03-10 | 19:00 | 2024-03-10 | 19:02 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 660mA, Ib- 648mA. -
|  | 2024-03-13 | 19:00 | 2024-03-13 | 19:02 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 661mA, Ib- 648mA. -
|  | 2024-03-14 | 10:47 | 2024-03-14 | 10:49 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 669mA, Ib- 656mA. -
|  | 2024-03-17 | 19:09 | 2024-03-17 | 19:11 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 654mA, Ib- 641mA. -
|  | 2024-03-28 | 21:04 | 2024-03-28 | 21:07 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Iy- 662mA, Ib- 650mA. -
|  | 2024-03-29 | 18:52 | 2024-03-29 | 18:53 | 0.00069444 | 0 | 1 | [5 empty] | O/C, Iy- 661mA, Ib- 650mA. -
|  | 2023-06-03 | 03:44 | 2023-06-03 | 03:47 | 0.0020833 | 0 | 3 | [5 empty] | TRIPPED ON O/C.
|  | 2023-06-06 | 16:42 | 2023-06-06 | 16:50 | 0.0055556 | 0 | 8 | [5 empty] | TRIPPED ON DIR O/C & E/F.
|  | 2023-07-01 | 19:37 | 2023-07-01 | 19:41 | 0.0027778 | 0 | 4 | [5 empty] | O/C.
|  | 2023-07-25 | 14:18 | 2023-07-25 | 14:28 | 0.0069444 | 0 | 10 | [5 empty] | O/C.
|  | 2023-08-10 | 21:01 | 2023-08-10 | 21:06 | 0.0034722 | 0 | 5 | [5 empty] | O/C. Over Load
|  | 2023-08-24 | 7:57 | 2023-08-24 | 8:03 | 0.0041667 | 0 | 6 | [5 empty] | O/C. Over Load
|  | 2023-08-26 | 5:45 | 2023-08-26 | 5:51 | 0.0041667 | 0 | 6 | [5 empty] | O/C. Over Load
|  | 2023-08-30 | 9:41 | 2023-08-30 | 9:50 | 0.00625 | 0 | 9 | [5 empty] | O/C. Over Load
|  | 2023-08-30 | 19:17 | 2023-08-30 | 19:20 | 0.0020833 | 0 | 3 | [5 empty] | O/C. Over Load
|  | 2023-09-12 | 01:35 | 2023-09-12 | 01:38 | 0.0020833 | 0 | 3 | [5 empty] | O/C. Over Load
|  | 2023-09-20 | 04:08 | 2023-09-20 | 17:26 | 0.55417 | 13 | 18 | [5 empty] | E/F. Jumper snapped at Loc.No.64
|  | 2023-09-29 | 06:15 | 2023-09-29 | 06:17 | 0.0013889 | 0 | 2 | [5 empty] | O/C. Over Load
|  | 2024-03-07 | 13:59 | 2024-03-07 | 14:01 | 0.0013889 | 0 | 2 | [5 empty] | O/C, Iy- 0.273A, Ib- 0.268A. -
|  | 2024-03-07 | 14:08 | 2024-03-07 | 14:13 | 0.0034722 | 0 | 5 | [5 empty] | O/C, E/F, Iy- 0.674A, Ib- 0.662A. -
|  | 2023-05-22 | 18:20 | 2023-05-22 | 18:37 | 0.011806 | 0 | 17 | [5 empty] | ZONE-1. Simultaneouly 132 KV Incoming Failed from Kesinga
|  | 2023-05-28 | 23:22 | 2023-05-28 | 23:42 | 0.013889 | 0 | 20 | [5 empty] | ZONE-1. Samultaneouly 132 KV Incoming Failed from Kesinga
|  | 2023-08-05 | 13:12 | 2023-08-05 | 13:20 | 0.0055556 | 0 | 8 | [5 empty] | At Junagarh end:- R-Y ph to E. 33kV Charbahal feeder VCB problem found.There was a delay in tripping due to which the TRF were tripped.The problem was rectified by E&Mr,Kesinga
|  | 2023-05-24 | 20:21 | 2023-05-24 | 20:56 | 0.024306 | 0 | 35 | [5 empty] | Master trip.
|  | 2023-07-05 | 11:44 | 2023-07-05 | 11:57 | 0.0090278 | 0 | 13 | [5 empty] | O/C.
|  | 2023-07-06 | 12:33 | 2023-07-06 | 12:45 | 0.0083333 | 0 | 12 | [5 empty] | O/C.
|  | 2023-08-24 | 11:32 | 2023-08-24 | 11:38 | 0.0041667 | 0 | 6 | [5 empty] | Over load. Over Load
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
395 | 132kV Bhawanipatna- Bhawanipatna RTSS |  |  |  |  | 0.060417 | 13 | 27 | [7 empty] | 2.102 | 7188 | 99.81% | 28.2719 | 15109.176
|  | 2023-12-16 | 16:13 | 2023-12-16 | 16:18 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on O/C. -
|  | 2023-12-16 | 16:23 | 2023-12-16 | 16:26 | 0.0020833 | 0 | 3 | [5 empty] | Tripped on O/C. -
|  | 2023-12-16 | 16:29 | 2023-12-16 | 16:44 | 0.010417 | 0 | 15 | [5 empty] | Tripped on O/C. -
|  | 2023-07-10 | 16:10 | 2023-07-10 | 16:43 | 0.022917 | 0 | 33 | [5 empty] | O/C , E/F.
|  | 2023-07-05 | 11:44 | 2023-07-05 | 11:57 | 0.0090278 | 0 | 13 | [5 empty] | O/C.
|  | 2023-07-06 | 12:33 | 2023-07-06 | 12:45 | 0.0083333 | 0 | 12 | [5 empty] | O/C.
|  | 2023-08-24 | 11:32 | 2023-08-24 | 11:38 | 0.0041667 | 0 | 6 | [5 empty] | Over load. Over Load
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
396 | 132kV Kesinga-Kesinga RTSS |  |  |  |  | 0 | 0 | 26 | [7 empty] | 4.952 | 8760 | 100% | 2.1459 | 43379.52
|  | 2023-09-25 | 17:32 | 2023-09-25 | 17:58 | 00:26 | 0 | 26 | [5 empty] | At Kesinga end:- O/C,R &B Phase. O/C Lightning &heavy Rain
397 | 132kV Kesinga-Powmex |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.53 | 8760 | 100% | 0 | 127282.8
398 | 132kV Kesinga- Vento Solar ckt-I |  |  |  |  | 0.047222 | 13 | 8 | [7 empty] | 5.74 | 8760 | 99.85% | 75.3853 | 50282.4
|  | 2023-12-06 | 00:54 | 2023-12-06 | 00:59 | 0.0034722 | 0 | 5 | [5 empty] | O/C. -
|  | 2023-12-06 | 00:14 | 2023-12-06 | 00:53 | 0.027083 | 0 | 39 | [5 empty] | O/C. -
|  | 2023-12-06 | 02:03 | 2023-12-06 | 02:27 | 0.016667 | 0 | 24 | [5 empty] | O/C. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
399 | 132kV Kesinga- Vento Solar ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.74 | 8760 | 100% | 0 | 50282.4
400 | 132kV Kharagprasad-Meramundali RTSS |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 1.17 | 8760 | 99.95% | 4.6605 | 10249.2
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
401 | 132kV Kharagprasad-MGM |  |  |  |  | 0.38056 | 9 | 8 | [7 empty] | 7.14 | 8760 | 99.9% | 65.212 | 62546.4
|  | 2023-07-31 | 12:44 | 2023-07-31 | 17:53 | 0.21458 | 5 | 9 | [5 empty] | Yph-Bph-E, Z-1, If=10.5kA. Jumper snapped
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
402 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 0.577 | 8760 | 99.95% | 2.2984 | 5054.52
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
403 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 0.577 | 8760 | 99.95% | 2.2984 | 5054.52
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
404 | 132kV Kharagprasad-Samal Metallic (SGEL) |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 1.03 | 8760 | 99.95% | 4.1028 | 9022.8
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
405 | 132kV Kuchei PG- Bangiriposhi Ckt-I |  |  |  |  | 0.175 | 15 | 42 | [7 empty] | 31.13 | 8760 | 99.82% | 488.741 | 272698.8
|  | 2023-09-02 | 03:48 | 2023-09-02 | 05:19 | 0.063194 | 1 | 31 | [5 empty] | At Kuchei end:- B/U Relay:- I>>Dir.Trip, O/C B phase Trip, Ib- 0.19k A Source failure Started phase=CAN,Trip zone=2,Ia=301.9A,Ib=364.3A, Ic=324.8A. Line Fault & feeder tripped from kuchei grid end Source fail No area Load Affected due to prevailing L/R at both end. Supply availed from Karanjia gss end(04:17 hrs to 05:33hrs) Line Fault
|  | 2024-02-07 | 06:11 | 2024-02-07 | 06:39 | 0.019444 | 0 | 28 | [5 empty] | At Kuchei end: B/U Relay: Ir- 0.4kA, O/C (R-Ph). -
|  | 2023-08-16 | 18:32 | 2023-08-16 | 20:28 | 0.080556 | 1 | 26 | [5 empty] | Incomer failure. O/C Rph, Ir=0.13kA
|  | 2023-07-03 | 12:25 | 2023-07-03 | 12:42 | 0.011806 | 0 | 17 | [5 empty] | NIL. Tripped at Kuchei grid end due to over drawal
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
406 | 132kV Kuchei PG- Bangiriposhi Ckt-II |  |  |  |  | 0.15694 | 15 | 16 | [7 empty] | 31.256 | 8760 | 99.83% | 477.1749 | 273802.56
|  | 2023-09-02 | 03:48 | 2023-09-02 | 05:19 | 0.063194 | 1 | 31 | [5 empty] | At Kuchei end:- B/U Relay:- I>>Dir.Trip, O/C B phase Trip, Ib- 0.19k A Source failure Started phase=CAN,Trip zone=2,Ia=301.9A,Ib=364.3A, Ic=324.8A. Line Fault & feeder tripped from kuchei grid end Source fail No area Load Affected due to prevailing L/R at both end. Supply availed from Karanjia gss end(04:17 hrs to 05:33hrs) Line Fault
|  | 2023-09-23 | 09:35 | 2023-09-23 | 09:37 | 0.0013889 | 0 | 2 | [5 empty] | Source failure. Source fail
|  | 2023-08-16 | 18:32 | 2023-08-16 | 20:28 | 0.080556 | 1 | 26 | [5 empty] | B/U Relay: (Kuchei Gss), I>> Dir. Trip, Picckup Time-78ms, Trip Time : 55ms, O/C R-phase Trip, Ir-0.13kA. -
|  | 2023-07-03 | 12:25 | 2023-07-03 | 12:42 | 0.011806 | 0 | 17 | [5 empty] | NIL. Tripped at Kuchei grid end due to over drawal
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
407 | 132kV Bangiriposhi- Rairangapur |  |  |  |  | 0.15556 | 13 | 55 | [7 empty] | 34.2 | 8760 | 99.84% | 475.95 | 299592
|  | 2023-09-02 | 03:48 | 2023-09-02 | 05:19 | 0.063194 | 0 | 35 | [5 empty] | At Kuchei end:- B/U Relay:- I>>Dir.Trip, O/C B phase Trip, Ib- 0.19k A Source failure Started phase=CAN,Trip zone=2,Ia=301.9A,Ib=364.3A, Ic=324.8A. Line Fault & feeder tripped from kuchei grid end Source fail No area Load Affected due to prevailing L/R at both end. Supply availed from Karanjia gss end(04:17 hrs to 05:33hrs) Line Fault
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
|  | 2023-08-16 | 18:32 | 2023-08-16 | 19:56 | 0.058333 | 0 | 31 | [5 empty] | Incomer failure. O/C Rph, Ir=0.13kA
|  | 2023-07-03 | 12:23 | 2023-07-03 | 12:50 | 0.01875 | 0 | 27 | [5 empty] | At Karanjia end:- DP relay:- General Trip, R-G, Y-G, Zone-4, Trip time=1ms, Distance pick up=L12, I4=0.18kA, IL2=0.16kA, IL3=0.13kA, Dist=-4.2km, Tripped at Kuchei end. Source failure. Due to over loading
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
408 | 132kV Rairangapur- Karanjia |  |  |  |  | 0.94722 | 17 | 32 | [7 empty] | 70.74 | 8760 | 99.8% | 1240.308 | 619682.4
|  | 2023-09-02 | 03:48 | 2023-09-02 | 05:19 | 0.063194 | 0 | 21 | [5 empty] | At Kuchei end:- B/U Relay:- I>>Dir.Trip, O/C B phase Trip, Ib- 0.19k A Source failure Started phase=CAN,Trip zone=2,Ia=301.9A,Ib=364.3A, Ic=324.8A. Line Fault & feeder tripped from kuchei grid end Source fail No area Load Affected due to prevailing L/R at both end. Supply availed from Karanjia gss end(04:17 hrs to 05:33hrs) Line Fault
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
|  | 2023-08-16 | 18:31 | 2023-08-16 | 19:04 | 0.022917 | 0 | 31 | [5 empty] | Source failure at Karanjia end. -
|  | 2023-07-03 | 12:22 | 2023-07-03 | 12:57 | 0.024306 | 0 | 27 | [5 empty] | At Karanjia end:- DP relay:- General Trip, R-G, Y-G, Zone-4, Trip time=1ms, Distance pick up=L12, I4=0.18kA, IL2=0.16kA, IL3=0.13kA, Dist=-4.2km, Tripped at Kuchei end. Source failure. Due to over loading
|  | 2023-04-14 | 12:51 | 2023-04-14 | 13:01 | 0.0069444 | 0 | 10 | [5 empty] | No relay indication at Karanjia GSS, At Rairangpur end: R phase to N,Zone-1,fault distance- 7.30km,IR-1.717KA,IY-91.28A,IB-237A. R- phase Insulator Puncture at Location no-312 of said line KARANJIA GRID P/S AVAILED FROM POLASPANGA END. Test charged but again
|  | 2023-04-14 | 13:01 | 2023-04-14 | 17:54 | 0.20347 | 0 | 22 | [5 empty] | At Rairangpur - ZONE-1,R-PHASE -N,DIST-7.062KM IA-1.665KA,IB-159.1A, IC-247.2A. R- phase Insulator Puncture at Location no-312 of said line KARANJIA GRID P/S AVAILED FROM POLASPANGA END. Test charged but again
|  | 2023-04-16 | 18:05 | 2023-04-16 | 18:21 | 0.011111 | 0 | 16 | [5 empty] | At Rairangpur -ZONE-1,B-PHASE -N, DIST-44.05KM IA-963.8A, IB-1.332KA,IC-177.6A At Karanjia-ZONE-1,LOOP L2-E, DIST-46.1KM IA-0.25KA,IB-0.29KA,IC-0.20A [SULATOR PUNCHER FOUND AT LOC. NO 226]. Test charge done & stood ok. T
|  | 2023-06-03 | 16:36 | 2023-06-03 | 17:27 | 0.035417 | 0 | 51 | [5 empty] | At Karanjia end:- R-E, Zone-1,fault distance-29Km, IR- 0.26KA, IY-0.25KA, IB-0.26KA At Rairangpur end:- R- N, Zone-1, SOFT OPTD, Zone-4, IR- 97.92A, IY-0A, IB-0A. Heavy rainfall, lightning and thunder storm observed
|  | 2023-10-03 | 00:52 | 2023-10-03 | 01:32 | 0.027778 | 0 | 40 | [5 empty] | At Karanjia end: B-N, Dist- 11.9 km, Ir- 0.17 kA, Iy- 0.15 kA, Ib- 0.23 kA No relay indication at Rairangpur GSS. Core 1 control cable from Console box to C/R panel of R-Ph CVT was damaged due to rat bite. Karanjia & Dhenkikote GSS availed power from Palaspanga GSS
|  | 2023-10-03 | 01:43 | 2023-10-03 | 08:03 | 0.26389 | 0 | 42 | [5 empty] | At Karanjia end: R-Y, Dist- 21.9 km, Ir- 0.07 kA, Iy- 0.06 kA, Ib- 0.07 kA No relay indication at Rairangpur GSS. Core 1 control cable from Console box to C/R panel of R-Ph CVT was damaged due to rat bite. Karanjia & Dhenkikote GSS availed power from Palaspanga GSS
|  | 2024-03-19 | 04:53 | 2024-03-19 | 11:26 | 0.27292 | 0 | 50 | [5 empty] | At Karanjia end: R-N, Dist- 94.8km At Rairangpur end: R-N, Ir- 99.044A, Iy- 198.8A, Ib- 2.204kA, Dist- 311.8km. Karanjia & Dhenkikote availed power supply from Polaspanga gss end. 132kV B-Ph LA Burst at Rairangpur.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
409 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0.20139 | 16 | 48 | [7 empty] | 40.7 | 8760 | 99.81% | 683.76 | 356532
|  | 2023-09-02 | 03:48 | 2023-09-02 | 04:09 | 0.014583 | 0 | 21 | [5 empty] | Source failure from Karanjia end. Line Fault & feeder tripped from kuchei grid end Source fail No area Load Affected due to prevailing L/R at both end. Supply availed from Karanjia gss end(04:17 hrs to 05:33hrs) Line Fault
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
|  | 2023-06-17 | 18:19 | 2023-06-17 | 18:31 | 0.0083333 | 0 | 12 | [5 empty] | Broken conducter, DP, Ia-54.40A Ib-65.58A,Ic-39.85A.
|  | 2023-06-24 | 13:41 | 2023-06-24 | 13:46 | 0.0034722 | 0 | 5 | [5 empty] | Broken conducter, DP, Ia-49.79A Ib-63.60A,Ic-32.41A. Broken conducter
|  | 2023-08-16 | 18:31 | 2023-08-16 | 19:04 | 0.022917 | 0 | 31 | [5 empty] | Source failure at Karanjia end. -
|  | 2023-07-03 | 11:34 | 2023-07-03 | 11:51 | 0.011806 | 0 | 17 | [5 empty] | At Joda end:- DP relay:- Zone-II, FL: L3-N, FD=46.038km, Fault Current:- Ia=209.25A, Ib=460.24A, Ic=2000.37A At Palasponga end:- DP relay:- Zone-I, CGT, Dist=1.43km, Fault Current:- Ia=231A, Ib=463A, Ic=530A, Ig=1090A,source fail from Karanjia end. B-Ph LA of Joda incomer burst at Palasponga end.
|  | 2023-04-14 | 12:51 | 2023-04-14 | 13:05 | 0.0097222 | 0 | 14 | [5 empty] | INCOMER FAIL FROM KARANJIA END. R- phase Insulator Puncture at Location no-312 of said line KARANJIA GRID P/S AVAILED FROM POLASPANGA END. Test charged but again
|  | 2023-04-14 | 13:39 | 2023-04-14 | 13:46 | 0.0048611 | 0 | 7 | [5 empty] | INCOMER FAIL FROM KARANJIA END. R- phase Insulator Puncture at Location no-312 of said line KARANJIA GRID P/S AVAILED FROM POLASPANGA END. Test charged but again
|  | 2023-04-16 | 18:06 | 2023-04-16 | 18:22 | 0.011111 | 0 | 16 | [5 empty] | INCOMER FAIL FROM KARANJIA END. Test charge done & stood ok. T
|  | 2023-04-25 | 14:05 | 2023-04-25 | 14:29 | 0.016667 | 0 | 24 | [5 empty] | At Karanjia: R phase to N,Zone-1,fault distance- 11.58Km,IR- 1.129KA,IY-43.03A,IB-73.42A, No relay indication at Dhenkikote end.
|  | 2023-05-26 | 13:36 | 2023-05-26 | 14:04 | 0.019444 | 0 | 28 | [5 empty] | R,B -N,Zone-1,fault distance- 28.7Km,IR-913.6A,IY-880.53A,IB- 1008A.
|  | 2023-06-03 | 16:36 | 2023-06-03 | 17:28 | 0.036111 | 0 | 52 | [5 empty] | Source failure. Heavy rainfall, lightning and thunder storm observed
|  | 2024-03-26 | 16:40 | 2024-03-26 | 17:02 | 0.015278 | 0 | 22 | [5 empty] | At Karanjia end: R-N, Zone 1, Dist- 4.088km, Ir- 1.271kA No Indication at Dhenkikote end. Heavy Rainfall, lightning & thunderstorm
|  | 2023-07-03 | 12:25 | 2023-07-03 | 12:42 | 0.011806 | 0 | 17 | [5 empty] | NIL. Tripped at Kuchei grid end due to over drawal
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
410 | 132kV Karanjia-Palasponga |  |  |  |  | 0.026389 | 0 | 27 | [7 empty] | 83.2 | 6756 | 99.99% | 37.44 | 562099.2
|  | 2023-07-03 | 12:20 | 2023-07-03 | 12:58 | 0.026389 | 0 | 27 | [5 empty] | Source failure. B-Ph LA of Joda incomer burst at Palasponga end.
411 | 132kV Karanjia-Turumunga |  |  |  |  | 0.015278 | 0 | 22 | [7 empty] | 35.443 | 2004 | 99.98% | 12.9958 | 71027.772
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
412 | 132kV Turumunga-Palasponga |  |  |  |  | 0.015278 | 0 | 22 | [7 empty] | 111.125 | 2004 | 99.98% | 40.7458 | 222694.5
|  | 2024-02-08 | 03:36 | 2024-02-08 | 03:58 | 0.015278 | 0 | 22 | [5 empty] | At Bangiriposi end: B/U Relay: O/C (R- Ph), Ir- 0.37kA, Iy- 0.24kA, Ib- 0.2kA, CVT Fuse fail.
413 | 132kV Kuchinda-SHIVA (Kutra) |  |  |  |  | 0.025694 | 0 | 16 | [7 empty] | 110 | 8760 | 100% | 29.3333 | 963600
|  | 2023-05-20 | 16:36 | 2023-05-20 | 17:13 | 0.025694 | 0 | 16 | [5 empty] | Tripped on D/P,Phase B-N,Fault Loc-37.14km,,IB=2304A.
414 | 132kV SHIVA (Kutra)-Rajgangpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23 | 8760 | 100% | 0 | 201480
415 | 132kV SHIVA (Kutra)-SHIVA Cement |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.01 | 8760 | 100% | 0 | 26367.6
416 | 132kV Kuchinda-Rajgangpur 'T' to Bamra RTSS |  |  |  |  | 0.22778 | 1 | 3 | [7 empty] | 10 | 8760 | 99.99% | 10.5 | 87600
|  | 2023-08-30 | 17:54 | 2023-08-30 | 22:36 | 0.19583 | 0 | 17 | [5 empty] | At Budhipadar end:- D/P 1(MICOM P444):Y ph-E, Zone 2, Fault dist- 83.37km, D/P 2(SIEMENS ): Y ph-E, Zone 2, Fault Dist-84.4km(164%), IL2- 2.17kA At Bamra end:- CB did not trip. Fault in 220kV Bamra - Tarkera feeder
|  | 2023-08-17 | 9:33 | 2023-08-17 | 10:19 | 0.031944 | 0 | 46 | [5 empty] | Master Trip, R-PH O/C, IA=2.672kA, IB=196.6A, IC=84 A, Zone-1, Fault Duration=71.72ms, Fault Resistance=6.530Ω, Dist=28.65km. -
417 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 0.75 | 23 | 35 | [7 empty] | 12.31 | 8760 | 99.73% | 290.3108 | 107835.6
|  | 2023-06-19 | 10:43 | 2023-06-19 | 12:31 | 0.075 | 1 | 48 | [5 empty] | At Lapanga end:- R-PH-G, DIST-0.45KM, Z1, IL1-2.1KA. FIRE INSIDE GSS
|  | 2023-07-29 | 20:00 | 2023-07-29 | 20:08 | 0.0055556 | 0 | 8 | [5 empty] | At Lapanga end:- MAIN:- Zone-1, No more detailes recorded.
|  | 2024-01-15 | 00:36 | 2024-01-15 | 16:40 | 0.66944 | 9 | 39 | [5 empty] | At Lapanga: Y-N, Iy- 8.7 kA, Zone 1. Tripped as a reflection of RTSS fault (B phase insulator string of RTSS Rengali feeder damaged)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
418 | 132kV Machkund PH-Jaynagar |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 42.6 | 8760 | 100% | 0 | 373176
419 | 132kV Machkund PH- Machkund RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 107 | 8760 | 100% | 0 | 937320
420 | 132kV Mendhasal-Khurda |  |  |  |  | 0.082639 | 13 | 40 | [7 empty] | 17.6 | 8760 | 99.84% | 240.5333 | 154176
|  | 2023-04-11 | 02:41 | 2023-04-11 | 03:44 | 0.04375 | 0 | 44 | [5 empty] | ATRI END POWER FAILURE.AS POWER WAS AVAILED FROM ATRI END,BANKI GRID PULLED OUT.COMPLETE POWER FAILURE
|  | 2023-06-18 | 22:55 | 2023-06-18 | 23:02 | 0.0048611 | 0 | 7 | [5 empty] | S/F 40. Bad Weather. M/S failed from MSAL end
|  | 2023-06-19 | 00:17 | 2023-06-19 | 00:46 | 0.020139 | 0 | 29 | [5 empty] | Source Failure. Bad Weather. M/S failed from Mendhasal end
|  | 2023-11-15 | 09:10 | 2023-11-15 | 09:30 | 0.013889 | 0 | 20 | [5 empty] | At Atri end: CKT I: R-N, Zone 2, Dist- 12.7 km, Ir- 3.266 kA; CKT II: R-N, Zone 2, Dist-9.334 km, Ir- 3.419 kA. Grid pulled out due to bursting of 132kV LA in R-Ph of TRF I
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
421 | 132kV Meramundali-BRG |  |  |  |  | 0.095139 | 14 | 17 | [7 empty] | 3.55 | 8760 | 99.84% | 50.7058 | 31098
|  | 2023-10-17 | 05:31 | 2023-10-17 | 06:31 | 0.041667 | 1 | 0 | [5 empty] | MT, Directional O/C 67 R operated.. Fault occurred in 11 kV system at BRG
|  | 2023-07-23 | 06:04 | 2023-07-23 | 06:36 | 0.022222 | 0 | 32 | [5 empty] | At Meramundali end:- R & B Ph Directional O/C, M/T At BRG end:- No tripping. No fault found
|  | 2024-01-27 | 13:29 | 2024-01-27 | 13:39 | 0.0069444 | 0 | 10 | [5 empty] | Directional O/C, M/T, Ir- 0.21 kA, Iy- 0.21 kA, Ib- 0.21 kA. -
|  | 2024-02-27 | 07:59 | 2024-02-27 | 08:13 | 0.0097222 | 0 | 14 | [5 empty] | Directional O/C, Ir- 0.22kA, Iy- 0.22kA, Ib- 0.22kA. -
|  | 2024-02-27 | 15:06 | 2024-02-27 | 15:13 | 0.0048611 | 0 | 7 | [5 empty] | Directional O/C, Ir- 0.22kA, Iy- 0.22kA, Ib- 0.22kA. -
|  | 2024-02-28 | 15:09 | 2024-02-28 | 15:13 | 0.0027778 | 0 | 4 | [5 empty] | Directional O/C , Ir- 0.22kA, Iy- 0.22kA, Ib- 0.22kA. -
|  | 2024-02-28 | 23:58 | 2024-02-29 | 0:08 | 0.0069444 | 0 | 10 | [5 empty] | Directional O/C, Ir- 0.22kA, Iy- 0.23kA, Ib- 0.22kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
422 | 132kV Meramundali- RML (DSP) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.53 | 8760 | 100% | 0 | 92242.8
423 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 1.728 | 8760 | 99.99% | 0.9792 | 15137.28
|  | 2023-06-04 | 19:02 | 2023-06-04 | 19:19 | 0.011806 | 0 | 17 | [5 empty] | Tripped at Meramandali end on Directional Over Current B phase & E/F. IA=0.16kA, IB=2.34kA, IC=1.90kA..
|  | 2023-10-07 | 21:39 | 2023-10-07 | 21:56 | 0.011806 | 0 | 17 | [5 empty] | At Chainpal end: Ir-0.4 kA, Iy- 2.8 kA, Ib-2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
424 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0.023611 | 0 | 34 | [7 empty] | 1.728 | 8760 | 99.99% | 0.9792 | 15137.28
|  | 2023-06-04 | 19:02 | 2023-06-04 | 19:19 | 0.011806 | 0 | 17 | [5 empty] | Tripped at Meramandali end on Directional Over Current B phase & E/F. IA=0.10kA, IB=2.36kA, IC=1.85kA..
|  | 2023-10-07 | 21:39 | 2023-10-07 | 21:56 | 0.011806 | 0 | 17 | [5 empty] | At Chainpal end: Ir-0.4 kA, Iy- 2.8 kA, Ib-2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
425 | 132kV Meramundali-Dhenkanal |  |  |  |  | 1899-12-31 05:57 | 0 | 15 | [7 empty] | 51.12 | 8760 | 100% | 12.78 | 447811.2
|  | 2023-06-04 | 20:24 | 06.06.23 | 2:21 | 1899-12-31 05:57 | 0 | 15 | [5 empty] | At Dhenkanal end:- DP relay operated, Z-1, Dist.- 7.536km, Ia=1.678KA, Ib=1.814KA, Ic=1.721KA At Meramundali end:- DP relay operated, Z-1, Dist.=27.65km, Ia=4.36KA, Ib=4.46KA, Ic=4.13KA [B-Ph Conductor from S/Y Gantry beam to Tower No-1 has been snapped and fell on 33 KV Bus at MRDL End and also B-Ph Wavetrap has been damaged]. LC taken by MRDL grid to attend the B/D. 132KV DKL-MRDL line was B/D. So no power supply to the station. Fault occured at Meramundali grid ,Power failure from 132KV DKL fdr . As the said period the 132 kV ICCL Fdr was in H/T condition at ICCL end, At 20:47 hrs 132KV supply availed from ICCL end.
426 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 5.517 | 8760 | 99.95% | 21.9761 | 48328.92
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: B/U:-Ir- 1.8 A, Iy- 957 A, Ib- 102.7 A At Kharagprasad end: B/U:-R-Y-B, Ir- 435 A, Iy- 108 A, Ib- 2.66 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
427 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0.16597 | 3 | 59 | [7 empty] | 5.517 | 8760 | 99.95% | 21.9761 | 48328.92
|  | 2023-10-07 | 21:39 | 08.10.23 | 1:38 | 0.16597 | 3 | 59 | [5 empty] | At Meramundali end: Main: R-Y-B, Ir- 5.4 kA, Iy-5.8 kA, Ib-6.84 kA, Dist-5.8 km, Zone 2, B/U: Y-B, Directional O/C & E/F, Ir-7.5 kA, Iy-8.01 kA, Ib-7.7 kA. 132kV B-Ph Main Bus Jumper snapped at Kharagprasad end.
428 | 132kV Meramundali- RML (FAD) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
429 | 132kV Meramundali-Khajuriakata |  |  |  |  | 0.38472 | 15 | 59 | [7 empty] | 33.5 | 8760 | 99.82% | 535.4417 | 293460
|  | 2023-06-10 | 16:40 | 2023-06-10 | 19:01 | 0.097917 | 0 | 8 | [5 empty] | At Khajuriakata end:-Z-1, Yph, E/F, Iy=2.14KA, Dist- 600mtr At Meramundali end:- Z-1, Yph, E/F, Iy-7.39kA, Dist- 6.01km. Charging delay due to disturbance at Meramundali end.
|  | 2023-09-02 | 15:29 | 2023-09-02 | 15:52 | 0.015972 | 0 | 23 | [5 empty] | At Khajuriakata end:- No tripping At Meramundali end:- Rph-G, Zone-1, Dist-23.2km, Ir- 4.165kA. E/F
|  | 2024-01-27 | 12:30 | 2024-01-27 | 15:51 | 0.13958 | 3 | 21 | [5 empty] | At Khajuriakata end: Zone 1, B-N, Ib- 0.65 kA, Dist- 17.9 km At Meramundali end: Zone 1, B-N, Ib- 7.6 kA, Dist- 6.25 km. -
|  | 2024-03-06 | 13:26 | 2024-03-06 | 16:35 | 0.13125 | 0 | 7 | [5 empty] | At Khajuriakata end: B-N, Zone 1, Dist-12.5km, Ib- 0.521kA At Meramundali end: B-N, Zone 1, Dist- 5.9km, Ib- 8 .15kA. Station Blackout occurred at khajuriakata grid end. Fire under Loc 15 & 16
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
430 | 132KV Dhenkanal-Nuapatna-Khajuriakata "T" feeder |  |  |  |  | 0.075 | 13 | 43 | [7 empty] | 2.4 | 8760 | 99.84% | 32.92 | 21024
|  | 2023-06-04 | 20:24 | 2023-06-04 | 20:39 | 0.010417 | 0 | 15 | [5 empty] | Power supply failure. LC taken by MRDL grid to attend the B/D. 132KV DKL-MRDL line was B/D. So no power supply to the station. Fault occured at Meramundali grid ,Power failure from 132KV DKL fdr . As the said period the 132 kV ICCL Fdr was in H/T condition at ICCL end, At 20:47 hrs 132KV supply availed from ICCL end.
|  | 2023-06-05 | 12:33 | 2023-06-05 | 12:42 | 0.00625 | 0 | 9 | [5 empty] | At Khajuriakata end:- B/U relay operated , B-phase O/C. 132KV DKL-MRDL line was B/D. So no power supply to the station.
|  | 2023-06-05 | 14:56 | 2023-06-05 | 15:04 | 0.0055556 | 0 | 8 | [5 empty] | At Khajuriakata end:- B/U relay operated , B-phase O/C. 132KV DKL-MRDL line was B/D. So no power supply to the station.
|  | 2023-06-29 | 14:41 | 2023-06-29 | 14:53 | 0.0083333 | 0 | 12 | [5 empty] | At Khajuriakata end:- Z-2,Bph,E/F,Ib-0.87KA,Dist-93.6KM. Line test charged & stood OK
|  | 2023-06-29 | 17:20 | 2023-06-29 | 17:26 | 0.0041667 | 0 | 6 | [5 empty] | At Khajuriakata end:- Z-2, Bph, E/F, Ib-0.729KA, Dist- 100.1KM. After thorough patrolling one insulator disc punctured found. The line charged & it stood OK.
|  | 2023-10-03 | 16:40 | 2023-10-03 | 16:43 | 0.0020833 | 0 | 3 | [5 empty] | No tripping at Dhenkanal end. B/U relay operated at Khajuriakata end.. P/S failure as 132kV Dhenkanal- Meramundali & 132kV Dhenkanal- Khajuriakata-Nuapatna Line tripped
|  | 2023-06-10 | 17:41 | 2023-06-10 | 17:43 | 0.0013889 | 0 | 2 | [5 empty] | At Khajuriakata end:- Bph, E/F, Backup optd. PS FAILURE AT KHAJURIAKATA GRID S/S
|  | 2023-06-10 | 16:38 | 2023-06-10 | 16:46 | 0.0055556 | 0 | 8 | [5 empty] | At Khajuriakata end:- No Trip At Dhenkanal end:- Z-1, Bph, O/C, Ib-1.99KA, Dist- 24.44KM At Nuapatna end:- H/T condition. PS FAILURE AT KHAJURIAKATA GRID S/S
|  | 2023-09-02 | 15:30 | 2023-09-02 | 15:58 | 0.019444 | 0 | 23 | [5 empty] | At Dhenkanal end:- No fault record found At Khajuriakata end:- DP relay operated with indication Z-1, Dist=23.2km, fault loop R-N, Ir=4.165kA At Nuapatna end:- H/T. The line test charged after informing SLDC & concerned line authority at k.kata end & it stood OK
|  | 2023-04-12 | 03:22 | 2023-04-12 | 03:35 | 0.0090278 | 0 | 13 | [5 empty] | Tripped. Charged through B/C and restored P/S
|  | 2023-04-12 | 03:42 | 2023-04-12 | 03:46 | 0.0027778 | 0 | 4 | [5 empty] | Charged through B/C and restored P/S.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
431 | 132kV Khajuriakata-Nuapatna |  |  |  |  | 0 | 0 | 0 | [7 empty] | 83.99 | 8760 | 100% | 0 | 735752.4
432 | 132kV Nuapatna-Arati Steel |  |  |  |  | 0.052083 | 13 | 8 | [7 empty] | 66.9 | 8760 | 99.85% | 878.62 | 586044
|  | 2023-06-17 | 14:54 | 2023-06-17 | 15:15 | 0.014583 | 0 | 14 | [5 empty] | Power supply failed from Nuapatna/Banki. Nuapatna and Arati were availing P/S from Banki
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
|  | 2023-06-12 | 19:20 | 2023-06-12 | 19:24 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on E/F and O/C. Bad weather, heavy thunder storm.
|  | 2023-06-16 | 10:44 | 2023-06-16 | 10:56 | 0.0083333 | 0 | 12 | [5 empty] | Feeder tripped at Arati end with following indication: Ia=544.1A, Ib=409.4A, Ic=460.A. No relay indication at Nuapana end.. Nuapatna and Banki were availing P/S from Arati
|  | 2023-06-23 | 10:15 | 2023-06-23 | 10:46 | 0.021528 | 0 | 31 | [5 empty] | Tripped with folowing indication at Arati end: Zone-2, dist-74.94km, ir=1.273kA, ib=1.353kA, power supply failed at Nuapatna end, no breaker tripped at Nuapatna end. Power supply interrupted at grid S/S Nuapatna for 28 min
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
433 | 132kV Mohana-Digapahandi |  |  |  |  | 0.03125 | 13 | 45 | [7 empty] | 29.48 | 8760 | 99.84% | 405.35 | 258244.8
|  | 2024-03-31 | 08:20 | 2024-03-31 | 08:26 | 0.0041667 | 0 | 6 | [5 empty] | Supply failure from Digapahandi end. -
|  | 2023-05-30 | 17:30 | 2023-05-30 | 17:37 | 0.0048611 | 0 | 7 | [5 empty] | Digapahandi end. DP relay optd. Zone - 1,AGT, Dist.-2.82KM, Fault current- Ia=476A, Ib-300A, Ic-526A, Ig=1292A. Rain & heavy thunderstoms at Digapahandi end
|  | 2023-09-08 | 11:34 | 2023-09-08 | 11:48 | 0.0097222 | 1 | 14 | [5 empty] | At Digapahandi end:- B/u relay optd. B-PH E/F, Ia-0.04kA, Ib- 0.07kA, Ic-0.04kA. The Akhusing side line isolator opened at Mohana GSS and line chared from Digpahandi end.
|  | 2023-09-27 | 12:30 | 2023-09-27 | 12:48 | 0.0125 | 0 | 18 | [5 empty] | At Digapahandi end:- DP relay optd. Zone -1, ABG, Dist.- 80.38km, Fault current- Ia=1444A, Ib-1427A, Ic-18A, Ig=0A.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
434 | 132kV Muniguda-Bissamcuttack RTSS |  |  |  |  | 0.175 | 18 | 1 | [7 empty] | 13.85 | 8760 | 99.79% | 249.5308 | 121326
|  | 2023-04-04 | 11:03 | 2023-04-04 | 11:05 | 0.0013889 | 0 | 2 | [5 empty] | OVER LOAD.
|  | 2023-04-06 | 15:14 | 2023-04-06 | 15:16 | 0.0013889 | 0 | 2 | [5 empty] | Transient fault.
|  | 2023-08-24 | 11:14 | 2023-08-24 | 11:16 | 0.0013889 | 0 | 2 | [5 empty] | Over load. Over Load
|  | 2023-08-24 | 11:27 | 2023-08-24 | 11:29 | 0.0013889 | 0 | 2 | [5 empty] | Over load. Over Load
|  | 2023-08-30 | 9:39 | 2023-08-30 | 9:45 | 0.0041667 | 0 | 6 | [5 empty] | Over load. -
|  | 2023-09-03 | 09:18 | 2023-09-03 | 09:20 | 0.0013889 | 0 | 2 | [5 empty] | Over Load.
|  | 2023-09-07 | 08:05 | 2023-09-07 | 08:06 | 0.00069444 | 0 | 1 | [5 empty] | Over Load.
|  | 2023-09-21 | 00:26 | 2023-09-21 | 00:27 | 0.00069444 | 0 | 1 | [5 empty] | Over Load.
|  | 2023-12-24 | 09:38 | 2023-12-24 | 09:40 | 0.0013889 | 0 | 2 | [5 empty] | Overload. -
|  | 2024-01-10 | 20:21 | 2024-01-10 | 20:24 | 0.0020833 | 0 | 3 | [5 empty] | O/C, Ir- 0.278kA, Iy- 0.275kA. -
|  | 2023-12-07 | 06:49 | 2023-12-07 | 06:50 | 0.00069444 | 0 | 1 | [5 empty] | Overload. -
|  | 2023-12-07 | 06:53 | 2023-12-07 | 06:55 | 0.0013889 | 0 | 2 | [5 empty] | Overload. -
|  | 2023-12-11 | 08:16 | 2023-12-11 | 08:17 | 0.00069444 | 0 | 1 | [5 empty] | Overload. -
|  | 2023-12-29 | 00:22 | 2023-12-29 | 00:23 | 0.00069444 | 5 | 1 | [5 empty] | Overload. -
|  | 2024-03-07 | 14:11 | 2024-03-07 | 14:12 | 0.00069444 | 0 | 1 | [5 empty] | Overload. -
|  | 2024-03-20 | 15:42 | 2024-03-20 | 15:44 | 0.0013889 | 0 | 2 | [5 empty] | Overload. -
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:13 | 3:41 | 0 | 30 | [5 empty] | No tripping at Therubali end. At Bhanjanagar end: B-N, Zone 3, Dist- 284 km, Ir- 0.148 kA, Iy- 0.233 kA, Ib- 0.703 kA. System out at Therubali end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
435 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 11.31 | 8760 | 100% | 1.885 | 99075.6
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:13 | 0.0069444 | 0 | 10 | [5 empty] | B/U relay: Ir-1.36 kA, Iy- 1.49 kA, Ib- 1.37 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
436 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0.0069444 | 0 | 10 | [7 empty] | 11.31 | 8760 | 100% | 1.885 | 99075.6
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:13 | 0.0069444 | 0 | 10 | [5 empty] | B/U relay: Ir-1.36 kA, Iy- 1.49 kA, Ib- 1.37 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
437 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0.82917 | 0 | 27 | [7 empty] | 13.28 | 8760 | 99.99% | 5.976 | 116332.8
|  | 2023-10-16 | 16:03 | 17.10.23 | 10:57 | 0.82917 | 0 | 27 | [5 empty] | Y-N, Dist- 0.41m , Zone 3, Iy- 2.378 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
438 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 13.28 | 8760 | 99.99% | 5.976 | 116332.8
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:30 | 0.01875 | 0 | 27 | [5 empty] | Y-N, Dist- 0.41m , Zone 3, Iy- 2.378 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
439 | 132kV Narendrapur-Jagannathpur RTSS |  |  |  |  | 0.069444 | 13 | 40 | [7 empty] | 0.51 | 8760 | 99.84% | 6.97 | 4467.6
|  | 2023-10-02 | 16:31 | 2023-10-02 | 17:23 | 0.036111 | 0 | 52 | [5 empty] | Main 1: R-Y-B, Zone 2, A/R Distk out , Dist- 131.7 km, Ir- 64.94 A, Iy- 1.659 kA, Ib- 1.536 kA Main 2: B-N, Zone 2, Dist- 131.84 km ,Iy- 1.756 kA, Ib- 1.622 kA. -
|  | 2023-11-27 | 07:33 | 2023-11-27 | 07:43 | 0.0069444 | 0 | 10 | [5 empty] | R & B Ph directional O/C, Ir- 1 kA, Ib- 1 kA. -
|  | 2023-06-07 | 04:50 | 2023-06-07 | 04:51 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on O/C with R & B Phase .Ir-1.02KAmp , Ib- 1.02KAmp..
|  | 2023-06-16 | 10:40 | 2023-06-16 | 11:12 | 0.022222 | 0 | 32 | [5 empty] | Tripped on Over Fluxing.. Over Fluxing
|  | 2024-02-09 | 23:32 | 2024-02-09 | 23:37 | 0.0034722 | 0 | 5 | [5 empty] | Directional O/C ( R & B Ph), Ir- 1kA, Ib- 1kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
440 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
441 | 132kV Nimapara-Konark |  |  |  |  | 0.099306 | 14 | 23 | [7 empty] | 19.91 | 8760 | 99.84% | 286.3722 | 174411.6
|  | 2023-04-22 | 04:31 | 2023-04-22 | 04:36 | 0.0034722 | 0 | 5 | [5 empty] | Tripped.
|  | 2023-04-23 | 07:04 | 2023-04-23 | 07:07 | 0.0020833 | 0 | 3 | [5 empty] | Tripped.
|  | 2023-06-08 | 19:16 | 2023-06-08 | 19:29 | 0.0090278 | 0 | 13 | [5 empty] | Supply failure.
|  | 2023-07-08 | 17:22 | 2023-07-08 | 17:51 | 0.020139 | 0 | 29 | [5 empty] | No relay indication. Source failure
|  | 2023-07-08 | 18:19 | 2023-07-08 | 18:23 | 0.0027778 | 0 | 4 | [5 empty] | No relay indication. Source failure
|  | 2023-07-08 | 19:16 | 2023-07-08 | 19:29 | 0.0090278 | 0 | 13 | [5 empty] | No relay indication. Source failure
|  | 2023-11-25 | 16:17 | 2023-11-25 | 17:04 | 0.032639 | 0 | 47 | [5 empty] | Failure from source. -
|  | 2023-06-08 | 17:22 | 2023-06-08 | 17:51 | 0.020139 | 0 | 29 | [5 empty] | Supply failure. conductor snapped at loc. No.121
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
442 | 132kV Nimapara-Puri |  |  |  |  | 0.042361 | 1 | 1 | [7 empty] | 29.6 | 8760 | 99.99% | 30.0933 | 259296
|  | 2023-06-02 | 16:43 | 2023-06-02 | 17:44 | 0.042361 | 1 | 1 | [5 empty] | Source failure due to overloading. 132 KV Pratapsan supply was extended to Samangara through Nimapara reserve bus. The feeder test charged but didn't stand. Jumper snapped of 132kV Samangara-Nimapara feeder. Station Supply availed from 132kV Puri. A/R not operated at Prapsasan.
443 | 132kV Nimapara-Samagara |  |  |  |  | 0.39375 | 13 | 52 | [7 empty] | 27.6 | 8760 | 99.84% | 382.72 | 241776
|  | 2023-06-07 | 18:11 | 2023-06-07 | 18:42 | 0.021528 | 0 | 31 | [5 empty] | source Failure. source Failure.Power supply availed from 132 KV Puri
|  | 2024-02-10 | 16:09 | 2024-02-10 | 19:55 | 0.15694 | 0 | 16 | [5 empty] | Ir- 518.1A, Iy- 618.7A, Ib- 542.6A. 132kV Nimapara-Puri Feeder was charged through reserve bus and Samagara Grid was availing power from Puri Grid through reserve bus.
|  | 2023-06-02 | 16:43 | 2023-06-02 | 21:53 | 0.21528 | 1 | 5 | [5 empty] | Source Failure, At Samangara-A/R Success Zone-I, Dist=3.5km, Ir-0.59kA At NimaparaTripped at 17:15 hrs -SOTF, Z1, AN, Ia=1.744KA, Ib=6.328A, Ic=6.384A, D=21.15km. Charged at Samangara end at 17:47hrs. [R-ph Jumper snapped at loc.91]. 132 KV Pratapsan supply was extended to Samangara through Nimapara reserve bus. The feeder test charged but didn't stand. Jumper snapped of 132kV Samangara-Nimapara feeder. Station Supply availed from 132kV Puri. A/R not operated at Prapsasan.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
444 | 132kV ICCL- Mania |  |  |  |  | 0.34861 | 14 | 54 | [7 empty] | 18.32 | 8760 | 99.83% | 272.968 | 160483.2
|  | 2023-06-17 | 15:02 | 2023-06-17 | 17:52 | 0.11806 | 0 | 42 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 15:09 (Only station supply aviled till 15:46 load limited to 20MW)
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:42 | 0.016667 | 0 | 24 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
|  | 2024-02-23 | 07:56 | 2024-02-23 | 08:19 | 0.015972 | 0 | 23 | [5 empty] | Incomer failure. -
|  | 2023-06-12 | 12:25 | 2023-06-12 | 12:36 | 0.0076389 | 0 | 11 | [5 empty] | INCOMER FAILED.
|  | 2023-09-30 | 11:17 | 2023-09-30 | 11:20 | 0.0020833 | 0 | 3 | [5 empty] | Source failure.
|  | 2023-09-30 | 11:31 | 2023-09-30 | 11:52 | 0.014583 | 0 | 21 | [5 empty] | Source failure.
|  | 2024-01-19 | 04:22 | 2024-01-19 | 04:42 | 0.013889 | 0 | 20 | [5 empty] | At Mania end: Zone 1, Dist- 2.8 km, Ir- 1.844 kA At ICCL end: Zone 1, Dist- 13.47 km, Ir- 4.6 kA. -
|  | 2023-06-12 | 11:42 | 2023-06-12 | 13:55 | 0.092361 | 0 | 11 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 11:53
|  | 2023-09-13 | 14:56 | 2023-09-13 | 16:19 | 0.057639 | 0 | 6 | [5 empty] | No indication, Incoming failed from ICCL end.. Supply availed from Kendrapara Grid at 15:02Hrs
|  | 2023-12-05 | 11:07 | 2023-12-05 | 11:14 | 0.0048611 | 0 | 6 | [5 empty] | Incomer failure from source end. No tripping at Salipur end.. Due to tripping of 132kV Choudwar- Bidanasi Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
445 | 132kV Mania- OCL |  |  |  |  | 0.33056 | 14 | 43 | [7 empty] | 4.063 | 8760 | 99.83% | 59.7938 | 35591.88
|  | 2023-06-17 | 15:02 | 2023-06-17 | 17:52 | 0.11806 | 0 | 57 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 15:09 (Only station supply aviled till 15:46 load limited to 20MW)
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:42 | 0.016667 | 0 | 24 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2023-06-12 | 12:25 | 2023-06-12 | 12:40 | 0.010417 | 0 | 15 | [5 empty] | INCOMER FAILED.
|  | 2023-07-04 | 14:23 | 2023-07-04 | 14:44 | 0.014583 | 0 | 21 | [5 empty] | At Mania end:- Event details -DP relay operated, Event -AGT, Zone-1, Location -2.23 KM, Ia-3603A -68°, Ib-86A -119°, Ic-121A +126°, In-3541A 110°, Ig-3542A -70°, Fault location angle 70.58°. At OCL end CB did not trip. Weather Condition at Mania- Lightening and raining
|  | 2024-02-23 | 07:56 | 2024-02-23 | 08:19 | 0.015972 | 0 | 23 | [5 empty] | Incomer failure. -
|  | 2023-06-12 | 11:42 | 2023-06-12 | 13:55 | 0.092361 | 0 | 11 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 11:53
|  | 2023-09-13 | 14:56 | 2023-09-13 | 16:19 | 0.057639 | 0 | 6 | [5 empty] | No indication, Incoming failed from ICCL end.. Supply availed from Kendrapara Grid at 15:02Hrs
|  | 2023-12-05 | 11:07 | 2023-12-05 | 11:14 | 0.0048611 | 0 | 6 | [5 empty] | Incomer failure from source end. No tripping at Salipur end.. Due to tripping of 132kV Choudwar- Bidanasi Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
446 | 132kV OCL-Salipur |  |  |  |  | 0.56944 | 19 | 5 | [7 empty] | 38.41 | 8760 | 99.78% | 732.9908 | 336471.6
|  | 2023-06-17 | 15:02 | 2023-06-17 | 17:52 | 0.11806 | 0 | 57 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 15:09 (Only station supply aviled till 15:46 load limited to 20MW)
|  | 2023-06-30 | 18:18 | 2023-06-30 | 20:04 | 0.073611 | 0 | 24 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2023-05-11 | 09:31 | 2023-05-11 | 14:52 | 0.22292 | 5 | 21 | [5 empty] | At Salipur-Dist. Trip Zone 1 Fault Duration 68.35 ms Relay Trip Time 80.02ms Fault Location 5.185km Ia=3.630kA Ib=56.58A Ic=129.5A Van=17.44kV Vbn=78.36kV Vcn=76.50kV Fault Resistance 1.688 Ohm.
|  | 2023-06-12 | 11:42 | 2023-06-12 | 13:55 | 0.092361 | 0 | 11 | [5 empty] | Power failure from source end.. 132kV supply availed from Kendrapara Grid at 11:53
|  | 2023-09-13 | 14:56 | 2023-09-13 | 16:19 | 0.057639 | 0 | 6 | [5 empty] | No indication, Incoming failed from ICCL end.. Supply availed from Kendrapara Grid at 15:02Hrs
|  | 2023-12-05 | 11:07 | 2023-12-05 | 11:14 | 0.0048611 | 0 | 6 | [5 empty] | Incomer failure from source end. No tripping at Salipur end.. Due to tripping of 132kV Choudwar- Bidanasi Line
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
447 | 132kV ICCL-Bahugram |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 21.14 | 8760 | 100% | 2.4663 | 185186.4
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
448 | 132kV Bahugram-Salipur |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 10.83 | 8760 | 100% | 1.2635 | 94870.8
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
449 | 132kV Paradeep-Tirtol |  |  |  |  | 1899-12-31 01:26 | 13 | 33 | [7 empty] | 38.43 | 8760 | 99.85% | 520.7265 | 336646.8
|  | 2023-06-04 | 20:01 | 2023-06-04 | 20:30 | 0.020139 | 0 | 28 | [5 empty] | At Jagatsinghpur end:- No Breaker tripped At Tirtol end:- Zone-1, Ia= 48.11A, Ib=1.939kA, Ic=163A, Dist-17.3km. Jagatsinghpur GSS availed 132kV P/S from Cuttack end at 20:24 . At 20:30 132kV Tirtol- Jagatsinghpur Line charged from Tirtol end & stood ok. 132kV Tirtol-Jagatsinghpur Line is in idle charged condition.
|  | 2023-06-07 | 19:15 | 08.06.23 | 17:41 | 0.97639 | 0 | 17 | [5 empty] | At Tirtol end: ZONE-1, Y-PHASE, Ib-206.4KA, Dist- 21.17km ,fault duration-48.28ms. Jagatsinghpur Gss was availing 132kV P/S from Cuttack end at 19:19 .
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 10 | [5 empty] | Supply Fail. -
|  | 2023-11-29 | 20:24 | 2023-11-29 | 20:45 | 0.014583 | 0 | 21 | [5 empty] | Y-N, Zone 1, Dist- 11.1 km. -
|  | 2023-10-13 | 14:13 | 2023-10-13 | 14:30 | 0:17 | 0 | 17 | [5 empty] | Supply Fail. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
450 | 132kV Tirtol- Jagatsinghpur |  |  |  |  | 0.27361 | 13 | 23 | [7 empty] | 29.26 | 8760 | 99.85% | 391.5963 | 256317.6
|  | 2023-05-03 | 16:33 | 2023-05-03 | 18:36 | 0.085417 | 0 | 10 | [5 empty] | Both 132kV JSPUR-CTC LINE & 132kV JSPUR- TIRTOL LINE synchronized at Jagatsinghpur GSS at 13:52 Hrs and stood OK.. Jagatsinghpur Gss was availing 132kV P/S from Tirtol end at 16:45Hrs.
|  | 2023-05-16 | 17:37 | 2023-05-16 | 19:52 | 0.09375 | 0 | 13 | [5 empty] | 132kV Ctc-Tirtol Line tripped on DP relay from Tirtol end with following relay indication:- Relay Indication at TIRTOL GSS Zone-1, Ib = 2.09kA Distance = 16.08KM. Jagatsinghpur Grid was availing power supply from 17:50Hrs from CTC end.
|  | 2023-06-04 | 20:02 | 2023-06-04 | 20:30 | 0.019444 | 0 | 28 | [5 empty] | At Tirtol end: ZONE-1, Y-PHASE, Ib-1.939KA, Dist-17.3km ,fault duration-53.31ms. Weather: Heavy lightening & Rain
|  | 2023-06-07 | 19:15 | 2023-06-07 | 19:19 | 0.0027778 | 0 | 4 | [5 empty] | 132kV Jagatsinghpur GSS P/S failed due to failure of CT at Paradeep side.. Jagatsinghpur Gss was availing 132kV P/S from Cuttack end at 19:19 .
|  | 2023-09-02 | 15:47 | 2023-09-02 | 15:58 | 0.0076389 | 0 | 11 | [5 empty] | At Jagatsinghpur end:- No Tripping At Tirtol end:- Zone-1, Ia= 369.6 A,Ib = 2.727 kA, Ic = 255.7 A, Distance = 1.89KM. At 15:58Hrs 132kV JSPUR-TIRTOL Line charged & stood ok.
|  | 2023-09-02 | 16:29 | 2023-09-02 | 17:48 | 0.054861 | 0 | 3 | [5 empty] | At Jagatsinghpur end:- No Tripping At Tirtol end:- Zone-1, Ia= 462.8 A,Ib = 2.097 kA, Ic = 367.1 A, Distance = 16.98KM. Jagatsinghpur GSS availed 132kV P/S from Cuttack end at 16:32 Hrs. At17:48 Hrs 132kV JSPUR- TIRTOL Line charged & stood ok.
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:13 | 0.0097222 | 0 | 14 | [5 empty] | 132kV incoming P/S failed from Tirtol end due to failure of P/S from Paradeep end. No relay operated at Jagatsinghpur GSS.. At 14:03 Hrs Jagatsinghpur GSS availed 132kV P/S from Cuttack end & at 14:13 Hrs Jagatsinghpur GSS extended the P/S to Tirtol GSS. At 14:55 Hrs 132kV Tirtol Jagatsinghpur Line was H/T from Jagatsinghpur end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
451 | 132kVJagatsinghpur-Gorakhnath RTSS |  |  |  |  | 1899-12-31 06:49 | 14 | 40 | [7 empty] | 16.53 | 8760 | 99.83% | 242.44 | 144802.8
|  | 2023-08-16 | 22:40 | 2023-08-16 | 23:36 | 0.038889 | 0 | 9 | [5 empty] | Zone-1, dist- 6.408km, Ia=525A, Ib=6.304kA, Ic= 264.1A. Weather: Heavy Rain fall and lightning
|  | 2023-10-15 | 21:18 | 2023-10-15 | 21:41 | 0.015972 | 0 | 23 | [5 empty] | At Cuttack end: O/C in Y-Phase & E/F (B/C Relay), Iy- 1.9 kA, Ic = 336A( DP Not Opearted) TRF I: O/C in Y Ph, Iy- 0.42 kA TRF II: O/C in RYB Ph, Ir- 1.01 kA, Iy- 0.69 kA, Ib- 0.96 kA No relay operated at Jagatsinghpur end.. At 21:40Hrs Jagatsinghpur GSS availed 132kV P/S from Cuttack end. At 21:45 Hrs 33kV side of TRF-I was charged & At 23:15 Hrs 132kV Side of TRF II was charged & At 23:17 Hrs 33kV Side of TRF II was charged
|  | 2023-11-10 | 22:52 | 2023-11-10 | 23:20 | 0.019444 | 0 | 22 | [5 empty] | No Tripping at Jagatsinghpur end. At Cuttack end: O/C & B/C, Ir- 0.43 kA, Ib- 1.98kA, Ic- 0.26kA DP:- Dist- 52.4 km, Ir-527A, Iy- 1.979 kA, Ib- 341A, Zone 3. At 23:00Hrs Jagatsinghpur GSS availed 132kV P/S from Tirtol end keeping Cuttack-Jagatsinghpur breaker in off condition. At 23:20Hrs 132kV Cuttack-JagatsinghpurLine charged from Cuttack end.
|  | 2023-10-20 | 17:54 | 21.10.23 | 13:54 | 0.83333 | 0 | 5 | [5 empty] | At Cuttack end: R-N, Zone 1, Dist- 26.48 km, Ir- 3.188 kA At Jagasinghpur end: Ir- 0.46 kA, Iy- 0.72 kA, Ib- 0.58 kA, Dist- 5.5 km, Zone 1 At 18:23 Hrs the said Line charged from Cuttack end, but again tripped. At Cuttack end: SOTF, Zone 1, Dist- 25.49 km, Ir- 2.833 kA. At 18:00 Hrs Jagatsinghpur availed 132kV P/S from Tirtol end. At 13:54 Hrs 132kV Cuttack-Jagatsinghpur Line Charged. At 13:57 Hrs Jagatsinghpur availed 132kV P/S from Cuttack end & 132kV Tirtol- Jagatsinghpur Line was H/T from Jagatsinghpur end.
|  | 2023-10-29 | 03:55 | 2023-10-29 | 04:23 | 0.019444 | 0 | 8 | [5 empty] | At Cuttack end: O/C & B/C, Ir- 0.44 kA, Iy- 2.02 kA, Ib- 0.27 kA, Dist- 51.99 km, Zone 3 20 MVA TRF-I:- O/C in RYB phase, Ir- 0.46 kA, Iy- 0.46 kA, Ib- 0.46 kA 20 MVA TRF-II:- O/C in RYB phase, Ir- 0.96 kA, Iy- 0.96 kA, Ib- 0.96 kA. At 04:02 Hrs Jagatsinghpur GSS availed 132kV P/S from Tirtol end. At 04:05 Hrs 20 MVA TRF-I & 20 MVA TRF-II were charged one after another.At 04:23 Hrs 132kV Cuttack- Jagatsinghpur Line charged & stood ok.
|  | 2023-05-03 | 16:35 | 2023-05-03 | 18:52 | 0.095139 | 0 | 30 | [5 empty] | 132kV Ctc-Jspur Line tripped on DP relay from both end with following relay indication:- Relay Indication at JSPUR GSS Zone-1, Ia= 8A, Ib = 7A,Ic= 1318.4 A Distance = 13.418KM, Fault Time = 88ms Relay Indication at CTC GSS Active Group 1, Zone-1, Started Phase :- BN, Tripped Phase:- ABC Ia= 565.1A, Ib = 4.748kA, Ic= 392.2 A Distance = 13.46KM, Fault Duration = 73.38ms, Relay trip time = 80ms. Jagatsinghpur Gss was availing 132kV P/S from Tirtol end at 16:45Hrs.
|  | 2023-05-16 | 17:37 | 2023-05-16 | 19:52 | 0.09375 | 0 | 13 | [5 empty] | 132kV Ctc-Tirtol Line tripped on DP relay from Tirtol end with following relay indication:- Relay Indication at TIRTOL GSS Zone-1, Ib = 2.09kA Distance = 16.08KM. Jagatsinghpur Grid was availing power supply from 17:50Hrs from CTC end.
|  | 2023-06-04 | 20:01 | 2023-06-04 | 20:24 | 0.015972 | 0 | 23 | [5 empty] | 132kV p/s failed from both Cuttack & Tirtol GSS with heavy spark inside Jagatsinghpur GSS. No Breaker tripped at Jagatsinghpur end. At Cuttack end:- Zone-2, Tripped on RYB, Ia= 543.5A, Ib = 2.306kA, Ic= 350.2 A, Dist-42.08km. Jagatsinghpur GSS availed 132kV P/S from Cuttack end at 20:24 .
|  | 2023-06-07 | 19:15 | 2023-06-07 | 19:19 | 0.0027778 | 0 | 4 | [5 empty] | 132kV Jagatsinghpur GSS P/S failed due to failure of CT at Paradeep side.. Jagatsinghpur Gss was availing 132kV P/S from Cuttack end at 19:19 .
|  | 2023-07-31 | 17:29 | 2023-07-31 | 19:34 | 0.086806 | 0 | 9 | [5 empty] | At Jagatsinghpur end:- DP Rlay operated. Zone-1, Distance-1Km, Ia-0.71kA, Ib-0.66kA, Ic-0.68kA At Cuttack end:- Zone-2, Tripped on RYB, Ia= 3.20kA, Ib = 0.695kA, Ic= 3.167kA, Distance=37.47km. Weather- Heavy rainfall & Lightening. 132kV Power supply failed from Cuttack end
|  | 2023-09-02 | 15:47 | 2023-09-02 | 15:58 | 0.0076389 | 0 | 11 | [5 empty] | At Jagatsinghpur end:- No Tripping At Tirtol end:- Zone-1, Ia= 369.6 A,Ib = 2.727 kA, Ic = 255.7 A, Distance = 1.89KM. At 15:58Hrs 132kV JSPUR-TIRTOL Line charged & stood ok.
|  | 2023-09-02 | 16:29 | 2023-09-02 | 17:48 | 0.054861 | 0 | 3 | [5 empty] | At Jagatsinghpur end:- No Tripping At Tirtol end:- Zone-1, Ia= 462.8 A,Ib = 2.097 kA, Ic = 367.1 A, Distance = 16.98KM. Jagatsinghpur GSS availed 132kV P/S from Cuttack end at 16:32 Hrs. At17:48 Hrs 132kV JSPUR- TIRTOL Line charged & stood ok.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
452 | 132kV Paradeep- Siju RTSS |  |  |  |  | 0.077778 | 13 | 52 | [7 empty] | 5.081 | 8760 | 99.84% | 70.4565 | 44509.56
|  | 2023-06-05 | 06:34 | 2023-06-05 | 06:42 | 0.0055556 | 0 | 8 | [5 empty] | O/C R&Y-PHASE Ia-974.8A,Ib-974.2A,Ic-0.
|  | 2023-07-08 | 03:40 | 2023-07-08 | 04:03 | 0.015972 | 0 | 23 | [5 empty] | O/C, R&Y-PHASE, Ia-286.2A, Ib-285.2A, Ic-0.
|  | 2023-07-18 | 20:48 | 2023-07-18 | 21:48 | 0.041667 | 1 | 0 | [5 empty] | CB Tripped due to control cable cut by the miscreants & no relay trip.
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | Source failure at Kendrapara. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
453 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0.35972 | 19 | 29 | [7 empty] | 7.171 | 8760 | 99.78% | 139.715 | 62817.96
|  | 2024-01-18 | 05:53 | 2024-01-18 | 10:31 | 0.19306 | 4 | 38 | [5 empty] | O/C (Y & B Ph) & E/F, Ir- 0.09 kA, Iy- 6.68 kA, Ib- 0.16 kA. Due to Heavy Fog the above said CKT doesnot charged and declared faulty till the clearance of Fog with
|  | 2024-01-25 | 04:46 | 2024-01-25 | 08:25 | 0.15208 | 2 | 30 | [5 empty] | O/C (R Ph) & E/F, Ir- 5.94 kA. Due to Heavy Fog the above said CKT did not charge and declared
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
454 | 132kV Paradeep- IFFCO - II |  |  |  |  | 0.014583 | 19 | 29 | [7 empty] | 7.171 | 8760 | 99.78% | 139.715 | 62817.96
|  | 2024-01-18 | 05:02 | 2024-01-18 | 10:31 | 05:29 | 4 | 38 | [5 empty] | O/C (R-Y-B) & E/F, Ir- 6.72 kA. Due to Heavy Fog the above said CKT doesnot charged and declared faulty till the clearance of Fog with
|  | 2024-01-25 | 05:54 | 2024-01-25 | 08:24 | 02:30 | 2 | 30 | [5 empty] | O/C (B Ph) & E/F, Ib- 5.27 kA. Due to Heavy Fog the above said CKT did not charge and declared
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
455 | 132kV Paradeep-PPL-I |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 6.2 | 8760 | 100% | 2.17 | 54312
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
456 | 132kV Paradeep-PPL-II |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 6.2 | 8760 | 100% | 2.17 | 54312
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
457 | 132kV Paradeep-PPT-I |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 7.65 | 8760 | 100% | 2.6775 | 67014
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
458 | 132kV Paradeep-PPT-II |  |  |  |  | 0.014583 | 0 | 21 | [7 empty] | 7.65 | 8760 | 100% | 2.6775 | 67014
|  | 2024-03-28 | 12:24 | 2024-03-28 | 12:45 | 0.014583 | 0 | 21 | [5 empty] | At Paradeep end: Y-B (O/C), Zone 1, Dist- 10.3km, Iy- 2.3kA, Ib- 2.6kA At New Duburi end: Main 1- Y-B, Zone 1, Dist- 97.5km, Iy- 2.5kA, Ib- 2.2kA; Main 2- Y-B, Zone 1, Dist- 97.5km, Iy- 2.53kA, Ib- 2.23kA.. -
459 | 132kV Patnagarh-Padampur |  |  |  |  | 0.39306 | 14 | 25 | [7 empty] | 44.24 | 8760 | 99.84% | 637.7933 | 387542.4
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:00 | 0.0055556 | 0 | 8 | [5 empty] | Source Failure
|  | 2023-09-13 | 18:35 | 2023-09-13 | 18:58 | 0.015972 | 0 | 21 | [5 empty] | TRIPPED on operation of Distance Protection relay. Relay details:Zone 1, IA=1.494KA, IB=2.398KA, IC=237.1A Fault Distance= 16.18km. From 18:56hrs, 132KV Bolangir New- Patnagarh ckt -II was in service o meet the load demand of GSS Patnagarh.
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure from 220/132KV GSS Sadeipali.
|  | 2023-12-17 | 00:48 | 2023-12-17 | 01:10 | 0.015278 | 0 | 22 | [5 empty] | Tripped from Patnagarh. -
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-04-26 | 19:26 | 2023-04-27 | 2:35 | 0.29792 | 0 | 10 | [5 empty] | S/D Availed for replacement of R phase Jumper at Loc No 140. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-04-26 | 19:16 | 2023-04-26 | 19:26 | 0.0069444 | 0 | 10 | [5 empty] | Phase-AN, Zone-1, Distance=7.162KM, Ia=375.2A, Ib=309.7A, Ic=605.3A. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-10-08 | 09:08 | 2023-10-08 | 09:19 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2023-10-08 | 14:16 | 2023-10-08 | 14:27 | 0.0076389 | 0 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2024-01-04 | 12:57 | 2024-01-04 | 13:01 | 0.0027778 | 0 | 4 | [5 empty] | Tripped due to sparking in the Y-Ph SI contact point of TRF-II. If- 186.3A. -
|  | 2024-03-15 | 09:22 | 2024-03-15 | 09:36 | 0.0097222 | 0 | 14 | [5 empty] | At Padampur end: B-N, Zone 1, Dist- 36.04km, Ir- 0.297kA, Iy- 0.576kA, Ib- 0.373kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
460 | 132kV Padampur-Padampur Solar |  |  |  |  | 0.011806 | 0 | 4 | [7 empty] | 10.5 | 8760 | 100% | 0.7 | 91980
|  | 2024-01-04 | 12:57 | 2024-01-04 | 13:14 | 0.011806 | 0 | 4 | [5 empty] | Tripped due to sparking in the Y-Ph SI contact point of TRF-II. If- 186.3A. -
461 | 132kV Padampur-Nuapada-I |  |  |  |  | 0.72292 | 24 | 39 | [7 empty] | 68 | 8760 | 99.72% | 1676.2 | 595680
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:00 | 00:08 | 0 | 8 | [5 empty] | Source failure
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2024-03-26 | 23:53 | 2024-03-27 | 0:14 | 0.014583 | 0 | 21 | [5 empty] | LBB. -
|  | 2024-03-27 | 20:28 | 2024-03-27 | 20:39 | 0.0076389 | 0 | 11 | [5 empty] | LBB. -
|  | 2024-03-28 | 10:00 | 2024-03-28 | 10:06 | 0.0041667 | 0 | 6 | [5 empty] | LBB. -
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure from 220/132KV GSS Sadeipali.
|  | 2023-09-20 | 01:38 | 2023-09-20 | 01:57 | 0.013194 | 0 | 19 | [5 empty] | Tripped due to DP operated, Phase-AN, Zone1, Distance=51.99KM Ia=81.47A, Ib=36.39A, Ic=129.5A.
|  | 2023-09-20 | 16:07 | 2023-09-20 | 16:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-09-29 | 23:10 | 2023-09-29 | 23:29 | 0.013194 | 0 | 19 | [5 empty] | Failed due to Patnagarh-Padampur line tripped.
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-08-16 | 13:22 | 2023-08-16 | 20:32 | 0.29861 | 0 | 13 | [5 empty] | R-phase LA burst, Ia-187.1A, Ib-128.9 A, Ic-238.7A, In-491.2A. Rph LA burst. supply was availed from GSS , Khariar
|  | 2023-09-02 | 14:37 | 2023-09-02 | 14:44 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Padampur due to DP operated.
|  | 2023-09-05 | 11:17 | 2023-09-05 | 11:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped from Padampur due to DP operated.
|  | 2023-10-11 | 10:00 | 2023-10-11 | 10:05 | 0.0034722 | 0 | 5 | [5 empty] | Supply failed from Source end(Bolangir New). -
|  | 2023-12-17 | 00:48 | 2023-12-17 | 01:10 | 00:22 | 0 | 22 | [5 empty] | Tripped from Patnagarh. -
|  | 2024-03-12 | 10:07 | 2024-03-12 | 10:21 | 0.0097222 | 0 | 14 | [5 empty] | LBB. -
|  | 2024-03-12 | 10:36 | 2024-03-12 | 10:51 | 0.010417 | 0 | 15 | [5 empty] | LBB. -
|  | 2023-04-24 | 17:05 | 2023-04-24 | 17:17 | 0.0083333 | 0 | 12 | [5 empty] | Phase-AN, Distance=54.93KM, Ia=951.6A, Ib=108.4A, Ic=141.1A, In=701.8A.
|  | 2023-04-26 | 19:16 | 2023-04-27 | 2:40 | 0.225 | 0 | 10 | [5 empty] | Source failure. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-04-26 | 19:16 | 2023-04-26 | 19:26 | 0.0069444 | 0 | 10 | [5 empty] | Phase-AN, Zone-1, Distance=7.162KM, Ia=375.2A, Ib=309.7A, Ic=605.3A. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-06-17 | 13:00 | 2023-06-17 | 13:10 | 0.0069444 | 0 | 10 | [5 empty] | Source Failure from 132/33KV GSS Khariar.
|  | 2023-07-23 | 13:18 | 2023-07-23 | 13:26 | 0.0055556 | 0 | 8 | [5 empty] | Distance Protection operated. Phase-BC, Zone-3, Location- 100.6km, Ia=61.3A, Ib=897.3A, Ic=841A.
|  | 2023-10-08 | 09:08 | 2023-10-08 | 09:19 | 0.0076389 | 7 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2024-03-15 | 09:22 | 2024-03-15 | 09:37 | 0.010417 | 0 | 15 | [5 empty] | Source failure from Patnagarh. -
|  | 2024-01-04 | 12:57 | 2024-01-04 | 13:02 | 0.0034722 | 0 | 4 | [5 empty] | Tripped due to sparking in the Y-Ph SI contact point of TRF-II. If- 186.3A. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
462 | 132kV Padampur-Nuapada-II |  |  |  |  | 0.72292 | 24 | 39 | [7 empty] | 68 | 8760 | 99.72% | 1676.2 | 595680
|  | 2023-04-18 | 16:52 | 2023-04-18 | 17:00 | 00:08 | 0 | 8 | [5 empty] | Source failure
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2024-03-26 | 23:53 | 2024-03-27 | 0:14 | 0.014583 | 0 | 21 | [5 empty] | LBB. -
|  | 2024-03-27 | 20:28 | 2024-03-27 | 20:39 | 0.0076389 | 0 | 11 | [5 empty] | LBB. -
|  | 2024-03-28 | 10:00 | 2024-03-28 | 10:06 | 0.0041667 | 0 | 6 | [5 empty] | LBB. -
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure from 220/132KV GSS Sadeipali.
|  | 2023-09-20 | 01:38 | 2023-09-20 | 01:57 | 0.013194 | 0 | 19 | [5 empty] | Tripped due to DP operated, Phase-AN, Zone1, Distance=51.99KM Ia=81.47A, Ib=36.39A, Ic=129.5A.
|  | 2023-09-20 | 16:07 | 2023-09-20 | 16:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-09-29 | 23:10 | 2023-09-29 | 23:29 | 0.013194 | 0 | 19 | [5 empty] | Failed due to Patnagarh-Padampur line tripped.
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-08-16 | 13:22 | 2023-08-16 | 20:32 | 0.29861 | 0 | 13 | [5 empty] | R-phase LA burst, Ia-187.1A, Ib-128.9 A, Ic-238.7A, In-491.2A. Rph LA burst. supply was availed from GSS , Khariar
|  | 2023-09-02 | 14:37 | 2023-09-02 | 14:44 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Padampur due to DP operated.
|  | 2023-09-05 | 11:17 | 2023-09-05 | 11:28 | 0.0076389 | 0 | 11 | [5 empty] | Tripped from Padampur due to DP operated.
|  | 2023-10-11 | 10:00 | 2023-10-11 | 10:05 | 0.0034722 | 0 | 5 | [5 empty] | Supply failed from Source end(Bolangir New). -
|  | 2023-12-17 | 00:48 | 2023-12-17 | 01:10 | 00:22 | 0 | 22 | [5 empty] | Tripped from Patnagarh. -
|  | 2024-03-12 | 10:07 | 2024-03-12 | 10:21 | 0.0097222 | 0 | 14 | [5 empty] | LBB. -
|  | 2024-03-12 | 10:36 | 2024-03-12 | 10:51 | 0.010417 | 0 | 15 | [5 empty] | LBB. -
|  | 2023-04-24 | 17:05 | 2023-04-24 | 17:17 | 0.0083333 | 0 | 12 | [5 empty] | Phase-AN, Distance=54.93KM, Ia=951.6A, Ib=108.4A, Ic=141.1A, In=701.8A.
|  | 2023-04-26 | 19:16 | 2023-04-27 | 2:40 | 0.225 | 0 | 10 | [5 empty] | Source failure. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-04-26 | 19:16 | 2023-04-26 | 19:26 | 0.0069444 | 0 | 10 | [5 empty] | Phase-AN, Zone-1, Distance=7.162KM, Ia=375.2A, Ib=309.7A, Ic=605.3A. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-06-17 | 13:00 | 2023-06-17 | 13:10 | 0.0069444 | 0 | 10 | [5 empty] | Source Failure from 132/33KV GSS Khariar.
|  | 2023-07-23 | 13:18 | 2023-07-23 | 13:26 | 0.0055556 | 0 | 8 | [5 empty] | Distance Protection operated. Phase-BC, Zone-3, Location- 100.6km, Ia=61.3A, Ib=897.3A, Ic=841A.
|  | 2023-10-08 | 09:08 | 2023-10-08 | 09:19 | 0.0076389 | 7 | 11 | [5 empty] | Supply failed from Bolangir (New) GSS. -
|  | 2024-03-15 | 09:22 | 2024-03-15 | 09:37 | 0.010417 | 0 | 15 | [5 empty] | Source failure from Patnagarh. -
|  | 2024-01-04 | 12:57 | 2024-01-04 | 13:02 | 0.0034722 | 0 | 4 | [5 empty] | Tripped due to sparking in the Y-Ph SI contact point of TRF-II. If- 186.3A. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
463 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0.015278 | 0 | 22 | [7 empty] | 15.45 | 8760 | 100% | 5.665 | 135342
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:25 | 0.015278 | 0 | 22 | [5 empty] | Y-N, Dist- 0.47 m, Zone 3, Iy- 1.238 kA At Purusottampur end: Y-B (O/C), E/F, Dist-17.6 km, Iy- 0.52 kA, Ib- 0.48 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
464 | 132kV Rairakhole- Rairakhole RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.5 | 8760 | 100% | 0 | 30660
465 | 132kV Rajgangpur-OCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.5 | 8760 | 100% | 0 | 4380
466 | 132kV Rajgangapur-Rajgangapur RTSS |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 4.2 | 8760 | 100% | 0.42 | 36792
|  | 2023-05-18 | 13:31 | 2023-05-18 | 13:37 | 0.0041667 | 0 | 6 | [5 empty] | TRIPPED ON R & Y PH O/C.
467 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.1 | 8760 | 100% | 0 | 237396
468 | 132kV Ranasinghpur-Badagada (Kesura) |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 34.23 | 8760 | 100% | 10.269 | 299854.8
|  | 2023-07-31 | 20:48 | 2023-07-31 | 21:06 | 0.0125 | 0 | 18 | [5 empty] | At Kesura end:- R-B ph O/C, IR=1.423A, IY=221A, IB=1.845kA At Ranasinghpur end:- No tripping. Ranasinghpur GSS was availing load from Kesura end. When 33kV Assotech feeder(faulty feeder) was charged at Ranasinghpur
469 | 132kV TS Alloys-Choudwar |  |  |  |  | 0.034028 | 12 | 42 | [7 empty] | 22.6 | 8760 | 99.86% | 287.02 | 197976
|  | 2023-06-17 | 14:54 | 2023-06-17 | 15:15 | 0.014583 | 0 | 14 | [5 empty] | Power supply failed from Nuapatna/Banki. Nuapatna and Arati were availing P/S from Banki
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:39 | 0.014583 | 0 | 21 | [5 empty] | On field verification it was found that R phase wavetrap ICCL-Choudwar fdr was on fire due to snake fault.. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
470 | 132kV TS Alloys-Ultratech |  |  |  |  | 0.024306 | 12 | 28 | [7 empty] | 22.067 | 8760 | 99.86% | 275.1019 | 193306.92
|  | 2023-06-17 | 14:54 | 2023-06-17 | 15:15 | 0.014583 | 0 | 14 | [5 empty] | Power supply failed from Nuapatna/Banki. Nuapatna and Arati were availing P/S from Banki
|  | 2023-06-04 | 20:40 | 2023-06-04 | 20:47 | 0.0048611 | 0 | 7 | [5 empty] | Trippped during rainy weather.
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
471 | 132kV Ultratech-Arati Steel |  |  |  |  | 0.024306 | 12 | 28 | [7 empty] | 18.704 | 8760 | 99.86% | 233.1765 | 163847.04
|  | 2023-06-17 | 14:54 | 2023-06-17 | 15:15 | 0.014583 | 0 | 14 | [5 empty] | Power supply failed from Nuapatna/Banki. Nuapatna and Arati were availing P/S from Banki
|  | 2023-06-04 | 20:40 | 2023-06-04 | 20:47 | 0.0048611 | 0 | 7 | [5 empty] | Trippped during rainy weather.
|  | 2024-03-28 | 12:42 | 2024-03-28 | 12:49 | 0.0048611 | 0 | 7 | [5 empty] | At Choudwar end: O/C (B Ph), Zone 1, Dist- 4.626km, Ib- 4.777kA At Bidanasi end: O/C (Y Ph), Zone 1, Dist- 7.5km, Iy- 5.6kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
472 | 132kV Rayagada-Akhusingh |  |  |  |  | 0.18194 | 18 | 14 | [7 empty] | 49.2 | 8760 | 99.79% | 897.08 | 430992
|  | 2023-04-04 | 23:44 | 2023-04-04 | 23:57 | 0.0090278 | 0 | 13 | [5 empty] | E/F
|  | 2023-06-10 | 12:18 | 2023-06-10 | 12:39 | 0.014583 | 0 | 21 | [5 empty] | Incoming failure
|  | 2023-06-14 | 06:17 | 2023-06-14 | 06:54 | 0.025694 | 0 | 37 | [5 empty] | E/F, Ia=71A, Ib=71.1A, Ic=167A, Dist=17.14km
|  | 2023-06-16 | 13:28 | 2023-06-16 | 14:11 | 0.029861 | 0 | 43 | [5 empty] | Incoming failure
|  | 2023-06-16 | 19:39 | 2023-06-16 | 20:17 | 0.026389 | 0 | 38 | [5 empty] | Incoming failure
|  | 2023-06-18 | 07:40 | 2023-06-18 | 07:50 | 0.0069444 | 0 | 10 | [5 empty] | Incoming failure
|  | 2023-06-20 | 15:01 | 2023-06-20 | 15:09 | 0.0055556 | 0 | 8 | [5 empty] | Incoming failure
|  | 2023-09-22 | 18:20 | 2023-09-22 | 18:46 | 0.018056 | 0 | 26 | [5 empty] | Incomer failure
|  | 2023-09-29 | 10:19 | 2023-09-29 | 10:42 | 0.015972 | 0 | 23 | [5 empty] | Incomer failure
|  | 2023-10-02 | 18:08 | 2023-10-02 | 18:38 | 0.020833 | 0 | 30 | [5 empty] | Machhkund I/C failed
|  | 2023-10-03 | 20:18 | 2023-10-03 | 20:27 | 0.00625 | 0 | 9 | [5 empty] | Machhkund I/C failed
|  | 2023-11-03 | 09:03 | 2023-11-03 | 09:07 | 0.0027778 | 0 | 4 | [5 empty] | E/F
|  | 2023-08-05 | 9:57 | 2023-08-05 | 10:12 | 0:15 | 0 | 15 | [5 empty] | Ia=140a, Ib=530a,Ic=110a, LOC=75.1km.
|  | 2023-08-12 | 19:26 | 2023-08-12 | 19:30 | 0:04 | 0 | 4 | [5 empty] | Ia=130a, Ib=260a,Ic=600a, LOC=131.3km., Zone=3, B-phase.
|  | 2023-06-19 | 01:33 | 2023-06-19 | 01:50 | 0.011806 | 0 | 17 | [5 empty] | Incoming failure.
|  | 2023-08-03 | 11:32 | 2023-08-03 | 11:39 | 0.0048611 | 0 | 7 | [5 empty] | Tripped from Machhkund end. -
|  | 2023-08-03 | 11:42 | 2023-08-03 | 12:45 | 0.04375 | 0 | 25 | [5 empty] | AutoTripped on General trip, E/F PU, IL1= 0.17kA, IL2= 0.62kA, IL3= 0.11kA 1614mS, Rsec= 94ohm, Xsec= 9.34ohm, Rpri= 282.01ohm, Xpri= 28.02 ohm, Dist= 71.8KM.. the line was declared faulty.Akhusingh gss availed load from Gunupur
|  | 2023-08-03 | 12:45 | 04.08.23 | 16:05 | 1899-12-31 03:20 | 0 | 20 | [5 empty] | AutoTripped on General trip, E/F PU, L2-E, Dir. O/C & E/F relay optd.IL1= 0.02kA, IL2= 0.36kA, IL3= 0.02kA 1614mS, Rsec= 44.96ohm, Xsec= 13.80ohm, Rpri= 134.88 Ohm, Xpri= 41.41 ohm, Dist= 98.6 KM.. Yph insulator puncture at Loc 4,10 & 428
|  | 2023-06-07 | 15:04 | 2023-06-07 | 15:13 | 0.00625 | 0 | 9 | [5 empty] | Incoming failure. Charged after getting confirmation from Rayagada GSS.
|  | 2023-06-12 | 14:24 | 2023-06-12 | 14:39 | 0.010417 | 0 | 15 | [5 empty] | Incoming failure.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
473 | 132kV Rayagada-Rayagada Traction |  |  |  |  | 0.35278 | 2 | 59 | [7 empty] | 2.646 | 8760 | 99.97% | 7.8939 | 23178.96
|  | 2023-10-02 | 18:08 | 2023-10-02 | 18:38 | 0.020833 | 0 | 5 | [5 empty] | Machhkund I/C failed
|  | 2024-03-09 | 10:42 | 2024-03-09 | 18:40 | 7:58 | 2 | 54 | [5 empty] | At Therubali end: Y-N, , Iy- 2.22 kA At Rayagada end: Y-N, , Iy- 2.75kA. Tree fallen on Conductor
474 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.3 | 8760 | 100% | 0 | 2628
475 | 132kV Rourkela-Bhalulata RTSS |  |  |  |  | 0.47917 | 23 | 30 | [7 empty] | 23.89 | 8760 | 99.73% | 561.415 | 209276.4
|  | 2023-04-19 | 10:20 | 2023-04-19 | 10:38 | 0.0125 | 0 | 18 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=57.71 km, zone-2,event =ABT,Fault current details-: IA=2143 A,IB=2237 A,IC=34 A, IN=0 A,IG=207 A. FDR CHARGED & STOOD OK
|  | 2023-04-25 | 07:20 | 2023-04-25 | 08:35 | 0.052083 | 1 | 15 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=0.75 km, zone-1,event =BGT,Fault current details-: IA=226 A,IB=13480 A,IC=179 A, IN=1 A,IG=13076 A. FDR CHARGED & STOOD OK
|  | 2023-04-27 | 15:33 | 2023-04-27 | 15:43 | 0.0069444 | 0 | 10 | [5 empty] | At Rourkela-D.P & M/T relay indication,D.P relay details-:loc=40.21 km, zone-1,event =AGT,Fault current details-: IA=2338 A,IB=369 A,IC=388 A, IN=0 A,IG=1585 A. FDR CHARGED & STOOD OK
|  | 2023-05-19 | 19:09 | 2023-05-19 | 20:02 | 0.036806 | 0 | 53 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=60.75 km, zone- 2,event =ABT,Fault current details-: IA=2199 A,IB=2236 A,IC=106 A, IN=0 A,IG=1170 A. BAD WEATHER
|  | 2023-09-17 | 13:56 | 2023-09-17 | 14:16 | 0.013889 | 0 | 20 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=34.86 km, zone-1,event =ABCT,Fault current details-: IA=3465 A,IB=3785 A,IC=3568 A,IG=290 A.
|  | 2023-09-19 | 18:25 | 2023-09-19 | 18:36 | 0.0076389 | 0 | 11 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=45 km, zone- 1,event =ABCT,Fault current details-: IA=2921 A,IB=3190 A,IC=2978 A.
|  | 2023-09-26 | 18:26 | 2023-09-26 | 19:29 | 0.04375 | 1 | 3 | [5 empty] | D.P & M/T relay indication,D.P relay details-:loc=36.02 km, zone-1,event =ABCT,Fault current details-: IA=3460 A,IB=3614 A,IC=3241 A,IG=213 A.
|  | 2023-10-10 | 11:39 | 2023-10-10 | 18:40 | 0.29236 | 7 | 1 | [5 empty] | Zone 1,Y-N, Dist- 12.87 km, Iy- 2.155 kA. -
|  | 2023-10-19 | 19:55 | 2023-10-19 | 20:06 | 0.0076389 | 0 | 11 | [5 empty] | At Rourkela end: Ir- 3.083 kA, Iy- 2.991 kA, Zone 1, Dist- 40.15 km At BK Steel end: Iy- 0.663 kA, Zone 1, Dist- 40.53 km. Feeder Charged but tripped immediately
|  | 2023-12-23 | 10:24 | 2023-12-23 | 10:32 | 0.0055556 | 0 | 8 | [5 empty] | At Rourkela end: O/C, Ir- 0.292 kA, Iy- 0.211 kA, Ib- 0.398 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
476 | 132 kV New Bolangir - Bolangir Ckt - I |  |  |  |  | 0.0125 | 0 | 18 | [7 empty] | 3.78 | 8760 | 100% | 1.134 | 33112.8
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:31 | 0.0090278 | 0 | 13 | [5 empty] | Failed from source. -
477 | 132kV Bolangir- ACME |  |  |  |  | 0.034722 | 12 | 20 | [7 empty] | 21.62 | 8760 | 99.86% | 266.6467 | 189391.2
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
478 | 132 kV ACME - Tusura |  |  |  |  | 0.034722 | 12 | 20 | [7 empty] | 24.02 | 8760 | 99.86% | 296.2467 | 210415.2
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
479 | 132 kV Tusura- Saintala |  |  |  |  | 0.034722 | 13 | 55 | [7 empty] | 22.38 | 8760 | 99.84% | 311.455 | 196048.8
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-06-09 | 14:27 | 2023-06-09 | 16:02 | 01:35 | 1 | 35 | [5 empty] | Tripped on E/f [Due to Y-ph CT of 132kV OPTCL-OFBL I/C (OFBL S/Y) Burst]. Due to Y-ph CT of 132kV OPTCL- OFBL I/C (OFBL S/Y) Burst
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
480 | 132kV Tusura -RTSS Deogaon road |  |  |  |  | 0.040972 | 12 | 29 | [7 empty] | 9.991 | 8760 | 99.86% | 124.721 | 87521.16
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
|  | 2023-08-19 | 17:20 | 2023-08-19 | 17:23 | 0:03 | 0 | 3 | [5 empty] | O/C. -
|  | 2023-10-01 | 11:19 | 2023-10-01 | 11:21 | 0:02 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-10-18 | 13:38 | 2023-10-18 | 13:40 | 0:02 | 0 | 2 | [5 empty] | O/C. -
|  | 2023-10-19 | 15:18 | 2023-10-19 | 15:20 | 0:02 | 0 | 2 | [5 empty] | O/C. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
481 | 132kV Saintala- ABREL |  |  |  |  | 0.034722 | 13 | 49 | [7 empty] | 3 | 8760 | 99.84% | 41.45 | 26280
|  | 2023-04-18 | 16:54 | 2023-04-18 | 16:59 | 0.0034722 | 0 | 5 | [5 empty] | Source Failure
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-06-09 | 14:27 | 2023-06-09 | 16:02 | 01:35 | 1 | 35 | [5 empty] | Tripped on E/f [Due to Y-ph CT of 132kV OPTCL-OFBL I/C (OFBL S/Y) Burst]. Due to Y-ph CT of 132kV OPTCL- OFBL I/C (OFBL S/Y) Burst
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
482 | 132kV ABREL- Kesinga |  |  |  |  | 0.036111 | 13 | 57 | [7 empty] | 33 | 8760 | 99.84% | 460.35 | 289080
|  | 2023-04-18 | 16:52 | 2023-04-18 | 16:59 | 0.0048611 | 0 | 7 | [5 empty] | O/C
|  | 2023-11-03 | 23:18 | 2023-11-03 | 23:55 | 0.025694 | 0 | 7 | [5 empty] | O/C R-Ph, E/F. -
|  | 2023-06-09 | 14:27 | 2023-06-09 | 16:02 | 01:35 | 1 | 35 | [5 empty] | Tripped on E/f [Due to Y-ph CT of 132kV OPTCL-OFBL I/C (OFBL S/Y) Burst]. Due to Y-ph CT of 132kV OPTCL- OFBL I/C (OFBL S/Y) Burst
|  | 2023-07-17 | 23:27 | 2023-07-17 | 23:35 | 0:08 | 0 | 8 | [5 empty] | No relay indication. Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
483 | 132kV Kesinga-Khariar |  |  |  |  | 0.12431 | 14 | 59 | [7 empty] | 57.7 | 8760 | 99.83% | 864.5383 | 505452
|  | 2023-04-22 | 20:49 | 2023-04-22 | 21:08 | 0.013194 | 0 | 19 | [5 empty] | DP.
|  | 2023-06-17 | 12:59 | 2023-06-17 | 13:09 | 0.0069444 | 0 | 10 | [5 empty] | O/C.
|  | 2023-06-20 | 13:20 | 2023-06-20 | 13:25 | 0.0034722 | 0 | 5 | [5 empty] | O/C.
|  | 2023-07-04 | 17:35 | 2023-07-04 | 17:47 | 0.0083333 | 0 | 12 | [5 empty] | DP, Zone-1, Dist-39.33km.
|  | 2023-07-12 | 02:57 | 2023-07-12 | 03:04 | 0.0048611 | 0 | 7 | [5 empty] | DP, Zone-1, Rph, Ir=164.7A.
|  | 2023-07-12 | 16:57 | 2023-07-12 | 17:03 | 0.0041667 | 0 | 6 | [5 empty] | D.P.
|  | 2023-07-31 | 03:55 | 2023-07-31 | 04:01 | 0.0041667 | 0 | 6 | [5 empty] | DP, Zone-1, Bph, Ib=1.59kA.
|  | 2023-09-26 | 19:33 | 2023-09-26 | 19:43 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end:- E/F, Zone-1, R-2.07kA, Dist-37.91km. E/F
|  | 2023-10-05 | 23:27 | 2023-10-05 | 23:38 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga end: Ir- 0.131 kA, Iy- 0.412 kA, Ib- 2.8 kA At Khariar end: Zone 1, Dist- 23.3 km from Kesinga end, B Ph O/C, Ib- 2.84 kA. -
|  | 2023-10-15 | 21:58 | 2023-10-15 | 22:10 | 0.0083333 | 0 | 12 | [5 empty] | At Kesinga end: Ir- 0.14 kA, Iy- 0.423 kA, Ib-2.85 kA At Khariar end: Zone 1, B Ph (O/C), Ib- 2.85 kA, Dist- 23.21 km from Kesinga end. -
|  | 2023-10-26 | 05:18 | 2023-10-26 | 05:24 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end: Ir- 139.9A Iy- 378.7A, Ib- 2.95 kA At Khariar end: Zone 1, Dist- 23.16 km from Kesinga end, B Ph (O/C), Ib- 2.95 kA. -
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-10 | 08:42 | 2024-01-10 | 08:48 | 0.0041667 | 0 | 6 | [5 empty] | O/C. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2023-05-10 | 04:50 | 2023-05-10 | 04:52 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Kesinga on over current R-Ph , 440Amp.. Tripped from Kesinga on over current R-Ph , 440Amp.
|  | 2023-08-30 | 17:10 | 2023-08-30 | 17:23 | 0.0090278 | 0 | 13 | [5 empty] | Tripped on R-Y -Phase O/C, Ir=460A, Iy=360A, Ib=300A. TRIPPED ON R-Y - Phase O/C R-ph:460Amp , Y-ph- 360Amp , B-ph-300Amp.
|  | 2023-11-23 | 00:12 | 2023-11-23 | 00:22 | 0.0069444 | 0 | 10 | [5 empty] | B-N, Zone 1, Dist-14.21 km from Kesinga end, Ib- 3.81 kA. -
|  | 2024-03-24 | 14:35 | 2024-03-24 | 14:38 | 0.0020833 | 0 | 3 | [5 empty] | BRC Alarm on DP. Tripped from GSS Khariar simultaneously with 33kV Khariar-1 feeder tripped on under frequency
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
484 | 132 kV Khariar - Kantabanji |  |  |  |  | 0.19583 | 16 | 42 | [7 empty] | 32.6 | 8760 | 99.81% | 544.42 | 285576
|  | 2023-06-02 | 11:00 | 2023-06-02 | 11:02 | 0.0013889 | 0 | 2 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-06 | 13:54 | 2023-06-06 | 14:07 | 0.0090278 | 0 | 13 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-06 | 14:38 | 2023-06-06 | 14:40 | 0.0013889 | 0 | 2 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-08-30 | 10:01 | 2023-08-30 | 10:12 | 0.0076389 | 0 | 11 | [5 empty] | Incomer failure. -
|  | 2023-10-05 | 23:28 | 2023-10-05 | 23:38 | 0.0069444 | 0 | 10 | [5 empty] | tripped from Khariar end. -
|  | 2023-10-31 | 02:03 | 2023-10-31 | 02:12 | 0.00625 | 0 | 9 | [5 empty] | At Khariar end: Zone 1, Dist- 23.16 km from Kesinga end, R Ph O/C, Ir - 3.95 kA. -
|  | 2023-11-03 | 21:58 | 2023-11-03 | 22:00 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Khariar end. -
|  | 2023-11-25 | 08:58 | 2023-11-25 | 09:02 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Khariar end. -
|  | 2023-11-25 | 17:48 | 2023-11-25 | 17:57 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Khariar end. -
|  | 2024-03-05 | 16:12 | 2024-03-05 | 16:17 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from GSS Khariar end. -
|  | 2024-03-05 | 17:02 | 2024-03-05 | 17:03 | 0.00069444 | 0 | 1 | [5 empty] | Tripped from GSS Khariar end. -
|  | 2023-04-22 | 20:50 | 2023-04-22 | 21:10 | 0.013889 | 0 | 20 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-04-22 | 20:49 | 2023-04-22 | 21:08 | 0.013194 | 0 | 19 | [5 empty] | DP.
|  | 2023-06-17 | 13:00 | 2023-06-17 | 13:11 | 0.0076389 | 0 | 11 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-17 | 12:59 | 2023-06-17 | 13:09 | 0.0069444 | 0 | 10 | [5 empty] | O/C.
|  | 2023-06-20 | 13:22 | 2023-06-20 | 13:26 | 0.0027778 | 0 | 4 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-20 | 13:20 | 2023-06-20 | 13:25 | 0.0034722 | 0 | 5 | [5 empty] | O/C.
|  | 2023-07-04 | 17:35 | 2023-07-04 | 17:47 | 0.0083333 | 0 | 12 | [5 empty] | DP, Zone-1, Dist-39.33km.
|  | 2023-07-12 | 02:57 | 2023-07-12 | 03:04 | 0.0048611 | 0 | 7 | [5 empty] | DP, Zone-1, Rph, Ir=164.7A.
|  | 2023-07-12 | 16:57 | 2023-07-12 | 17:03 | 0.0041667 | 0 | 6 | [5 empty] | D.P.
|  | 2023-07-31 | 03:55 | 2023-07-31 | 04:01 | 0.0041667 | 0 | 6 | [5 empty] | DP, Zone-1, Bph, Ib=1.59kA.
|  | 2023-09-26 | 19:33 | 2023-09-26 | 19:43 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end:- E/F, Zone-1, R-2.07kA, Dist-37.91km. E/F
|  | 2023-10-05 | 23:27 | 2023-10-05 | 23:38 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga end: Ir- 0.131 kA, Iy- 0.412 kA, Ib- 2.8 kA At Khariar end: Zone 1, Dist- 23.3 km from Kesinga end, B Ph O/C, Ib- 2.84 kA. -
|  | 2023-10-15 | 21:58 | 2023-10-15 | 22:10 | 0.0083333 | 0 | 12 | [5 empty] | At Kesinga end: Ir- 0.14 kA, Iy- 0.423 kA, Ib-2.85 kA At Khariar end: Zone 1, B Ph (O/C), Ib- 2.85 kA, Dist- 23.21 km from Kesinga end. -
|  | 2023-10-26 | 05:18 | 2023-10-26 | 05:24 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end: Ir- 139.9A Iy- 378.7A, Ib- 2.95 kA At Khariar end: Zone 1, Dist- 23.16 km from Kesinga end, B Ph (O/C), Ib- 2.95 kA. -
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-10 | 08:42 | 2024-01-10 | 08:48 | 0.0041667 | 0 | 6 | [5 empty] | O/C. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2023-05-10 | 04:50 | 2023-05-10 | 04:52 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Kesinga on over current R-Ph , 440Amp.. Tripped from Kesinga on over current R-Ph , 440Amp.
|  | 2023-08-30 | 17:10 | 2023-08-30 | 17:23 | 0.0090278 | 0 | 13 | [5 empty] | Tripped on R-Y -Phase O/C, Ir=460A, Iy=360A, Ib=300A. TRIPPED ON R-Y - Phase O/C R-ph:460Amp , Y-ph- 360Amp , B-ph-300Amp.
|  | 2023-11-23 | 00:12 | 2023-11-23 | 00:22 | 0.0069444 | 0 | 10 | [5 empty] | B-N, Zone 1, Dist-14.21 km from Kesinga end, Ib- 3.81 kA. -
|  | 2024-03-24 | 14:35 | 2024-03-24 | 14:38 | 0.0020833 | 0 | 3 | [5 empty] | BRC Alarm on DP. Tripped from GSS Khariar simultaneously with 33kV Khariar-1 feeder tripped on under frequency
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
485 | 132kV Kantabanji- Kantabanji RTSS |  |  |  |  | 0.22778 | 17 | 28 | [7 empty] | 4 | 8760 | 99.8% | 69.8667 | 35040
|  | 2023-04-01 | 11:57 | 2023-04-01 | 11:58 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-04-03 | 12:38 | 2023-04-03 | 12:43 | 0.0034722 | 0 | 5 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-04-12 | 23:44 | 2023-04-12 | 23:45 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-04-19 | 10:34 | 2023-04-19 | 10:35 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-04-21 | 05:38 | 2023-04-21 | 05:40 | 0.0013889 | 0 | 2 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-04-29 | 19:37 | 2023-04-29 | 19:38 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-06-02 | 11:00 | 2023-06-02 | 11:02 | 0.0013889 | 0 | 2 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-03 | 20:54 | 2023-06-03 | 20:55 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-06-06 | 13:54 | 2023-06-06 | 14:07 | 0.0090278 | 0 | 13 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-06 | 14:38 | 2023-06-06 | 14:40 | 0.0013889 | 0 | 2 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-20 | 18:40 | 2023-06-20 | 18:41 | 0.00069444 | 0 | 1 | [5 empty] | Tripped on Overcurrent (line to line fault).
|  | 2023-08-30 | 10:01 | 2023-08-30 | 10:12 | 0.0076389 | 0 | 11 | [5 empty] | Incomer failure. -
|  | 2023-10-01 | 22:52 | 2023-10-01 | 22:53 | 0.00069444 | 0 | 1 | [5 empty] | tripped on L-G fault with fault current 1.2 kA. -
|  | 2023-10-05 | 23:28 | 2023-10-05 | 23:38 | 0.0069444 | 0 | 10 | [5 empty] | tripped from Khariar end. -
|  | 2023-10-31 | 02:03 | 2023-10-31 | 02:12 | 0.00625 | 0 | 9 | [5 empty] | At Khariar end: Zone 1, Dist- 23.16 km from Kesinga end, R Ph O/C, Ir - 3.95 kA. -
|  | 2023-11-03 | 21:58 | 2023-11-03 | 22:00 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Khariar end. -
|  | 2023-11-12 | 04:50 | 2023-11-12 | 04:51 | 0.00069444 | 0 | 1 | [5 empty] | L-L Fault. -
|  | 2023-11-23 | 05:32 | 2023-11-23 | 05:33 | 0.00069444 | 0 | 1 | [5 empty] | L-L Fault. -
|  | 2023-11-25 | 08:58 | 2023-11-25 | 09:02 | 0.0027778 | 0 | 4 | [5 empty] | Tripped from Khariar end. -
|  | 2023-11-25 | 17:48 | 2023-11-25 | 17:57 | 0.00625 | 0 | 9 | [5 empty] | Tripped from Khariar end. -
|  | 2023-11-29 | 15:36 | 2023-11-29 | 15:37 | 0.00069444 | 0 | 1 | [5 empty] | L-L Fault. -
|  | 2023-12-01 | 18:14 | 2023-12-01 | 18:16 | 0.0013889 | 0 | 2 | [5 empty] | L-L Fault, If- 560A. -
|  | 2023-12-14 | 16:26 | 2023-12-14 | 16:27 | 0.00069444 | 0 | 1 | [5 empty] | L-L fault. -
|  | 2023-12-29 | 22:12 | 2023-12-29 | 22:14 | 0.0013889 | 0 | 2 | [5 empty] | L-L fault. -
|  | 2024-01-07 | 16:58 | 2024-01-07 | 16:59 | 0.00069444 | 0 | 1 | [5 empty] | L-L fault, If- 0.57kA. -
|  | 2024-01-31 | 10:24 | 2024-01-31 | 10:36 | 0.0083333 | 0 | 12 | [5 empty] | L-L Fault with If- 0.560 kA. -
|  | 2024-02-02 | 15:28 | 2024-02-02 | 15:31 | 0.0020833 | 0 | 3 | [5 empty] | L-L fault with If- 0.634kA. -
|  | 2024-02-04 | 15:05 | 2024-02-04 | 15:08 | 0.0020833 | 0 | 3 | [5 empty] | L-L fault with If- 0.64kA. -
|  | 2024-02-11 | 16:43 | 2024-02-11 | 16:45 | 0.0013889 | 0 | 2 | [5 empty] | L-L fault with If- 0.418kA. -
|  | 2024-02-12 | 14:34 | 2024-02-12 | 14:36 | 0.0013889 | 0 | 2 | [5 empty] | L-L fault with If- 0.602kA. -
|  | 2024-03-05 | 16:12 | 2024-03-05 | 16:17 | 0.0034722 | 0 | 5 | [5 empty] | Tripped from GSS Khariar end. -
|  | 2024-03-05 | 17:02 | 2024-03-05 | 17:03 | 0.00069444 | 0 | 1 | [5 empty] | Tripped from GSS Khariar end. -
|  | 2024-03-28 | 04:59 | 2024-03-28 | 05:00 | 0.00069444 | 0 | 1 | [5 empty] | L-L fault, If- 0.576kA. -
|  | 2023-04-22 | 20:50 | 2023-04-22 | 21:10 | 0.013889 | 0 | 20 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-04-22 | 20:49 | 2023-04-22 | 21:08 | 0.013194 | 0 | 19 | [5 empty] | DP.
|  | 2023-06-17 | 13:00 | 2023-06-17 | 13:11 | 0.0076389 | 0 | 11 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-17 | 12:59 | 2023-06-17 | 13:09 | 0.0069444 | 0 | 10 | [5 empty] | O/C.
|  | 2023-06-20 | 13:22 | 2023-06-20 | 13:26 | 0.0027778 | 0 | 4 | [5 empty] | INCOMER SUPPLY FAILED FROM GSS KHARIAR END.
|  | 2023-06-20 | 13:20 | 2023-06-20 | 13:25 | 0.0034722 | 0 | 5 | [5 empty] | O/C.
|  | 2023-07-04 | 17:35 | 2023-07-04 | 17:47 | 0.0083333 | 0 | 12 | [5 empty] | DP, Zone-1, Dist-39.33km.
|  | 2023-07-12 | 02:57 | 2023-07-12 | 03:04 | 0.0048611 | 0 | 7 | [5 empty] | DP, Zone-1, Rph, Ir=164.7A.
|  | 2023-07-12 | 16:57 | 2023-07-12 | 17:03 | 0.0041667 | 0 | 6 | [5 empty] | D.P.
|  | 2023-07-31 | 03:55 | 2023-07-31 | 04:01 | 0.0041667 | 0 | 6 | [5 empty] | DP, Zone-1, Bph, Ib=1.59kA.
|  | 2023-09-26 | 19:33 | 2023-09-26 | 19:43 | 0.0069444 | 0 | 10 | [5 empty] | At Kesinga end:- E/F, Zone-1, R-2.07kA, Dist-37.91km. E/F
|  | 2023-10-05 | 23:27 | 2023-10-05 | 23:38 | 0.0076389 | 0 | 11 | [5 empty] | At Kesinga end: Ir- 0.131 kA, Iy- 0.412 kA, Ib- 2.8 kA At Khariar end: Zone 1, Dist- 23.3 km from Kesinga end, B Ph O/C, Ib- 2.84 kA. -
|  | 2023-10-15 | 21:58 | 2023-10-15 | 22:10 | 0.0083333 | 0 | 12 | [5 empty] | At Kesinga end: Ir- 0.14 kA, Iy- 0.423 kA, Ib-2.85 kA At Khariar end: Zone 1, B Ph (O/C), Ib- 2.85 kA, Dist- 23.21 km from Kesinga end. -
|  | 2023-10-26 | 05:18 | 2023-10-26 | 05:24 | 0.0041667 | 0 | 6 | [5 empty] | At Kesinga end: Ir- 139.9A Iy- 378.7A, Ib- 2.95 kA At Khariar end: Zone 1, Dist- 23.16 km from Kesinga end, B Ph (O/C), Ib- 2.95 kA. -
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-10 | 08:42 | 2024-01-10 | 08:48 | 0.0041667 | 0 | 6 | [5 empty] | O/C. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2023-05-10 | 04:50 | 2023-05-10 | 04:52 | 0.0013889 | 0 | 2 | [5 empty] | Tripped from Kesinga on over current R-Ph , 440Amp.. Tripped from Kesinga on over current R-Ph , 440Amp.
|  | 2023-08-30 | 17:10 | 2023-08-30 | 17:23 | 0.0090278 | 0 | 13 | [5 empty] | Tripped on R-Y -Phase O/C, Ir=460A, Iy=360A, Ib=300A. TRIPPED ON R-Y - Phase O/C R-ph:460Amp , Y-ph- 360Amp , B-ph-300Amp.
|  | 2023-11-23 | 00:12 | 2023-11-23 | 00:22 | 0.0069444 | 0 | 10 | [5 empty] | B-N, Zone 1, Dist-14.21 km from Kesinga end, Ib- 3.81 kA. -
|  | 2024-03-24 | 14:35 | 2024-03-24 | 14:38 | 0.0020833 | 0 | 3 | [5 empty] | BRC Alarm on DP. Tripped from GSS Khariar simultaneously with 33kV Khariar-1 feeder tripped on under frequency
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
486 | 132 kV Khariar - Nuapada |  |  |  |  | 0.082639 | 13 | 49 | [7 empty] | 76.43 | 8760 | 99.84% | 1056.0078 | 669526.8
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-10 | 08:42 | 2024-01-10 | 08:48 | 0.0041667 | 0 | 6 | [5 empty] | O/C. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2023-04-18 | 14:15 | 2023-04-18 | 14:18 | 0.0020833 | 0 | 3 | [5 empty] | DP Operated.
|  | 2023-05-15 | 13:39 | 2023-05-15 | 13:45 | 0.0041667 | 0 | 6 | [5 empty] | DP Operated, Started phase C, zone 1, 4.3km.
|  | 2023-09-07 | 07:12 | 2023-09-07 | 08:15 | 0.04375 | 0 | 53 | [5 empty] | Tripped due to LBB operated.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
487 | 132kV Nuapada-Nuapada RTSS |  |  |  |  | 0.46528 | 16 | 47 | [7 empty] | 4.528 | 8760 | 99.81% | 75.9949 | 39665.28
|  | 2023-12-28 | 08:05 | 2023-12-28 | 08:14 | 0.00625 | 0 | 9 | [5 empty] | O/C, Ir- 0.54 kA, Iy- 0.56 kA, Ib- 0.49 kA. Tripped on O/C at Khariar end. -
|  | 2024-01-10 | 08:42 | 2024-01-10 | 08:48 | 0.0041667 | 0 | 6 | [5 empty] | O/C. -
|  | 2024-01-16 | 09:24 | 2024-01-16 | 09:34 | 0.0069444 | 0 | 10 | [5 empty] | O/C. -
|  | 2024-02-09 | 08:47 | 2024-02-09 | 09:02 | 0.010417 | 0 | 15 | [5 empty] | At Kesinga end: O/C, Ir- 0.44kA, Iy- 0.44kA, Ib- 0.34kA. -
|  | 2024-02-09 | 11:51 | 2024-02-09 | 11:58 | 0.0048611 | 0 | 7 | [5 empty] | At Kesinga end: O/C, Ir- 0.42kA, Iy- 0.45kA, Ib- 0.34kA. -
|  | 2023-04-18 | 14:15 | 2023-04-18 | 14:18 | 0.0020833 | 0 | 3 | [5 empty] | DP Operated.
|  | 2023-05-15 | 13:39 | 2023-05-15 | 13:45 | 0.0041667 | 0 | 6 | [5 empty] | DP Operated, Started phase C, zone 1, 4.3km.
|  | 2023-05-27 | 23:19 | 2023-05-27 | 23:21 | 0.0013889 | 0 | 2 | [5 empty] | DP Operated, zone 1, 3.7km.
|  | 2023-06-24 | 23:46 | 2023-06-24 | 23:51 | 0.0034722 | 0 | 5 | [5 empty] | tripped on o/c.
|  | 2023-09-07 | 07:12 | 2023-09-07 | 08:05 | 0.036806 | 0 | 53 | [5 empty] | Tripped due to LBB operated.
|  | 2024-03-26 | 23:53 | 2024-03-27 | 0:14 | 0.014583 | 0 | 21 | [5 empty] | LBB. -
|  | 2024-03-27 | 20:28 | 2024-03-27 | 20:39 | 0.0076389 | 0 | 11 | [5 empty] | LBB. -
|  | 2024-03-28 | 10:00 | 2024-03-28 | 10:06 | 0.0041667 | 0 | 6 | [5 empty] | LBB. -
|  | 2024-01-13 | 02:40 | 2024-01-13 | 02:42 | 0.0013889 | 0 | 2 | [5 empty] | Dist-3.17 km, Ir- 2.726A, Ib- 50mA. -
|  | 2023-05-20 | 22:44 | 2023-05-20 | 23:08 | 0.016667 | 0 | 24 | [5 empty] | Source Failure.
|  | 2023-09-20 | 01:38 | 2023-09-20 | 01:57 | 0.013194 | 0 | 19 | [5 empty] | Tripped due to DP operated, Phase-AN, Zone1, Distance=51.99KM Ia=81.47A, Ib=36.39A, Ic=129.5A.
|  | 2023-09-20 | 16:07 | 2023-09-20 | 16:20 | 0.0090278 | 0 | 13 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-09-29 | 23:10 | 2023-09-29 | 23:29 | 0.013194 | 0 | 19 | [5 empty] | Failed due to Patnagarh-Padampur line tripped.
|  | 2023-09-23 | 11:39 | 2023-09-23 | 11:49 | 0.0069444 | 0 | 10 | [5 empty] | Tripped from Source end GSS Sadeipali.
|  | 2023-04-24 | 17:05 | 2023-04-24 | 17:17 | 00:12 | 0 | 12 | [5 empty] | Phase-AN, Distance=54.93KM, Ia=951.6A, Ib=108.4A, Ic=141.1A, In=701.8A.
|  | 2023-04-26 | 19:26 | 2023-04-27 | 2:35 | 0.29792 | 0 | 10 | [5 empty] | S/D Availed for replacement of R phase Jumper at Loc No 140. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2023-04-26 | 19:16 | 2023-04-26 | 19:26 | 00:10 | 0 | 10 | [5 empty] | Phase-AN, Zone-1, Distance=7.162KM, Ia=375.2A, Ib=309.7A, Ic=605.3A. Supply was availed from Khariar- Nuapada line and extended to Padampur GSS
|  | 2024-03-15 | 09:22 | 2024-03-15 | 09:36 | 00:14 | 0 | 14 | [5 empty] | At Padampur end: B-N, Zone 1, Dist- 36.04km, Ir- 0.297kA, Iy- 0.576kA, Ib- 0.373kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
488 | 132kV Salipur-Kendrapara |  |  |  |  | 0.099306 | 12 | 36 | [7 empty] | 34 | 8760 | 99.86% | 428.4 | 297840
|  | 2023-06-30 | 18:18 | 2023-06-30 | 18:28 | 0.0069444 | 0 | 10 | [5 empty] | At Kendrapara end:-TRIPPED ON M/R DUE TO INCOMING FAIL AT SALIPUR END. Ir=499 A,Iy=996.38 A, Ib=1.61 KA At Salipur end:- No tripping. Entire Grid pulled out Snake fault in GSS, Choudwar
|  | 2023-10-09 | 12:39 | 2023-10-09 | 13:59 | 0.055556 | 0 | 16 | [5 empty] | At RAMCO end: Zone 1, Dist-36.6 km, Ir- 0.19 kA, Iy- 1.91 kA, Ib- 1.78 kA. Pattamundai grid was availing power supply from RAMCO end through Kendrapara reserve bus
|  | 2023-10-17 | 13:59 | 2023-10-17 | 14:52 | 0.036806 | 0 | 10 | [5 empty] | Supply Fail. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
489 | 132kV Samagara-Puri |  |  |  |  | 0.040972 | 0 | 59 | [7 empty] | 3.99 | 8760 | 99.99% | 3.9235 | 34952.4
|  | 2024-02-22 | 16:11 | 2024-02-22 | 17:10 | 0.040972 | 0 | 59 | [5 empty] | Faulty. -
490 | 132kV Samagara-Malatipatpur RTSS |  |  |  |  | 0.23125 | 14 | 3 | [7 empty] | 5.535 | 8760 | 99.84% | 77.7668 | 48486.6
|  | 2024-02-10 | 16:09 | 2024-02-10 | 19:55 | 0.15694 | 0 | 16 | [5 empty] | Ir- 518.1A, Iy- 618.7A, Ib- 542.6A. 132kV Nimapara-Puri Feeder was charged through reserve bus and Samagara Grid was availing power from Puri Grid through reserve bus.
|  | 2023-06-02 | 16:42 | 2023-06-02 | 17:30 | 0.033333 | 0 | 48 | [5 empty] | R Phase to Earth fault ,Zone 3 OPTD, Ir=2.1KA, Iy=0.51KA, Ib=1.02KA. 132 KV Pratapsan supply was extended to Samangara through Nimapara reserve bus. The feeder test charged but didn't stand. Jumper snapped of 132kV Samangara-Nimapara feeder. Station Supply availed from 132kV Puri. A/R not operated at Prapsasan.
|  | 2024-02-22 | 16:11 | 2024-02-22 | 17:10 | 0.040972 | 0 | 59 | [5 empty] | Faulty. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
491 | 132kV Samagara-Satasankha Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.07 | 8760 | 100% | 0 | 245893.2
492 | 132kV Samagara-Satasankha Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.07 | 8760 | 100% | 0 | 245893.2
493 | 132kV Sambalpur-Shyam DRI |  |  |  |  | 0.44514 | 20 | 54 | [7 empty] | 28.91 | 8760 | 99.76% | 604.219 | 253251.6
|  | 2023-05-18 | 10:45 | 2023-05-18 | 12:55 | 0.090278 | 2 | 10 | [5 empty] | Tripped on Yph E/F, Z1, Ia= 303A, Ib=2770A,Ic=435A, Ig=3281A,VA= 107.37KV, VB=76.64KV, VC=93.55KV,Vn=104.63KV, Fault dist.= 12.56KM Shyam DRI end:Yph E/F, Z1, Ia= 230A, Ib=3440A,Ic=360A, Fault dist.= 19.9KM. Transient fault
|  | 2023-08-19 | 10:58 | 2023-08-19 | 17:23 | 0.26736 | 4 | 38 | [5 empty] | At Sambalpur end:- Tripped on Z1, R- Yph O/C, Ia= 3593A, Ib=3496A,Ic=120A, In=92A, Fault dist.= 18.3km At Shyam DRI end:- Tripped on Z1, Ia= 6380A, Ib=6480A,Ic=60A, In=480A Fault dist.=6.8KM. fault found at Loc No. 86-87 & cleared
|  | 2023-09-30 | 17:07 | 2023-09-30 | 17:51 | 0.030556 | 0 | 44 | [5 empty] | Tripped on Z1, Y B- Yph O/C E/F, Ia= 554A, Ib=2888A,Ic=1930A, In=2170A, Fault dist.= 25.37KM.
|  | 2023-10-07 | 17:23 | 2023-10-07 | 18:08 | 0.03125 | 0 | 45 | [5 empty] | H/T. -
|  | 2024-03-19 | 21:16 | 2024-03-19 | 21:53 | 0.025694 | 0 | 37 | [5 empty] | At Sambalpur end: R-Y, E/F, Zone 1, Dist- 15.7km, Ir- 3.587kA, Iy- 0.131kA, Ib- 0.162kA At Shyam DRI end: R-Ph E/F, Zone 1, Dist- 9.8km. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
494 | 132kV Shamuka-Puri |  |  |  |  | 0.018056 | 0 | 6 | [7 empty] | 16.9 | 8760 | 100% | 1.69 | 148044
|  | 2023-07-20 | 09:43 | 2023-07-20 | 10:09 | 0.018056 | 0 | 6 | [5 empty] | Supply failure from Shamuka end due to automatic openeing of Isolator. Source failure
495 | 132kV Shyam DRI-Aryan Ispat |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4.2 | 8760 | 100% | 0 | 36792
496 | 132kV Aryan Ispat - Lapanga |  |  |  |  | 0.089583 | 12 | 39 | [7 empty] | 3.9 | 8760 | 99.86% | 49.335 | 34164
|  | 2023-08-22 | 7:43 | 2023-08-22 | 9:17 | 0.065278 | 0 | 4 | [5 empty] | O/C, E/F IR-0.521KA, IY-0.192KA, IC-3.569 KA. -
|  | 2023-10-07 | 17:19 | 2023-10-07 | 17:39 | 0.013889 | 0 | 20 | [5 empty] | At Lapanga end: R-N, Zone 1, Dist- 3.5km, IR=4.4kA At Aryan end: R-N, Zone 1, Dist- 2.93km. -
|  | 2024-02-16 | 16:46 | 2024-02-16 | 17:01 | 0.010417 | 0 | 15 | [5 empty] | At Jharsuguda end: Y-Ph, E/F, O/C, Ir- 0.343kA, Iy- 1.542kA, Ib- 0.367kA No tripping at Lapanga end. Tripped due to Y phase conductor snapped at Aryan switchyard.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
497 | 132kV Lapanga-SMC Power |  |  |  |  | 0.74375 | 19 | 48 | [7 empty] | 4.7 | 8760 | 99.77% | 93.06 | 41172
|  | 2023-07-29 | 19:17 | 2023-07-29 | 19:30 | 0.0090278 | 0 | 13 | [5 empty] | Ir=91.50A, Iy=67.57A, Ib=520A, In=503A, Vry=135kV, Vyb=105.7kV, Vbr=94.76kV. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2023-08-16 | 16:55 | 2023-08-16 | 18:26 | 0.063194 | 1 | 31 | [5 empty] | Tripped on E/F, Ir=129.5A, Iy=285A, Ib=132.5A, In=321A, Vry=116.4kV,Vyb=108.4kV, Vbr=134.4kV. Tripped from SMC end, Heavy Lightening and rain at SMC end
|  | 2023-11-15 | 02:57 | 2023-11-15 | 19:04 | 0.67153 | 6 | 4 | [5 empty] | At Lapanga end: Y-B, Zone 1, Dist- 3.04 km, Iy- 14.45 kA, Ib- 14.32kA No tripping at SMC end. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
498 | 132kV SMC Power-Kuchinda |  |  |  |  | 0.20625 | 16 | 57 | [7 empty] | 52.53 | 8760 | 99.81% | 890.3835 | 460162.8
|  | 2023-07-29 | 19:17 | 2023-07-29 | 19:30 | 0.0090278 | 0 | 13 | [5 empty] | Ir=91.50A, Iy=67.57A, Ib=520A, In=503A, Vry=135kV, Vyb=105.7kV, Vbr=94.76kV. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2023-08-16 | 16:55 | 2023-08-16 | 18:26 | 0.063194 | 1 | 31 | [5 empty] | Tripped on E/F, Ir=129.5A, Iy=285A, Ib=132.5A, In=321A, Vry=116.4kV,Vyb=108.4kV, Vbr=134.4kV. Tripped from SMC end, Heavy Lightening and rain at SMC end
|  | 2023-05-20 | 16:36 | 2023-05-20 | 16:52 | 0.011111 | 0 | 16 | [5 empty] | Tripped on D/P,Phase C-N,Zone-3,Fault Loc- 67.67km,IA=44A,IB=72A,IC=1415A.
|  | 2023-06-14 | 18:39 | 2023-06-14 | 19:33 | 0.0375 | 0 | 54 | [5 empty] | tripped ph B,Distance protection Zone1,Fault location=31.44Km,Ia=166.2A,Ib=917.5A,Ic=79.11A. power drawn from Rajgangpur end Via Kutra switching station.
|  | 2023-06-14 | 16:04 | 2023-06-14 | 17:05 | 0.042361 | 1 | 1 | [5 empty] | tripped ph B,Distance protection Zone1,Fault location=28.33Km,Ia=199.0A,Ib=902.7A,Ic=83.65A. Line patrolling was done & no fault was found.
|  | 2023-06-24 | 01:55 | 2023-06-24 | 02:00 | 0.0034722 | 0 | 5 | [5 empty] | 132kv SMC(incoming) feeder tripped from Lapanga end 41. power drawn from Rajgangpur end Via Kutra switching station.
|  | 2023-07-18 | 20:55 | 2023-07-18 | 21:35 | 0.027778 | 0 | 40 | [5 empty] | tripped ph C N, Distance protection Zone2, Fault location=48.99km, Ia=108A, Ib=322.8A, Ic=1.633kA. Tripped from SMC end. Power restored from smc
|  | 2023-12-14 | 19:18 | 2023-12-14 | 19:35 | 0.011806 | 0 | 17 | [5 empty] | R-N, Zone 1, Dist- 5.923 km, Ir- 1.128 kA, Iy- 0.098 kA, Ib- 0.212 kA. -
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
499 | 132kV Soro-Bhadrak |  |  |  |  | 1899-12-31 08:37 | 17 | 48 | [7 empty] | 45.62 | 8760 | 99.8% | 812.036 | 399631.2
|  | 2023-05-31 | 23:22 | 2023-06-01 | 13:16 | 0.57917 | 5 | 22 | [5 empty] | Tripped on Y-phase O/C & B- phase O/C, Zone-1, started phase BN, tripped phase ABC, fault duration= 63.34 ms, relay trip time=80.01ms, fault location= 2.346km, IA=430.1A, IB=7.042KA, IC=318.1A. After field verification it is found that the conductor has snapped in between loc. No. 5 &6 hence the feeder is declared as faulty. L/C taken & work is under process.
|  | 2023-06-19 | 00:30 | 2023-06-19 | 18:59 | 0.77014 | 0 | 12 | [5 empty] | Tripped on Y phase ,B phase O/C,Zone-I,Started phase- BCN,Tripped phase-ABC,Fault duration-73.26ms,Fault location-3.717KM,IA=308.5A,IB=6.082KA,IC=5.140KA. After field verification it is found that the conductor has snapped in between loc. No. 5 &6 hence the feeder is declared as faulty. L/C taken & work is under process.
|  | 2024-02-21 | 08:31 | 2024-02-21 | 08:45 | 0.0097222 | 0 | 14 | [5 empty] | At Bhadrak Grid end: O/C (R-Y-B), Ir- 0.64kA, Iy- 0.64kA, Ib- 0.64kA No tripping at Soro end. Source Failure from Balasore GSS end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
500 | 132kV Jayanagar-Sunabeda |  |  |  |  | 0.05 | 1 | 12 | [7 empty] | 40 | 8760 | 99.99% | 48 | 350400
|  | 2023-04-23 | 21:53 | 2023-04-23 | 22:55 | 0.043056 | 1 | 2 | [5 empty] | A-N , Z-1 , If=6.1KA, Dist=8.6KM.
|  | 2023-09-05 | 16:30 | 2023-09-05 | 16:40 | 0.0069444 | 0 | 10 | [5 empty] | Z-1,Y-G,Dist-26.42Km,If-3.39KA.
501 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.6 | 8760 | 100% | 0 | 110376
502 | 132kV Sunabeda-HAL |  |  |  |  | 0.05 | 1 | 12 | [7 empty] | 0.7 | 8760 | 99.99% | 0.84 | 6132
|  | 2023-04-23 | 21:53 | 2023-04-23 | 22:55 | 0.043056 | 1 | 2 | [5 empty] | A-N , Z-1 , If=6.1KA, Dist=8.6KM.
|  | 2023-09-05 | 16:30 | 2023-09-05 | 16:40 | 0.0069444 | 0 | 10 | [5 empty] | Z-1,Y-G,Dist-26.42Km,If-3.39KA.
503 | 132kV Sunabeda-Pottangi |  |  |  |  | 0.05 | 1 | 12 | [7 empty] | 33 | 8760 | 99.99% | 39.6 | 289080
|  | 2023-04-23 | 21:53 | 2023-04-23 | 22:55 | 0.043056 | 1 | 2 | [5 empty] | A-N , Z-1 , If=6.1KA, Dist=8.6KM.
|  | 2023-09-05 | 16:30 | 2023-09-05 | 16:40 | 0.0069444 | 0 | 10 | [5 empty] | Z-1,Y-G,Dist-26.42Km,If-3.39KA.
504 | 132kV Tarkera-Kalunga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.48 | 8760 | 100% | 0 | 135604.8
505 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
506 | 132kV Tarkera-Chhend-I |  |  |  |  | 0.075694 | 1 | 34 | [7 empty] | 6.165 | 8760 | 99.98% | 9.6585 | 54005.4
|  | 2023-11-06 | 09:52 | 2023-11-06 | 11:41 | 0.075694 | 1 | 34 | [5 empty] | Zone 3, Dist- 0.78 km, Iy- 5.178 kA. -
507 | 132kV Tarkera-Chhend-II |  |  |  |  | 0.0625 | 1 | 30 | [7 empty] | 6.165 | 8760 | 99.98% | 9.2475 | 54005.4
|  | 2023-11-06 | 09:52 | 2023-11-06 | 11:22 | 0.0625 | 1 | 30 | [5 empty] | Zone 3, Dist- 0.78 km, Iy- 5.185 kA. -
508 | 132kV Tarkera-Rajgangpur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.1 | 8760 | 100% | 0 | 211116
509 | 132kV Tarkera-Rajgangpur-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.1 | 8760 | 100% | 0 | 211116
510 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
511 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
512 | 132kV Tarkera-Rourkela-I |  |  |  |  | 1899-12-31 01:32 | 0 | 43 | [7 empty] | 3 | 8760 | 99.99% | 2.15 | 26280
|  | 2023-10-01 | 11:55 | 02.10.23 | 13:37 | 1899-12-31 01:32 | 0 | 23 | [5 empty] | At Rourkela end: Y-N, Zone 1, Dist- 62 km, Iy-4.471 kA At Tarkera end: B/U : Y-N, Iy- 7.6 kA. Y-ph conductor snapped between tower 3 & 4
|  | 2023-10-05 | 14:04 | 2023-10-05 | 15:36 | 01:32 | 0 | 20 | [5 empty] | At Rourkela end: Ir- 12.507 kA, Ib- 12.43 kA At Tarkera end: Ir- 14.78 kA. -
513 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
514 | 132kV Tarkera-Rourkela-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
515 | 132kV Jayapatna- Dabugaon |  |  |  |  | 0.76528 | 0 | 38 | [7 empty] | 65.59 | 8760 | 99.99% | 41.5403 | 574568.4
|  | 2023-04-22 | 22:33 | 23.04.2023 | 17:39 | 0.75417 | 0 | 22 | [5 empty] | DP Operated at Dabugaon end,no relay operated at Jaypatna end [Jumper snapped at Loc-40].
|  | 2023-12-28 | 12:32 | 2023-12-28 | 12:48 | 0.011111 | 0 | 16 | [5 empty] | 132kV Power Supply outage occurred at Jayapatna Grid due to Power Swing block.. -
516 | 132kV Dabugaon -Umerkote |  |  |  |  | 0.82292 | 14 | 1 | [7 empty] | 45.49 | 8760 | 99.84% | 637.6182 | 398492.4
|  | 2023-04-22 | 22:33 | 23.04.2023 | 17:39 | 0.75417 | 0 | 22 | [5 empty] | DP Operated at Dabugaon end,no relay operated at Jaypatna end [Jumper snapped at Loc-40].
|  | 2023-12-28 | 12:32 | 2023-12-28 | 12:48 | 0.011111 | 0 | 16 | [5 empty] | 132kV Power Supply outage occurred at Jayapatna Grid due to Power Swing block.. -
|  | 2023-04-23 | 16:18 | 2023-04-23 | 16:38 | 0.013889 | 0 | 20 | [5 empty] | Source end failure.
|  | 2023-06-26 | 14:20 | 2023-06-26 | 14:38 | 0.0125 | 0 | 18 | [5 empty] | Y-B fault.
|  | 2023-06-27 | 17:56 | 2023-06-27 | 18:41 | 0.03125 | 0 | 45 | [5 empty] | Y-B fault. Line patrolling was done and no fault found.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
517 | 132kV Tentulikhunti-Dabugaon |  |  |  |  | 0.072917 | 13 | 45 | [7 empty] | 42.8 | 8760 | 99.84% | 588.5 | 374928
|  | 2023-04-22 | 22:52 | 2023-04-22 | 23:14 | 0.015278 | 0 | 22 | [5 empty] | O/C & E/F,DP Operated at Tentulikhunti end,no relay operated at Dabugaon end.
|  | 2023-04-23 | 16:18 | 2023-04-23 | 16:38 | 0.013889 | 0 | 20 | [5 empty] | Source end failure.
|  | 2023-06-26 | 14:20 | 2023-06-26 | 14:38 | 0.0125 | 0 | 18 | [5 empty] | Y-B fault.
|  | 2023-06-27 | 17:56 | 2023-06-27 | 18:41 | 0.03125 | 0 | 45 | [5 empty] | Y-B fault. Line patrolling was done and no fault found.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
518 | 132kV Tentulikhunti-Vento Solar |  |  |  |  | 0.036111 | 0 | 37 | [7 empty] | 4.192 | 8760 | 99.99% | 2.5851 | 36721.92
|  | 2023-05-12 | 06:13 | 2023-05-12 | 07:05 | 0.036111 | 0 | 37 | [5 empty] | Supply Fail.
519 | 132kV Therubali-IMFA |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2 | 8760 | 100% | 0 | 17520
520 | 132kV Therubali-JK Pur |  |  |  |  | 0.089583 | 0 | 39 | [7 empty] | 9.68 | 8760 | 99.99% | 6.292 | 84796.8
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:23 | 0.089583 | 0 | 39 | [5 empty] | DP Relay, IR = 32A, IY = 17A, IB = 17A Indravati end-Broken conductor indication, IR = 288A, IY = 522A, IB = 443A.. System Failure at Therubali Grid
521 | 132kV Therubali-Rayagada |  |  |  |  | 0.33194 | 0 | 15 | [7 empty] | 19.6 | 8760 | 100% | 4.9 | 171696
|  | 2024-03-09 | 10:42 | 2024-03-09 | 18:40 | 7:58 | 0 | 15 | [5 empty] | At Therubali end: Y-N, , Iy- 2.22 kA At Rayagada end: Y-N, , Iy- 2.75kA. Tree fallen on Conductor
522 | 132kV Therubali-RTSS Bhalumaska |  |  |  |  | 0.089583 | 0 | 15 | [7 empty] | 31.1 | 8760 | 100% | 7.775 | 272436
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:23 | 0.089583 | 0 | 15 | [5 empty] | DP Relay, IR = 32A, IY = 17A, IB = 17A Indravati end-Broken conductor indication, IR = 288A, IY = 522A, IB = 443A.. System Failure at Therubali Grid
523 | 132kV TTPS-Angul |  |  |  |  | 0.028472 | 1 | 22 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 15.6 | 8760 | 99.99% | 21.32 | 136656
|  | 2023-05-18 | 15:05 | 2023-05-18 | 15:46 | 0.028472 | 1 | 22 | [5 empty] | Tripped on DP Relay,Fault loop-L2N,Fault current -4.042KA, Fault abs. distance-4.54KM
524 | 132kV TTPS-Chainpal-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 3 | 8760 | 100% | 0 | 26280
525 | 132kV TTPS-Chainpal-II |  |  |  |  | 0.17014 | 17 | 54 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 3 | 8760 | 99.8% | 53.7 | 26280
|  | 2023-05-29 | 12:16 | 2023-05-29 | 12:36 | 0.013889 | 0 | 40 | [5 empty] | Tripped at TTPS end on Distance Protection Relay with indication B-E, IB=1.4kA, Fault Distance 22.6Km. Heavy rain and severe lighting
|  | 2023-06-04 | 19:01 | 2023-06-04 | 20:38 | 0.067361 | 1 | 54 | [5 empty] | Tripped at TTPS end on Distance Protection Relay with indication Z3, Fault Distance 40Km, IA=0.227kA, IB=0.227kA, IC=2.18kA.
|  | 2023-06-11 | 06:45 | 2023-06-11 | 08:53 | 0.088889 | 3 | 20 | [5 empty] | Tripped at TTPS end only. DP Relay, Z3, Distance=41.26kM, IA=0.189kA, IB=1.94kA, IC=0.205kA. Relay setting at TTPS end is problematic.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
526 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
527 | 132kV TTPS- Gondia |  |  |  |  | 0 | 0 | 0 | [7 empty] | 85.383 | 8760 | 100% | 0 | 747955.08
528 | 132kV Gondia-Jabamayee FAlloys |  |  |  |  | 0 | 0 | 0 | [7 empty] | 39.178 | 8760 | 100% | 0 | 343199.28
529 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
530 | 132kV Tusura-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.8 | 8760 | 100% | 0 | 129648
(17): 8786.4891; (20): 88144.7981; (21): 154567758.732 | 0.00057027
ICTs / AUTOS
1 | New Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
2 | New Duburi 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
3 | Lapanga 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
4 | Lapanga 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
5 | Meramundali 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Mendhasal 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
8 | Mendhasal 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
9 | Mendhasal 315MVA ICT – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
10 | Aska New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
11 | Aska New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
12 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
13 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
14 | Balasore 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
15 | Balasore 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
16 | Balasore 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
17 | Bamra 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
18 | Bamra 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 2292 | 100% | 0 | 916800
19 | Bargarh New 160MVA Auto – I |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 2023-04-15 | 19:34 | 2023-04-15 | 19:44 | 0.0069444 | 0 | 10 | [5 empty] | Back up operation operated.
20 | Bargarh New 160MVA Auto – II |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 2023-04-15 | 19:34 | 2023-04-15 | 19:44 | 0.0069444 | 0 | 10 | [5 empty] | Back up operation operated.
21 | Bidanasi 100MVA Auto – I |  |  |  |  | 0.014583 | 0 | 21 | [6 empty] | 100 |  | 8760 | 100% | 87.5 | 2190000
|  | 2023-06-17 | 14:48 | 2023-06-17 | 15:09 | 0.014583 | 0 | 21 | [5 empty] | E/F with M/T relay operated. IL1-0,IL2-0.73KAmp,IL3- 0.54KAmp. B- PH SI to main bus jumper snapped
22 | Bidanasi 100MVA Auto - II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
23 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
24 | Bhadrak 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
25 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
26 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
27 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
28 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
29 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
30 | Budhipadar 160MVA Auto – I |  |  |  |  | 0.82847 | 0 | 38 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 2023-07-29 | 19:17 | 2023-07-29 | 19:30 | 0.0090278 | 0 | 13 | [5 empty] | 220kV Side:- B/U Relay, O/C, Bph 132kV Side:- O/C, E/F, BPH, IR=0.78kA, IY=0.7kA, IB=4.14kA. The sais feeder tripped at Lakhanpur end only. Weather: Heavy lightning 132kV Incoming supply fail weather-lightening and rain sulator puncture(which pha weather-lightening and rain Heavy rain & lightning and rain.
|  | 2024-03-09 | 14:07 | 2024-03-09 | 19:40 | 0.81944 | 0 | 25 | [5 empty] | Overfluxing.
31 | Budhipadar 160MVA Auto – II |  |  |  |  | 0.023611 | 0 | 27 | [6 empty] | 160 |  | 8760 | 99.99% | 180 | 3504000
|  | 2023-10-06 | 16:16 | 2023-10-06 | 16:50 | 0.023611 | 0 | 27 | [5 empty] | Tripped due to fault in 220kV Main Bus II. Tripping of 220kV Budhipadar- Bamra Feeder initiated Bus bar fault in 220kV Main Bus II leading to tripping of all feeders in Main Bus II. 33 kV side of TRF I & II was under S/D
32 | Chandaka 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
33 | Chandaka 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
34 | Chandaka 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
35 | Chandaka 160MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
36 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
37 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
38 | Cuttack 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
39 | Cuttack 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
40 | Dhamara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8196 | 100% | 0 | 3278400
41 | Dhamara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 3468 | 100% | 0 | 1387200
42 | Duburi 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
43 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
44 | Duburi 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
45 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
46 | Goda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
47 | Goda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
48 | Gunupur 160MVA Auto – I |  |  |  |  | 1899-12-31 00:07 | 2 | 55 | [6 empty] | 160 |  | 8760 | 99.97% | 1166.6667 | 3504000
|  | 2023-05-31 | 20:08 | 01.06.23 | 19:38 | 0.97917 | 2 | 18 | [5 empty] | At Therubali end:- BGT(Y-ph), Z-2, Location-60.83 km, Iy- 2.3 kA At Gunupur end:- Busbar relay (LBB)operated. All 3-phs Conductors snap from beam mounted isolators at Gunupur due to heavy wind and rain .Grid blackout. Gunupur availed supply from Akhusingh.
|  | 2024-03-20 | 05:35 | 2024-03-20 | 06:12 | 0.025694 | 0 | 37 | [5 empty] | Bus-bar trip(96). -
49 | Gunupur 160MVA Auto – II |  |  |  |  | 1899-12-31 00:33 | 2 | 55 | [6 empty] | 160 |  | 8760 | 99.97% | 1166.6667 | 3504000
|  | 2023-05-31 | 20:08 | 01.06.23 | 19:38 | 0.97917 | 2 | 18 | [5 empty] | At Therubali end:- BGT(Y-ph), Z-2, Location-60.83 km, Iy- 2.3 kA At Gunupur end:- Busbar relay (LBB)operated. All 3-phs Conductors snap from beam mounted isolators at Gunupur due to heavy wind and rain .Grid blackout. Gunupur availed supply from Akhusingh.
|  | 2024-03-20 | 05:35 | 2024-03-20 | 06:38 | 0.04375 | 0 | 37 | [5 empty] | Bus-bar trip(96). -
50 | Jayanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
51 | Jayanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
52 | Jayapatna 160MVA Auto – I |  |  |  |  | 0.15903 | 3 | 30 | [6 empty] | 160 |  | 8760 | 99.96% | 1400 | 3504000
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:21 | 0.15903 | 3 | 30 | [5 empty] | Tripped on Differential. Jumper Snapped at Loc No. 132,
53 | Jayapatna 160MVA Auto – II |  |  |  |  | 0.15903 | 3 | 30 | [6 empty] | 160 |  | 8760 | 99.96% | 1400 | 3504000
|  | 2023-12-28 | 12:32 | 2023-12-28 | 16:21 | 0.15903 | 3 | 30 | [5 empty] | Tripped on Differential. Jumper Snapped at Loc No. 132,
54 | Joda 160MVA Auto – I |  |  |  |  | 0.0076389 | 0 | 11 | [6 empty] | 160 |  | 8760 | 100% | 73.3333 | 3504000
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:16 | 0.0076389 | 0 | 11 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
55 | Joda 160MVA Auto – II |  |  |  |  | 0.0069444 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:15 | 0.0069444 | 0 | 10 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
56 | Joda 100MVA Auto – III |  |  |  |  | 0.019444 | 0 | 12 | [6 empty] | 100 |  | 8760 | 100% | 41.6667 | 2190000
|  | 2023-08-26 | 11:05 | 2023-08-26 | 11:33 | 0.019444 | 0 | 12 | [5 empty] | 132KV R-Ph jumper of 220/132KV 100MVA Auto-III on Bus-coupler snapped creating heavy fault & pulled out 132KV Side of Auto-I,Auto-II, Auto-III,132KV Barbil,132KV Palasponga,132KV Kenduposi, 132KV FAP,132KV Banspani RTSS & 33KV outgoing feeders was affected.. -
57 | Katapalli 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
58 | Katapalli 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
59 | Katapalli 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
60 | Kesinga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
61 | Kesinga 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
62 | Kuarnmunda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
63 | Lapanga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
64 | Lapanga 160MVA Auto – II |  |  |  |  | 0.047222 | 1 | 7 | [6 empty] | 160 |  | 8760 | 99.99% | 446.6667 | 3504000
|  | 2023-10-07 | 17:19 | 09.10.23 | 17:40 | 0.014583 | 0 | 20 | [5 empty] | HV side: O/C, E/F LV side: REF Protection. -
|  | 2024-01-15 | 00:36 | 2024-01-15 | 01:23 | 0.032639 | 0 | 47 | [5 empty] | Differential trip. Tripped as a reflection of RTSS fault (B phase insulator string of RTSS Rengali feeder damaged)
65 | Mendhasal 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
66 | Mendhasal 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
67 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
68 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
69 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
70 | Meramundali-B 500MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 500 |  | 8760 | 100% | 0 | 10950000
71 | Meramundali-B 500MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 500 |  | 8760 | 100% | 0 | 10950000
72 | Narendrapur 160MVA Auto – I |  |  |  |  | 0.021528 | 0 | 31 | [6 empty] | 160 |  | 8760 | 99.99% | 366.6667 | 3504000
|  | 2023-06-16 | 10:40 | 2023-06-16 | 11:11 | 0.021528 | 0 | 31 | [5 empty] | Tripped on Over Fluxing.. Over Fluxing
73 | Narendrapur 160MVA Auto – II |  |  |  |  | 0.038194 | 0 | 55 | [6 empty] | 160 |  | 8760 | 99.99% | 366.6667 | 3504000
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:26 | 0.015972 | 0 | 23 | [5 empty] | Auto TRF II: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 2.14 kA, Iy- 2.18 kA, Ib- 2.12 kA Auto TRF III: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 0.80 kA, Iy- 0.83 kA, Ib- 0.81 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
|  | 2023-06-16 | 10:40 | 2023-06-16 | 11:12 | 0.022222 | 0 | 32 | [5 empty] | Tripped on Over Fluxing.. Over Fluxing
74 | Narendrapur 100MVA Auto – III |  |  |  |  | 0.015972 | 0 | 23 | [6 empty] | 100 |  | 8760 | 100% | 95.8333 | 2190000
|  | 2023-10-16 | 16:03 | 2023-10-16 | 16:26 | 0.015972 | 0 | 23 | [5 empty] | Auto TRF II: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 2.14 kA, Iy- 2.18 kA, Ib- 2.12 kA Auto TRF III: 220kV side- O/C, E/F, M/R; 132kV side- M/R, Ir- 0.80 kA, Iy- 0.83 kA, Ib- 0.81 kA. Burst of Y Phase CT in 132 kV Bus Coupler Bay at Chhatrapur GSS
|  | 2023-06-16 | 10:40 | 2023-06-16 | 11:07 | 0.01875 | 0 | 27 | [5 empty] | Tripped on Over Fluxing.. Over Fluxing
75 | New Bolangir 160MVA Auto I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
76 | New Bolangir 160 MVA Auto II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
77 | New Bolangir 160 MVA Auto III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
78 | Paradeep 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
79 | Paradeep 160 MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
80 | Paradeep 160 MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
81 | Pratapsasan 160 MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
82 | Pratapsasan 160 MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
83 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
84 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
85 | Tarkera 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
86 | Tarkera 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
87 | Tarkera 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
88 | Tarkera 100MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
89 | Therubali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
90 | Therubali 100MVA Auto – II |  |  |  |  | 0.084028 | 0 | 39 | [6 empty] | 100 |  | 8760 | 99.99% | 162.5 | 2190000
|  | 2023-05-15 | 11:14 | 2023-05-15 | 13:15 | 2:01 | 0 | 39 | [5 empty] | Tripped without any indication.. System Failure at Therubali Grid
91 | Therubali 160MVA Auto –III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
15135
(16): Sub-total (ICTs / Autos); (20): 7154.1667; (21): 326526900 | 2.191e-05 | 99.9978
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 95298.9647 | 481094658.732
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00019809
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9802

## ANNEXURE-III
Transmission Element Data as on 31/03/17 ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
a) Transmission Lines
SL. NO | Name of the Transmission line |  | Voltage Level(in KV) | S/C or D/C | Line Length (in Ckt KM) | Conductor Type & Characteristics | No. of Sub-Conductor (NSC) | Date of Comm. / Comm. Operation
| From | To
1 | Rengali-Kuchei PG | Kolaghat PG | 400 | S/C | 483 | Twin Moose | 2 | 1995
2 | Indravati PH | Indravati PG | 400 | S/C | 7.4 | Twin Moose | 2 | 03/09/09
3 | Meramundal I | Mendhasal I | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
4 | Meramundal I | Mendhasal II | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
3 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
4 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
5 | Meramundali | JSPL I | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
6 | Meramundali | JSPL II | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
7 | Balimela | U. Seluru | 220 | S/C | 24.76 | Single Zebra | 1 | 1982
8 | Balimela | Jayanagar-I | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
9 | Balimela | Jayanagar-II | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
10 | Balimela | Jayanagar-III | 220 | S/C | 93.46 | Single Zebra | 1 | 1982
11 | Balasore | Bhadrak | 220 | S/C | 80 | Single Zebra | 1 | 22.10.08
12 | Barkote | Tarkera | 220 | D/C | 97.48 | Single Zebra | 1 | 1979
13 | Bhanjanagar | Meramundali-I | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
14 | Bhanjanagar | Meramundali-II | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
15 | Bhanjanagar | Mendhasal | 220 | D/C | 156 | Single Zebra | 1 | 1989
16 | Bhanjanagar | Nayagarh | 220 | D/C | 46.47 | Single Zebra | 1 | 1989
17 | Bidanasi | Mendhasal ckt II | 220 | D/C | 15 | Single Zebra | 1 | 2008
18 | Bidanasi | Mendhasal ckt III | 220 | D/C | 15 | Single Zebra | 1 | 2008
19 | Bisra | Tarkera-I | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
20 | Bisra | Tarkera-II | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
21 | Budhipadar | IbTPS -I | 220 | D/C | 26 | Single Zebra | 1 | 1995
22 | Budhipadar | IbTPS -II | 220 | D/C | 26 | Single Zebra | 1 | 1995
23 | Budhipadar | IbTPS -III | 220 | D/C | 25.38 | Single Zebra | 1 | 1995
24 | Budhipadar | IbTPS -IV | 220 | D/C | 25.38 | Single Zebra | 1 | 07/01/08
25 | Budhipadar | Raigarh | 220 | D/C | 60 | Single Zebra | 1 | 1995
26 | Budhipadar | Korba-II | 220 | D/C | 60 | Single Zebra | 1 | 1995
27 | Budhipadar | Katapalli -I | 220 | D/C | 61.679 | Single Zebra | 1 | 20/04/07
28 | Budhipadar | Katapalli -II | 220 | D/C | 61.769 | Single Zebra | 1 | 20/04/07
29 | Budhipadar | SPS I | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
30 | Budhipadar | SPS II | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
31 | Budhipadar | Bhusan Steel-I | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
32 | Budhipadar | Bhusan Steel-II | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
33 | Chandaka | Mendhasal ckt I | 220 | D/C | 19 | Single Zebra | 1 | 2008
34 | Chandaka | Mendhasal ckt II | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
35 | Chandaka | Mendhasal ckt III | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
36 | Chandaka | Mendhasal ckt IV | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
37 | Duburi | Duburi (New) ckt I | 220 | D/C | 11.056 | Single Zebra | 1 | 1996
38 | Duburi | Duburi (New) ckt II | 220 | D/C | 11.056 | Single Zebra | 1 | 1997
39 | Duburi | NINL | 220 | S/C | 6 | Single Zebra | 1 | 01/06/2000
40 | Duburi (New) | Balasore | 220 | D/C | 137.36 | Single Zebra | 1 | 1997
41 | Indravati PH | Therubali-I | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
42 | Indravati PH | Therubali-II | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
43 | Indravati PH | Therubali-III | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
44 | Indravati PH | Therubali-IV | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
45 | Jayanagar | Jeyapore PG-I | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
46 | Jayanagar | Jeyapore PG-II | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
47 | Jayanagar | Laxmipur ckt I | 220 | D/C | 65 | Single Zebra | 1 | 1974
48 | Jayanagar | Laxmipur Ckt II | 220 | D/C | 65 | Single Zebra | 1 | 1974
49 | Jindal | Jamsedpur DVC | 220 | S/C | 20.8 | Single Zebra | 1 | 1985
50 | Joda | RCPur PG | 220 | S/C | 15.5 | Single Zebra | 1 | 1985
51 | Joda | Jindal | 220 | S/C | 21 | Single Zebra | 1 | 1985
52 | Joda | TSIL Ckt. | 220 | S/C | 7.3 | Single Zebra | 1 | 23/03/07
53 | Katapali | Bolangir-I | 220 | D/C | 117.85 | Single Zebra | 1 | 2010
54 | Katapali | Bolangir-II | 220 | D/C | 117.85 | Single Zebra | 1 | 2011
55 | Kuchei PG | Balasore Ckt I | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
56 | Kuchei PG | Balasore Ckt II | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
57 | Laxmipur | Therubali Ckt I | 220 | D/C | 56 | Single Zebra | 1 | 1974
58 | Laxmipur | Therubali Ckt II | 220 | D/C | 56 | Single Zebra | 1 | 1974
59 | Laxmipur | Utkal Alu,ina Ckt I | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
60 | Laxmipur | Utkal Alu,ina Ckt II | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
61 | Mendhasal | Bidanasi-II | 220 | D/C | 32.99 | Single Zebra | 1 | 2003
62 | Meramundali | Bidanasi-II | 220 | D/C | 90.94 | Single Zebra | 1 | 2003
63 | Meramundali | Duburi-I | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
64 | Meramundali | Duburi-II | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
65 | Meramundali | BSSL (Bhusan) I | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
66 | Meramundali | BSSL (Bhusan) II | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
67 | NALCO | Meramundali-I | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
68 | NALCO | Meramundali-II | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
69 | NALCO | Rengali PH | 220 | S/C | 71.337 | Single Zebra | 1 | 1984
70 | Nayagarh | Mendhasal | 220 | D/C | 90 | Single Zebra | 1 | 1989
71 | Narendrapur | Mendhasal I | 220 | D/C | 75 | Single Zebra | 1 | 02/07/2010
72 | New Duburi | Paradeep Ckt-I | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
73 | New Duburi | Paradeep Ckt-II | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
74 | Rengali GD | Rengali PG -I | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
75 | Rengali GD | Rengali PG -II | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
76 | Rengali GD | Chandiposh (T) | 220 | D/C | 162.08 | Single Zebra | 1 | 26/03/2000
77 | Rengali GD | Barkote | 220 | D/C | 55 | Single Zebra | 1 | 1979
78 | Rengali PH | Rengali GD -I | 220 | D/C | 5 | Single Zebra | 1 | 1997
79 | Rengali PH | Rengali GD -II | 220 | D/C | 5 | Single Zebra | 1 | 1997
80 | Rengali PH | STPS | 220 | S/C | 29.5 | Single Zebra | 1 | 1984
81 | STPS (Kaniha) | TTPS | 220 | S/C | 34.5 | Single Zebra | 1 | 1984
82 | STPS | Meramundali-I | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
83 | STPS | Meramundali-II | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
84 | Tarkera | Budhipadar-I | 220 | D/C | 109 | Single Zebra | 1 | 1995
85 | Tarkera | Budhipadar-II | 220 | D/C | 109 | Single Zebra | 1 | 1995
86 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 2008
87 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 1995
88 | Therubali | Narendrapur-I | 220 | D/C | 196 | Single Zebra | 1 | 2013
89 | Therubali | Narendrapur-II | 220 | D/C | 196 | Single Zebra | 1 | 20/08/2001
90 | Therubali | Bhanjanagar-I | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
91 | Therubali | Bhanjanagar-II | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
92 | TTPS | Meramundali-I | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
93 | TTPS | Meramundali-II | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
94 | TTPS | Joda-I | 220 | D/C | 154 | Single Zebra | 1 | 1967
95 | TTPS | Joda-II | 220 | D/C | 154 | Single Zebra | 1 | 1970
96 | U. Kolab | Jayanagar-I | 220 | D/C | 6 | Single Zebra | 1 | 1987
97 | U. Kolab | Jayanagar-II | 220 | D/C | 6 | Single Zebra | 1 | 1987
98 | U. Kolab | Therubali | 220 | S/C | 128 | Single Zebra | 1 | 1984
Transmission Element Data as on 31/03/17 | [6 empty] | ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
b) Sub Stations
SL. NO | Name of the Sub-Station |  | Voltage Level(in KV) | NO. of ICTs/ AUTOs | MVA Capacity of ICTs / Autos | Date of Commissioning | Date of Comml. Operation
1 | MERAMUNDALI |  | 400/220/132 | 2 | 315 | 02/06/05
|  |  | 220/132 | 2 | 100 | 2002
|  |  |  | 1 | 100 | 2014 | 19.03.2014
2 | MENDHASAL |  | 400/220 | 2 | 315 | 2010
|  |  | 220/132 | 1 | 100 | 2006
|  |  | 220/132 | 1 | 100 | 2010
|  |  | 220/132 | 1 | 100 | 2014
3 | BIDANASI |  | 220/132 | 2 | 100 | 2004
|  |  |  | 1 | 100 | 2013 | 17.07.2013
5 | BHANJANAGAR |  | 220/132 | 2 | 160 | 1984,2014 | 05.01.2014
6 | BHADRAK |  | 220/132 | 2 | 100 | 2008,2009
7 | CHANDAKA |  | 220/132 | 2 | 160 | 2012
|  |  |  | 2 | 100 | 1989
8 | CUTTACK |  | 220/132 | 1 | 160 | 2017
9 | NARENDRAPUR |  | 220/132 | 2 | 160 | 1999
|  |  |  | 1 | 100 | 2012
10 | THERUBALI |  | 220/132 | 2 | 100 | 1981
11 | BALASORE |  | 220/132 | 2 | 160 | 2012
12 | JAYANAGAR |  | 220/132 | 2 | 100 | 1997
13 | DUBURI |  | 220/132 | 3 | 100 | 1989
14 | BUDHIPADAR |  | 220/132 | 2 | 160 | 1995
15 | TARKERA |  | 220/132 | 4 | 100 | 1981
16 | JODA |  | 220/132 | 2 | 100 | 1969
17 | KATAPALLI |  | 220/132 | 2 | 100 | 2007
18 | PARADEEP |  | 220/132 | 2 | 100,160,50 | 2009,2011,2009
19 | BOLANGIR NEW |  | 220/132 | 3 | 100 | 2011,2014 | 05.05.2014
20 | LAPANGA |  | 220/132 | 2 | 160 | 2014
21 | ATRI |  | 220/132 | 2 | 160 | 2016
22 | SAMANGARA |  | 220/132 | 2 | 160 | 2015,2016

## Lines not owned by OPTCL
PERIOD : 2019-20
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
44 | 220kV Budhipadar-Korba-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
34 | 220kV Budhipadar-Vedant Ckt.-I |  |  |  |  | 0.052083 | 0 | 39 | [7 empty] | 16.67 | 8760 | 99.99% | 10.8355 | 146029.2
|  | 30.06.19 | 1:06 | 30.06.19 | 1:22 | 0:16 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 2020-04-27 | 2:48 | 2020-04-27 | 4:40 | 0:23 | 0 | 23 | [5 empty] | At Budhipadar-D/P-I I) Dist Gen Trip, II) Relay Trip L1, III)Relay Trip L2 IV) Relay Trip L3, V) Zone-I, FL = AG, Ia=16.12 KA D/P-II(SIEMENS SIPROTEC 7SA52)-I) Dist Gen Trip II) Relay Trip L1, III)Relay Trip L2, IV) Relay Trip L3 V) Zone-I,FL = AG, Ia=16.21 KA
34 | 220kV Budhipadar-Vedant Ckt.-II |  |  |  |  | 0.052083 | 0 | 39 | [7 empty] | 16.67 | 8760 | 99.99% | 10.8355 | 146029.2
|  | 30.06.19 | 1:05 | 30.06.19 | 1:42 | 0:37 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
345 | 132 kV Palasponga - Essar |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 19.093 | 8760 | 100% | 2.5457 | 167254.68
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 22.12.19 | 0:25 | 22.12.19 | 0:35 | 0.0069444 | 0 | 10 | [5 empty] | At Polasponga end-Tripped on; O/C & E/F, Ia=0.48KA, Ib=0.54KA, Ic=0.53KA
|  | 26.12.19 | 2:58 | 26.12.19 | 3:06 | 0.0055556 | 0 | 8 | [5 empty] | At Polasponga end-Tripped on;O/C & E/F, Ia=0.16KA, Ib=0.24KA, Ic=0.33KA
|  | 22.10.19 | 15:07 | 22.10.19 | 15:11 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on Over current & Earth Fault at Polasponga end
|  | 06.10.19 | 15:25 | 06.10.19 | 16:00 | 0.024306 | 0 | 35 | [5 empty] | Tripped on E/F at Palasponga end.
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.
|  | 29.04.19 | 21:33 | 29.04.19 | 21:38 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 405A, Ib= 340A, Ic= 242.8A, In= 0.1A, Ig= 4.66A
|  | 28.04.19 | 15:06 | 28.04.19 | 15:09 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia= 423.4A, Ib= 355.9A, Ic= 309.8A, In= 0.09A, Ig= 2.4A
|  | 25.04.19 | 7:58 | 25.04.19 | 8:06 | 0.0055556 | 0 | 8 | [5 empty] | O/C,E/F (Y PH), Ia= 221.5A, Ib= 654.1A, Ic=161.2A, In= 0.1A, Ig= 686.26A
|  | 25.04.19 | 23:41 | 25.04.19 | 23:46 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 421A, Ib= 361A, Ic=277.7A, In= 0.03A, Ig= 3.12A
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 16.04.19 | 1:17 | 16.04.19 | 1:21 | 0.0027778 | 0 | 4 | [5 empty] | O/C(R,PH),IA=415.3,IB=381.2,IC=353 IN=0.05,IG2.56
|  | 15.04.19 | 1:18 | 15.04.19 | 1:20 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia= 396.4A, Ib=376.6KA, Ic=388.0KA IN=0.05
|  | 14.04.19 | 0:09 | 14.04.19 | 0:11 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia=416, Ib=338.5KA, Ic=347.5KA,IN=0.05,IG=5.95
|  | 14.04.19 | 4:03 | 14.04.19 | 4:06 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA , IN=0.0A, IG=1.1
|  | 13.04.19 | 5:25 | 13.04.19 | 5:34 | 0.00625 | 0 | 9 | [5 empty] | O/C (B PH), Ia=1532A, Ib= 1037A, Ic=366.2, In= 0.00A, Ig= 4.9A
|  | 12.04.19 | 16:38 | 12.04.19 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | E/F WITH DP Z, Ia=80.81A, Ib=1.019KA, Ic=55.05, In=1.052KA, Ig= 1.05KA
|  | 07.04.19 | 16:01 | 07.04.19 | 16:03 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia=396.4A, Ib= 376.04A, Ic=388.84A Ig=51.8A
|  | 02.04.19 | 0.275 | 02.04.19 | 6:39 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia=414.1A, Ib= 341.7A, Ic=285.9A, In= 0.09A, Ig= 5.73A
|  | 02.04.19 | 3:02 | 02.04.19 | 3:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C (B PH), Ia= 435.38A, Ib= 355.4A, Ic=333.3A, In= 0.0A, Ig= 3.94A
|  | 01.04.19 | 20:53 | 01.04.19 | 20:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia= 421.5A, Ib= 364.0A, Ic= 388.0A, In= 0.05A, Ig= 5.56A
345 | 132 kV Palasponga - MSP | [14 empty] | 7.5 | 8760 | 100% | 0 | 65700
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 29.10.19 | 14:05 | 29.10.19 | 14:11 | 0.0041667 | 0 | 6 | [5 empty] | At Palasponga-Tripped
|  | 28.10.19 | 10:17 | 28.10.19 | 10:27 | 0.0069444 | 0 | 10 | [5 empty] | Tripped From Karanjia Grid s/s
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.