## P-3 Berhampur
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Berhampur Circle | category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33KV Grid S/s Berhampur
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 0:14 | 4 | 1:05 |  |  |  | 0.054861
(ii) | 20 MVA Transformer-2 | POWER | 3 | 34:04 | 1 | 0:14 | 3 | 0:37 |  |  |  | 1899-12-31 10:55
(iii) | 40 MVA Transformer-3 | POWER | 1 | 0:21 | 1 | 0:14 | 4 | 5:06 | 33KV CT failed,Replaced by new one |  |  | 0.23681
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
(i) | 132kV Narendrapur-Berhampur Ckt-1 | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 0:08 | [5 empty] | 0.0055556
(ii) | 132kV Narendrapur-Berhampur Ckt-2 | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 0:44 | [5 empty] | 0.030556
(iii) | 132 KV Berhampur-Digaphandi S/C line | FEEDER | 3 | 0:27 | 0 | 0:00 | 2 | 0:47 | Tripping due to Lightning(Auto Recloser scheme implimated) |  |  |  |  | 0.051389
132/33KV Grid S/s Dighapahandi
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 4 | 0:48 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.033333
(ii) | 20 MVA Transformer-2 | POWER | 3 | 0:45 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.03125
(iii) | 12.5 MVA Transformer-3 | POWER | 3 | 0:45 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.03125
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
(i) | 132KV Mohana - Digaphandi SC line | FEEDER | 6 | 2:00 | 0 | 0:00 | 4 | 0:59 | [5 empty] | 0.12431
(ii) | 132KV Digapahandi - Chikiti Circuit-1 | FEEDER | 2 | 0:19 | 0 | 0:00 | 1 | 1:05 | [5 empty] | 0.058333
(iii) | 132KV Digapahandi - Chikiti Circuit-2 | FEEDER | 2 | 0:19 | 0 | 0:00 | 1 | 1:05 | [5 empty] | 0.058333
132/33KV Grid S/s Mohana
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 1 | 696:22 | 3 | 0:31 | 1 | 1051:17 | B Phase Bushing replaced & filtration of transformer oil done. |  |  | 1900-03-12 20:10
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 1:05 | 2 | 24:06 | [5 empty] | 1899-12-31 01:11
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
(i) | 132KV Mohana- Akhusing line | FEEDER | 4 | 82:27 | 1 | 0:28 | 9 | 229:09 | [5 empty] | 1900-01-12 00:04
132/33KV Grid S/s Chikiti
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
132/33KV Grid S/s Hinjili
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 14:18 | 0 | 0:00 |  |  |  | 0.59583
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
(i) | 132KV Hinili - Aska New | FEEDER | 1 | 0:53 | 0 | 0:00 | 1 | 12:58 | [5 empty] | 0.57708
(ii) | 132KV Hinili - Berhampur | FEEDER | 0 | 0:00 | 1 | 0:12 | 3 | 45:26 | [5 empty] | 1899-12-31 21:38
220/132/33kV GRID S/s Narendrapur
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 5 | 21:32 | 1 | 896:27 | 0 | 0:00 |  |  | 1900-02-06 05:59
(ii) | 160MVA Auto 2 | AUTO | 3 | 1:50 | 0 | 0:00 | 2 | 1:57 |  |  | 0.15764
(iii) | 100MVA Auto 3 | AUTO | 5 | 17:15 | 0 | 0:00 | 4 | 4:08 |  |  | 0.89097
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 4 | 9:07 | 0 | 0:00 | 4 | 13:29 |  |  |  | 0.94167
(ii) | 40 MVA Transformer-2 | POWER | 1 | 0:26 | 0 | 0:00 | 3 | 1:35 |  |  |  | 0.084028
(iii) | 40 MVA Transformer-3 | POWER | 3 | 24:19 | 1 | 6:07 | 8 | 12:13 |  |  |  | 1899-12-31 18:39
(iii) | 40 MVA Transformer-4 | POWER | 2 | 2:04 | 0 | 0:00 | 3 | 0:57 |  |  |  | 0.12569
3 | Bus Fault
(i) | BUS-I | BUS | 1 | 0:24 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0.016667
(ii) | BUS-II | BUS | 0 | 0:00 | 0 | 0:00 | 2 | 1:48 |  |  |  |  | 0.075
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Narendrapur-Gunupur | FEEDER | 6 | 6:18 | 3 | 1:16 | 5 | 3:19 | [5 empty] | 0.45347
(ii) | 220kV Narendrapur-Atri Ckt-1 | FEEDER | 12 | 5:33 | 4 | 40:05 | 8 | 2:43 | [5 empty] | 1900-01-01 00:21
(iii) | 220kV Narendrapur-Atri Ckt-2 | FEEDER | 16 | 8:39 | 2 | 0:00 | 13 | 74:12 | [5 empty] | 1900-01-02 10:51
(iv) | 220kV Narendrapur-Tata Ckt-1 | FEEDER | [11 empty] | 0
(v) | 220kV Narendrapur-Tata Ckt-2 | FEEDER | 3 | 1:06 | 1 | 65:08 | 3 | 0:50 | [5 empty] | 1900-01-01 19:04
(vi) | 132 kV Narendrapur-Chatrapur Ckt 1 | FEEDER | 4 | 5:52 | 2 | 0:34 | 0 | 0:00 | [5 empty] | 0.26806
(vii) | 132 kV Narendrapur-Chatrapur Ckt 2 | FEEDER | 2 | 2:49 | 2 | 0:00 | 0 | 0:00 | [5 empty] | 0.11736
(viii) | 132 kv Railway Traction Feeder | FEEDER | 3 | 0:04 | 2 | 0:15 | 4 | 0:29 | [5 empty] | 0.033333
132/33KV Grid S/s Aska
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 3 | 0:32 | 0 | 0:00 | 4 | 0:46 |  |  |  | 0.054167
(ii) | 40 MVA Transformer-2 | POWER | 3 | 0:35 | 0 | 0:00 | 2 | 15:47 |  |  |  | 0.68194
(iii) | 40 MVA Transformer-3 | POWER | 3 | 0:43 | 0 | 0:00 | 2 | 6:30 |  |  |  | 0.30069
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132kV Aska-Purusottampur | FEEDER | 3 | 1:00 | 0 | 0:00 | 4 | 10:16 | [5 empty] | 0.46944
(ii) | 132kV Aska-Aska New 1 | FEEDER | 1 | 1:06 | 0 | 0:00 | 1 | 3:13 | [5 empty] | 0.17986
(iii) | 132kV Aska-Aska New 2 | FEEDER | 1 | 1:06 | 1 | 4:47 | 0 | 0:00 | [5 empty] | 0.24514
220/132/33kV GRID S/s Bhanjanagar
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA Auto 2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 1 | 7:58 | 1 | 18:37 | 3 | 1:16 |  |  |  | 1899-12-31 03:51
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 2 | 27:57 | 3 | 5:31 |  |  |  | 1899-12-31 09:28
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 1 | 1:10 | 3 | 0:00 |  |  |  | 0.048611
3 | Bus Fault | BUS | [10 empty] | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220 kv Bhanjanagar-Narasinghpur | FEEDER | 3 | 4:44 | 0 | 0:00 | 3 | 5:07 | [5 empty] | 0.41042
(ii) | 220 kv Bhanjanagar-Meramundali | FEEDER | 3 | 3:53 | 2 | 5:33 | 4 | 15:20 | [5 empty] | 1899-12-31 00:46
(iii) | 220 kv Bhanjanagar-Nayagarh | FEEDER | 3 | 0:35 | 1 | 3:02 | 2 | 8:47 | [5 empty] | 0.51667
(iv) | 220 kv Bhanjanagar-Mendhasala | FEEDER | 5 | 99:47 | 1 | 2:49 | 3 | 7:22 | [5 empty] | 1900-01-03 13:58
(v) | 132 kv Bhanjanagar-Aska-1 | FEEDER | 1 | 0:55 | 0 | 0:00 | 1 | 0:38 | [5 empty] | 0.064583
(vi) | 132 kv Bhanjanagar-Aska-2 | FEEDER | 1 | 0:18 | 0 | 0:00 | 2 | 19:29 | [5 empty] | 0.82431
(vii) | 132 kv Bhanjanagar-G.Udaygiri | FEEDER | 4 | 22:01 | 1 | 8:59 | 1 | 5:55 | [5 empty] | 1899-12-31 12:55
220/132/33kV GRID S/s Aska New
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 1 | 0:47 | 0 | 0:00 | 0 | 0:00 |  |  | 0.032639
(ii) | 160MVA Auto 2 | AUTO | 1 | 1:02 | 0 | 0:00 | 0 | 0:00 |  |  | 0.043056
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 3 | 21:51 | 0 | 0:00 | 2 | 1:34 |  |  |  | 0.97569
(ii) | 20 MVA Transformer-2 | POWER | 3 | 1:05 | 0 | 0:00 | 1 | 0:34 |  |  |  | 0.06875
3 | Bus Fault | BUS | 0 | 0:00 | 1 | 0:29 | 0 | 0:00 |  |  |  |  | 0.020139
4 | EHT Feeder Fault | FEEDER
(i) | 220 kv Bhanjanagar-Aska New-1 | FEEDER | 1 | 1:01 | 1 | 0:29 | 1 | 1:01 | [5 empty] | 0.10486
(ii) | 220 kv Bhanjanagar-Aska New-2 | FEEDER | 0 | 0:00 | 1 | 25:39 | 0 | 0:00 | [5 empty] | 1899-12-31 01:39
(iii) | 220 kv Narendrapur-Aska New | FEEDER |  |  | 0 | 0:00 | 5 | 0:13 | [5 empty] | 0.0090278
(iv) | 220 kv Therubali-Aska New | FEEDER |  |  | 0 | 0:00 | 5 | 5:55 | [5 empty] | 0.24653
132/33KV Grid S/s Phulbani
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 3 | 12:40 | 1 | 0:40 |  |  |  | 0.55556
(ii) | 12.5 MVA Transformer - 2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 4:22 |  |  |  | 0.18194
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 kv Phulbani-G.Udaygiri | FEEDER | 5 | 22:46 | 2 | 0:54 | 5 | 22:46 | [5 empty] | 1899-12-31 22:26
132/33KV Grid S/s G. Udaygiri
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 1 | 1:30 | 1 | 0:58 | 0 | 0:00 |  |  |  | 0.10278
(ii) | 20 MVA Transformer - 2 | POWER | 1 | 1:30 | 1 | 1:14 | 1 | 1:08 |  |  |  | 0.16111
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
132/33KV Grid S/s Balugaon
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 3 | 0:13 | 1 | 0:25 | 1 | 0:13 |  |  |  | 0.035417
(ii) | 20 MVA Transformer-2 | POWER | 4 | 0:36 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.025
(iii) | 12.5 MVA Transformer-3 | POWER | 3 | 0:16 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.011111
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Solari Traction line | FEEDER | 2 | 0:18 | 1 | 0:06 | 1 | 0:20 | [5 empty] | 0.030556
132/33KV Grid S/s Chatrapur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 4 | 0:50 | 4 | 0:50 | 2 | 0:21 |  |  |  | 0.084028
(ii) | 20 MVA Transformer-2 | POWER | 4 | 0:50 | 4 | 0:51 | 2 | 0:21 |  |  |  | 0.084722
(iii) | 20 MVA Transformer-3 | POWER | 4 | 15:45 | 4 | 0:51 | 2 | 0:21 |  |  |  | 0.70625
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Chatrapur- IRE-1 | FEEDER | 1 | 0:13 | 1 | 0:25 | 0 | 0:00 | [5 empty] | 0.026389
(ii) | 132 KV Chatrapur- IRE-2 | FEEDER | 2 | 0:41 | 1 | 0:25 | 1 | 6:04 | [5 empty] | 0.29861
(iii) | 132 KV Chatrapur- Ganjam | FEEDER | 1 | 0:10 | 1 | 1:06 | 0 | 0:00 | [5 empty] | 0.052778
(iv) | 132 KV Chatrapur- Rambha traction | FEEDER | 6 | 18:02 | 1 | 0:23 | 1 | 0:36 | [5 empty] | 0.79236
(v) | 132 KV Chatrapur-Balugaon | FEEDER | 10 | 2:28 | 1 | 0:30 | 2 | 9:31 | [5 empty] | 0.52014
132/33KV Grid S/s Ganjam
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 1 | 0:09 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.00625
(ii) | 12.5 MVA Transformer-2 | POWER | 5 | 1:45 | 2 | 1:18 | 0 | 0:00 |  |  |  | 0.12708
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV GIL FEEDER | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Purusottampur
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:18 |  |  |  | 0.0125
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:17 |  |  |  | 0.011806
(iii) | 20 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:15 |  |  |  | 0.010417
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Chatrapur- Purusottampur | FEEDER | 1 | 0:39 | 1 | 0:24 | 0 | 0:00 | [5 empty] | 0.04375
|  |  |  | 1900-02-16 15:33 |  | 1900-02-16 21:00 |  | 1900-03-07 22:53
| Total |  |  |  | 1900-06-13 11:26 |  |  |  |  | 0 | 1900-02-07 08:58 | 1900-03-26 01:22 | 0.11181 | 1900-02-07 22:25 | 1900-06-13 11:26
[10 empty] | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Power Trf = SUM(M5:[Power Trf, row above])
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = SUM(N5:[Bus Fault, row above])
EHT Feeder Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
EHT Feeder Fault = SUM(O5:[EHT Feeder Fault, row above])
Auto Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = SUM(L5:[Auto Trf, row above])
Duration of Trippings (Hr:Mn) = SUM(E5:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G5:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I5:[FORM P-3, row above])
ICT = SUM(K5:[ICT, row above])

## P-3 Bhubaneswar
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Bhubaneswar Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33KV Grid S/s Arugul
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 1 | 0:44 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.030556
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Atri-Argul Circuit-I | FEEDER | 4 | 2:12 | 0 | 0:00 | 2 | 3:10 | [5 empty] | 0.22361
(ii) | 132 kV Atri-Argul Circuit-II | FEEDER | 2 | 0:52 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.036111
220/132/33kV GRID S/s Atri
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA Auto 2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:49 |  |  |  | 0.034028
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 kV Atri-Mendhasal Circuit-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 22:22 | [5 empty] | 0.93194
(ii) | 220 kV Atri-Pandiabil Circuit-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 0:25 | [5 empty] | 0.017361
(iii) | 220 kV Atri-Pandiabil Circuit-II | FEEDER | 1 | 0:21 | 0 | 0:00 | 1 | 0:25 | [5 empty] | 0.031944
132/33KV Grid S/s Banki
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Atri-Banki | FEEDER | 1 | 1:08 | 0 | 0:00 | 2 | 1:01 | [5 empty] | 0.089583
(ii) | 132 kV Banki-Nuapatna | FEEDER | 8 | 8:00 | 3 | 0:32 | 1 | 4:21 | [5 empty] | 0.53681
132/33KV Grid S/s Chandpur
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 4 | 3:39 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.15208
(ii) | 12.5 MVA Transformer-2 | POWER | 2 | 0:44 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.030556
(iii) | 20 MVA Transformer-3 | POWER | 2 | 0:58 | 1 | 1:00 | 1 | 1:32 |  |  |  | 0.14583
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Atri-Chandpur | FEEDER | 2 | 5:21 | 0 | 0:00 | 5 | 5:06 | [5 empty] | 0.43542
(ii) | 132 KV Chandpur-Balugaon | FEEDER | 2 | 2:36 | 2 | 9:46 | 2 | 2:06 | [5 empty] | 0.60278
132/33KV Grid S/s Khurda
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 1 | 0:39 | 1 | 12:32 | 0 | 0:00 | Declared Faulty |  |  | 0.54931
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:35 | 1 | 1:10 |  |  |  | 0.072917
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 1 | 1:10 | 1 | 0:40 |  |  |  | 0.076389
(iv) | 40 MVA Transformer-4 | POWER | 0 | 0:00 | 1 | 0:19 | 3 | 1:45 |  |  |  | 0.086111
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Khurda- Atri Ckt-I | FEEDER | 1 | 0:44 | 1 | 0:20 | 0 | 0:00 | [5 empty] | 0.044444
(ii) | 132KV Khurda- Atri Ckt-II | FEEDER | 1 | 0:44 | 1 | 0:20 | 0 | 0:00 | [5 empty] | 0.044444
(iii) | 132KV Khurda- Kaipadar TSS Line | FEEDER | 3 | 1:20 | 1 | 0:20 | 0 | 0:00 | [5 empty] | 0.069444
400/220/132 KV Grid S/s Mendhasal
1 | ICT | ICT
(i) | 315 MVA ICT-1 | ICT | 0 | 0:00 | 0 | 0:00 | 1 | 0:29 |  | 0.020139
(ii) | 315 MVA ICT-2 | ICT | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0
(iii) | 315 MVA ICT-3 | ICT | 0 | 0:00 | 0 | 0:00 | 1 | 1:44 |  | 0.072222
2 | Auto Transformer | AUTO
(i) | 100MVA Auto 1 | AUTO | 8 | 17:28 | 1 | 2:00 | 3 | 8:35 |  |  | 1899-12-31 04:03
(i) | 100MVA Auto 2 | AUTO | 1 | 2:28 | 0 | 0:00 | 0 | 0:00 |  |  | 0.10278
3 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 1 | 1:06 | 0 | 0:00 | 1 | 24:00 |  |  |  | 1899-12-31 01:06
(ii) | 20 MVA Transformer-1I | POWER | 2 | 3:46 | 0 | 0:00 | 1 | 1:25 |  |  |  | 0.21597
4 | Bus Fault | BUS
(i) | 400 kV Bus-1 | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 400 kV Bus-2 | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(iii) | 220 kV Bus-1 | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(iv) | 220 kV Bus-2 | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(v) | 132 kV Bus | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
5 | EHT Feeder Fault | FEEDER
(i) | 400KV Mendhasal- Meramundali Ckt-I | FEEDER | 4 | 5:02 | 1 | 0:34 | 1 | 1:08 | [5 empty] | 0.28056
(ii) | 400KV Mendhasal- Meramundali Ckt-II | FEEDER | 4 | 20:31 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.85486
(iii) | 132KV Mendhasal- Khurda | FEEDER | 2 | 43:23 | 0 | 0:00 | 1 | 10:04 | [5 empty] | 1900-01-01 05:27
220/33KV Grid S/s Nayagarh
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 5 | 5:37 | 1 | 0:07 | 4 | 54:17 |  |  |  | 1900-01-01 12:01
(ii) | 20 MVA Transformer-2 | POWER | 5 | 3:11 | 0 | 0:00 | 4 | 3:29 |  |  |  | 0.27778
(iii) | 40 MVA Transformer-3 | POWER | 6 | 3:53 | 4 | 7:42 | 4 | 2:52 |  |  |  | 0.60208
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 kV Nayagarh-Mendhasal | FEEDER | 3 | 1:10 | 0 | 0:00 | 1 | 0:23 | [5 empty] | 0.064583
132/33KV Grid S/s Nimapara
1 | Power Transformer | POWER | [9 empty] | 0
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS | 0 | 0:00 | 1 | 4:13 | 0 | 0:00 |  |  |  |  | 0.17569
3 | EHT Feeder Fault | FEEDER
132/33KV Grid S/s Puri
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 1 | 0:58 | 1 | 1:21 | 0 | 0:00 |  |  |  | 0.096528
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 1 | 74:40 | 0 | 0:00 |  |  |  | 1900-01-02 02:40
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Shamuka-Puri | FEEDER | 3 | 1:20 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.055556
(ii) | 132KV Nimapara-Puri | FEEDER | 1 | 21:38 | 0 | 0:00 | 1 | 21:51 | [5 empty] | 1899-12-31 19:29
(iii) | 132KV Samangara-Puri | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Satasankha
1 | Power Transformer | POWER | [9 empty] | 0
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:00 | 2 | 0:17 |  |  |  | 0.011806
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
220/132/33kV GRID S/s Samangara
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA Auto 2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:36 |  |  |  | 0.025
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:02 | 2 | 3:30 |  |  |  | 0.14722
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 KV Pandiabil- Samngara Fdr - I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(ii) | 221 KV Pandiabil- Samngara Fdr - II | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 13:33 | [5 empty] | 0.56458
(iii) | 132 KV Samangara- Nimapada Fdr | FEEDER | 4 | 1:51 | 1 | 1:11 | 2 | 9:13 | [5 empty] | 0.51042
(iv) | 132 KV Samangara-Satasankha Fdr -I | FEEDER | 0 | 0:00 | 1 | 0:35 | 0 | 0:00 | [5 empty] | 0.024306
(v) | 133 KV Samangara-Satasankha Fdr -II | FEEDER | 1 | 0:07 | 1 | 2:14 | 0 | 0:00 | [5 empty] | 0.097917
(vi) | 132 KV Samangara- RTSS Maltipatpur Fdr | FEEDER | 0 | 0:00 | 2 | 9:36 | 0 | 0:00 | [5 empty] | 0.4
132/33KV Grid S/s Shamuka
1 | Power Transformer | POWER
(i) | 31.5 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 31.5 MVA Transformer-2 | POWER | 0 | 0:00 |  |  |  |  | (A)-31.5 MVA TRF- II- Failed on dtd-10.12.23 (B)New 40 MVA TRF Commissioned on dtd -22.05.24 |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Atri-Shamuka | FEEDER | 2 | 12:48 | 0 | 0:00 | 1 | 8:07 | [5 empty] | 0.87153
132/33KV Grid S/s Konark
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 2 | 0:19 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.013194
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
3 | 132 kV Nimapara-Konark | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Bhubaneswar
1 | Power Transformer | POWER
(i) | 63 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 4 | 6:45 |  |  |  | 0.28125
(ii) | 63 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 14:11 |  |  |  | 0.59097
(iii) | 63 MVA Transformer-3 | POWER | 0 | 0:00 | 1 | 0:25 | 3 | 6:27 |  |  |  | 0.28611
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Chandaka- Bhubaneswar Fdr -1 | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 1:20 | [5 empty] | 0.055556
(ii) | 132KV Chandaka- Bhubaneswar Fdr -2 | FEEDER | 1 | 3:25 | 1 | 2:33 | 0 | 0:00 | [5 empty] | 0.24861
132/33KV Grid S/s Ranasinghpur
1 | Power Transformer | POWER
(i) | 63 MVA Transformer-1 | POWER | 4 | 9:23 | 2 | 0:28 | 0 | 0:00 |  |  |  | 0.41042
(ii) | 63 MVA Transformer-2 | POWER | 3 | 1:20 | 2 | 0:28 | 0 | 0:00 |  |  |  | 0.075
(iii) | 63 MVA Transformer-3 | POWER | 4 | 9:17 | 2 | 0:30 | 1 | 0:54 |  |  |  | 0.44514
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Chandaka-Ransinghpur fdr | FEEDER | 3 | 9:22 | 0 | 0:00 | 3 | 3:29 | [5 empty] | 0.53542
132/33KV Grid S/s Kesura
1 | Power Transformer | POWER
(i) | 63 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 0:28 | 3 | 1:10 |  |  |  | 0.068056
(ii) | 63 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 1:41 | 5 | 12:48 |  |  |  | 0.60347
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Kesura-Pratapsasan | FEEDER | 2 | 9:26 | 1 | 2:09 | 4 | 1:03 | [5 empty] | 0.52639
(ii) | 132 KV Kesura-Ranasinghpur | FEEDER | 5 | 6:57 | 0 | 0:00 | 3 | 1:27 | [5 empty] | 0.35
220/132/33kV GRID S/s Chandaka
1 | Auto Transformer | AUTO
(i) | 100MVA Auto 1 | AUTO | 1 | 1:45 | 0 | 0:00 | 1 | 0:55 |  |  | 0.11111
(ii) | 160MVA Auto 2 | AUTO | 2 | 7:29 | 1 | 0:19 | 0 | 0:00 |  |  | 0.325
(iii) | 100MVA Auto 3 | AUTO | 0 | 0:00 | 0 | 0:00 | 3 | 10:01 |  |  | 0.41736
(iv) | 160MVA Auto 4 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 63 MVA Transformer-1 | POWER | 3 | 9:01 | 0 | 0:00 | 1 | 5:00 |  |  |  | 0.58403
(ii) | 63 MVA Transformer-2 | POWER | 1 | 0:19 | 1 | 0:05 | 1 | 0:14 |  |  |  | 0.026389
(iii) | 63 MVA Transformer-3 | POWER | 1 | 2:25 | 1 | 0:11 | 3 | 1:31 |  |  |  | 0.17153
3 | Bus Fault | BUS | [10 empty] | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Mendhasal-Chandaka Ckt-1 | FEEDER | 2 | 0:57 | 2 | 0:44 | 3 | 1:51 | [5 empty] | 0.14722
(ii) | 220kV Mendhasal-Chandaka Ckt-2 | FEEDER | 1 | 2:11 | 2 | 1:12 | 0 | 0:00 | [5 empty] | 0.14097
(iii) | 220kV Mendhasal-Chandaka Ckt-3 | FEEDER | 4 | 8:14 | 2 | 3:14 | 2 | 0:40 | [5 empty] | 0.50556
(iv) | 220kV Chandaka (B)-Chandaka | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(v) | 132kV Chandaka- Nimapara | FEEDER | 5 | 18:13 | 1 | 2:16 | 6 | 4:38 | [5 empty] | 1899-12-31 01:07
(vi) | 132kV Chandaka- Mendhasal | FEEDER | 2 | 5:57 | 1 | 0:01 | 0 | 0:00 | [5 empty] | 0.24861
(vii) | 132kV Chandaka- BPPL | FEEDER | 4 | 3:21 | 1 | 2:31 | 0 | 0:00 | [5 empty] | 0.24444
220/132/33kV GRID S/s Pratapsasan
1 | Auto Transformer | AUTO
(i) | 160MVA Auto-1 | AUTO | 0 | 0:00 | 0 | 0:00 | 2 | 1:32 |  |  | 0.063889
(ii) | 160MVA Auto-2 | AUTO | 0 | 0:00 | 0 | 0:00 | 4 | 10:29 |  |  | 0.43681
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 3 | 33:11 | 0 | 0:00 |  |  |  | 1899-12-31 09:11
3 | Bus Fault | BUS | 0 | 0:00 | 0 | 0:00 | 2 | 1:32 |  |  |  |  | 0.063889
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Pratapsasan-Pandiabil Ckt-1 | FEEDER | 1 | 3:08 | 0 | 0:00 | 3 | 2:10 | [5 empty] | 0.22083
(ii) | 220kV Pratapsasan-Pandiabil Ckt-2 | FEEDER | 0 | 0:00 | 1 | 1:05 | 2 | 1:32 | [5 empty] | 0.10903
(iii) | 132 kV Pratapsasan-Phulnakhra Ckt-1 | FEEDER | 0 | 0:00 | 2 | 21:44 | 2 | 0:52 | [5 empty] | 0.94167
(iv) | 132 kV Pratapsasan-Phulnakhra Ckt-2 | FEEDER | 1 | 5:19 | 1 | 3:42 | 1 | 0:21 | [5 empty] | 0.39028
220/132/33kV GRID S/s Chandaka-B
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA Auto 2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Mendhasal-Chandaka B | FEEDER | 1 | 1:57 | 0 | 0:00 | 4 | 11:16 | [5 empty] | 0.55069
(ii) | 220kV Chandaka B-Unit 8 | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(iii) | 220kV Chandaka B-Mancheswar (B) UG cable | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | Charged on 3/4/23,10:44 hrs after cable repair |  |  |  |  | 0
220/33KV Grid S/s Infocity-II
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | Under Defunct Condition |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 3 | 8:42 | 6 | 3:03 | 4 | 2:02 |  |  |  | 0.57431
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220KV Mendhasal - Infocity (II) | FEEDER | 4 | 46:34 | 0 | 0:00 | 1 | 0:33 | [5 empty] | 1899-12-31 23:07
(ii) | 220KV Atri - Infocity (II) | FEEDER | 1 | 0:37 | 0 | 0:00 | 2 | 24:16 | [5 empty] | 1899-12-31 00:53
132/33kV GRID S/s Unit 8
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 2 | 3:16 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.13611
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
132/33KV Grid S/s GIS Mancheswar-B
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 12:00 | 0 | 0:00 |  |  |  | 0.5
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Bhuabneswar- Mancheswar- B GIS | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
|  |  |  | 1900-01-13 19:13 |  | 1900-01-08 09:09 |  | 1900-01-13 05:24
| Total |  |  |  | 1900-02-06 09:46 |  |  |  |  | 0.092361 | 1900-01-01 15:01 | 1900-01-14 08:39 | 0.23958 | 1900-01-19 02:08 | 1900-02-06 09:46
[10 empty] | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = SUM(M4:[Power Trf, row above])
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Auto Trf = SUM(L4:[Auto Trf, row above])
ICT = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
ICT = SUM(K4:[ICT, row above])
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = SUM(N4:[Bus Fault, row above])
Duration of Trippings (Hr:Mn) = SUM(E2:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G2:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I2:[FORM P-3, row above])

## P-3 Bolangir
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Bolangir Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33kV Grid S/S, Bolangir
1 | Power Transformer | POWER
(i) | 40 MVA Transformer 1 | POWER | 4 | 7:46 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.32361
(ii) | 40 MVA Transformer 2 | POWER | 1 | 0:22 | 0 | 0:00 | 3 | 1:32 |  |  |  | 0.079167
(iii) | 40 MVA Transformer 3 | POWER | 3 | 1:11 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.049306
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Bolangir new - Bolangir Ckt-I | FEEDER | 0 | 0:00 | 9 | 64:46 | 6 | 2:59 | [5 empty] | 1900-01-01 19:45
(ii) | 132 kV Bolangir new - Bolangir Ckt-II | FEEDER | 0 | 0:00 | 8 | 37:59 | 6 | 2:24 | [5 empty] | 1899-12-31 16:23
(iii) | 132 kV Bolangir - ACME | FEEDER | 1 | 0:13 | 7 | 33:35 | 9 | 33:52 | [5 empty] | 1900-01-01 19:40
132/33kV Grid S/S, Boudh
1 | Power Transformer | POWER
(i) | 20 MVA Transformer 1 | POWER | 7 | 0:50 | 2 | 0:11 | 8 | 1:04 |  |  |  | 0.086806
(ii) | 20 MVA Transformer 2 | POWER | 2 | 0:16 | 2 | 0:11 | 12 | 6:05 |  |  |  | 0.27222
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132Kv Sonepur - Boudh | FEEDER | 9 | 2:00 | 9 | 1:51 | 5 | 2:16 | [5 empty] | 0.25486
220/132kv Grid S/S New Bolangir
1 | Auto Transformer | AUTO
(i) | 160MVA Auto Transformer No-I | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 2:12 |  |  | 0.091667
(ii) | 160MVA Auto Transformer No-II | AUTO | 1 | 1:40 | 2 | 5:04 | 3 | 2:18 |  |  | 0.37639
(iii) | 160MVA Auto Transformer No-III | AUTO | 0 | 0:00 | 1 | 0:34 | 1 | 0:22 |  |  | 0.038889
2 | Power Transformer | POWER
(i) | 20 MVA Transformer 1 | POWER | 1 | 2:23 | 2 | 0:19 | 4 | 2:59 |  |  |  | 0.23681
(ii) | 40 MVA Transformer 2 | POWER | 1 | 0:19 | 3 | 4:50 | 4 | 2:19 |  |  |  | 0.31111
3 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220KV PGCIL-Boalngir new ckt-I | FEEDER | 0 | 0:00 | 1 | 9:15 | 0 | 0:00 | [5 empty] | 0.38542
(ii) | 220KV PGCIL-Boalngir new ckt-II | FEEDER | 2 | 1:30 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.0625
(iii) | 220 kV Bolangir New- Kesinga | FEEDER | 3 | 2:29 | 1 | 0:35 | 5 | 20:16 | [5 empty] | 0.97222
(iv) | 132kv Bolangir New- Barpali | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 1:59 | [5 empty] | 0.082639
(v) | 132 kV Bolangir New – Sonepur | FEEDER | 6 | 9:48 | 1 | 0:51 | 3 | 2:34 | [5 empty] | 0.55069
132/33kV Grid S/S, Patnagarh
1 | Power Transformer | POWER
(i) | 40 MVA Transformer 1 | POWER | 6 | 2:49 | 2 | 0:23 | 5 | 1:26 |  |  |  | 0.19306
(ii) | 20 MVA Transformer 2 | POWER | 6 | 29:54 | 0 | 0:00 | 0 | 0:00 |  |  |  | 1899-12-31 05:54
(iii) | 20 MVA Transformer 3 | POWER | 13 | 3:44 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.15556
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Bolangir new–Patnagarh ckt -I | FEEDER | 3 | 0:56 | 1 | 0:23 | 1 | 0:30 | [5 empty] | 0.075694
(ii) | 132 kV Bolangir new–Patnagarh ckt-II | FEEDER | 3 | 0:57 | 3 | 0:17 | 2 | 2:07 | [5 empty] | 0.13958
(iii) | 132 kV Patnagarh-Padampur | FEEDER | 3 | 7:55 | 1 | 0:14 | 6 | 1:56 | [5 empty] | 0.42014
132/33kV Grid S/S, Sonepur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer 1 | POWER | 4 | 0:35 | 3 | 1:16 | 0 | 0:00 |  |  |  | 0.077083
(ii) | 40 MVA Transformer 2 | POWER | 1 | 0:14 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0097222
(iii) | 40 MVA Transformer 3 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
132/33kV Grid S/S, Tushra
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 13 | 1:35 | 17 | 2:30 | 16 | 2:49 |  |  |  | 0.2875
(ii) | 40 MVA Transformer-2 | POWER | 19 | 2:16 | 30 | 4:16 | 21 | 1:18 |  |  |  | 0.32639
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 kV ACME - Tushra | FEEDER | 1 | 0:13 | 1 | 0:02 | 2 | 0:28 | [5 empty] | 0.029861
(ii) | 132Kv Tushra- Kesinga line | FEEDER | 1 | 0:10 | 0 | 0:00 | 2 | 0:48 | [5 empty] | 0.040278
(iii) | 132Kv Tushra-RTSS Deogaon Road | FEEDER | 2 | 0:06 | 4 | 0:11 | 1 | 0:02 | [5 empty] | 0.013194
132/33kV Grid S/S, Birmaharajpur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 7 | 2:12 | 1 | 1:28 | 0 | 0:00 |  |  |  | 0.15278
(ii) | 20 MVA Transformer-2 | POWER | 1 | 1:36 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.066667
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 kV Sonepur- Birmaharajpur | FEEDER | 1 | 5:31 | 6 | 1:16 | 0 | 0:00 | [5 empty] | 0.28264
132/33kV Grid S/S, Bhawanipatna
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 0 | 0:00 | 7 | 3:10 | 2 | 0:12 |  |  |  | 0.14028
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:09 |  |  |  | 0.00625
(iii) | 20 MVA Transformer-3 | POWER | 0 | 0:00 | 7 | 3:08 | 2 | 0:12 |  |  |  | 0.13889
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Bhawanipatna- Lanjigarh RTSS | FEEDER | 17 | 22:47 | 27 | 1:23 | 37 | 1:18 | [5 empty] | 1899-12-31 01:28
(ii) | 132KV Bhawanipatna- Bhawanipatna RTSS | FEEDER | 1 | 0:32 | 10 | 1:01 | 10 | 1:07 | [5 empty] | 0.11111
220/132/33 kV Grid S/S Jayapatna
1 | Auto Transformer | AUTO
(i) | 160MVA Auto Transformer 1 | AUTO | 0 | 0:00 | 24 | 115:23 | 0 | 0:00 |  |  | 1900-01-03 19:23
(ii) | 160MVA Auto Transformer 2 | AUTO | 4 | 10:04 | 26 | 132:34 | 1 | 10:52 |  |  | 1900-01-05 09:30
2 | Power Transformer | POWER
(i) | 40 MVA Transformer 1 | POWER | 3 | 1:46 | 0 | 0:00 | 2 | 1:40 |  |  |  | 0.14306
(ii) | 40 MVA Transformer 2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 kV Indravati - Jayapatna | FEEDER | 1 | 1:08 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.047222
(ii) | 220 kV Jayapatna - Kasipur | FEEDER | 1 | 0:12 | 1 | 1:00 | 2 | 1:05 | [5 empty] | 0.095139
(iii) | 132 kV Jayapatna - Dabugaon | FEEDER | 2 | 19:20 | 1 | 0:13 | 0 | 0:00 | [5 empty] | 0.81458
(iv) | 132 kV Jayapatna- Megalift Feeder- I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(v) | 132 kV Jayapatna- Megalift Feeder- II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kV Grid S/S, Junagarh
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 7 | 1:23 | 0 | 0:00 | 1 | 0:23 |  |  |  | 0.073611
(ii) | 20 MVA Transformer-2 | POWER | 1 | 0:23 | 1 | 36:53 | 1 | 4392:00 |  |  |  | 1900-07-02 13:16
(iii) | 20 MVA Transformer-3 | POWER | 2 | 1:05 | 2 | 2:16 | 3 | 1:48 |  |  |  | 0.21458
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 kV Junagarh-Bhawanipatna | FEEDER | 2 | 0:24 | 2 | 0:16 | 11 | 3:23 | [5 empty] | 0.16875
220/132/33kV Grid S/S, Kesinga
1 | Auto Transformer | AUTO
(i) | 160MVA Auto Transformer 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 2 | 0:48 |  |  | 0.033333
(ii) | 160MVA Auto Transformer 2 | AUTO | 0 | 0:00 | 0 | 0:00 | 2 | 0:57 |  |  | 0.039583
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 5 | 0:56 | 3 | 0:20 | 1 | 0:05 |  |  |  | 0.05625
(ii) | 40 MVA Transformer-2 | POWER | 4 | 0:31 | 2 | 15:00 | 1 | 0:05 |  |  |  | 0.65
(iii) | 20 MVA Transformer-3 | POWER | 4 | 0:31 | 2 | 0:14 | 3 | 1:23 |  |  |  | 0.088889
3 | Bus Fault | BUS
4 | EHT Feeder fault | FEEDER
(i) | 220 kV Bolangir PG - Kesinga | FEEDER | 2 | 0:30 | 2 | 5:45 | 1 | 0:53 | [5 empty] | 0.29722
(ii) | 220 kV New Bolangir - Kesinga | FEEDER | 4 | 2:15 | 1 | 0:35 | 2 | 1:11 | [5 empty] | 0.16736
(iii) | 132kV Kesinga- Junagarh | FEEDER | 3 | 0:25 | 1 | 0:09 | 3 | 0:50 | [5 empty] | 0.058333
(iv) | 132kV Kesinga RTSS | FEEDER | 2 | 0:26 | 0 | 0:00 | 2 | 0:45 | [5 empty] | 0.049306
(v) | 132kV Kesinga - ABReL | FEEDER | 0 | 0:00 | 0 | 0:00 | 4 | 1:12 | [5 empty] | 0.05
(vi) | 132kV Kesinga - Powmax | FEEDER | 0 | 0:00 | 0 | 0:00 | 6 | 2:30 | [5 empty] | 0.10417
(vii) | 132kV Kesinga - Vento Solar -I | FEEDER | 1 | 0:10 | 3 | 1:07 | 3 | 0:13 | [5 empty] | 0.0625
(viii) | 132kV Kesinga - Vento Solar-II | FEEDER | 0 | 0:00 | 1 | 1:00 | 4 | 0:16 | [5 empty] | 0.052778
(viii) | 132kv Kesinga-Bhawanipatna | FEEDER | 7 | 2:12 | 5 | 1:30 | 5 | 1:02 | [5 empty] | 0.19722
132/33kV Grid S/S, Saintala
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 2 | 1:52 | 4 | 0:37 | 1 | 0:15 |  |  |  | 0.11389
(ii) | 10 MVA Transformer-2 | POWER | 1 | 0:11 | 4 | 0:28 | 1 | 0:08 |  |  |  | 0.032639
(iii) | 10 MVA Transformer-3 | POWER | 7 | 21:19 | 5 | 17:46 | 7 | 8:54 |  |  |  | 1899-12-31 23:59
2 | Bus Fault | BUS | [10 empty] | 0
3 | EHT Feeder fault | FEEDER | [11 empty] | 0
132/33kV Grid S/S, Khariar
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 3 | 0:12 | 0 | 0:00 | 3 | 0:27 |  |  |  | 0.027083
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:03 |  |  |  | 0.0020833
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Kesinga- Khariar | FEEDER | 10 | 1:46 | 11 | 1:46 | 18 | 4:52 | [5 empty] | 0.35
(ii) | 132KV Khariar - Kantabanji | FEEDER | 4 | 0:28 | 1 | 0:05 | 1 | 0:09 | [5 empty] | 0.029167
(iii) | 132KV Khariar-Nuapada | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kV Grid S/S, Nuapada
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 2 | 7:19 | 1 | 1:35 | 1 | 0:24 |  |  |  | 0.3875
(ii) | 20 MVA Transformer-2 | POWER | 1 | 1:16 | 2 | 2:25 | 4 | 1:05 |  |  |  | 0.19861
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Padampur-Nuapada Ckt-1 | FEEDER | 12 | 7:51 | 3 | 0:37 | 1 | 0:17 | [5 empty] | 0.36458
(ii) | 132KV Padampur-Nuapada Ckt-2 | FEEDER | 0 | 0:00 | 4 | 2:18 | 4 | 19:53 | [5 empty] | 0.92431
(iii) | 132KV Nuapada - Nuapada RTSS | FEEDER | 3 | 1:00 | 1 | 0:02 | 1 | 0:18 | [5 empty] | 0.055556
132/33kV Grid S/S, Padampur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer 1 | POWER | 8 | 1:01 | 7 | 1:41 | 11 | 1:08 |  |  |  | 0.15972
(ii) | 20 MVA Transformer 2 | POWER | 17 | 2:06 | 12 | 2:38 | 6 | 2:08 |  |  |  | 0.28611
(iii) | 40 MVA Transformer 3 | POWER | 14 | 1:18 | 4 | 0:41 | 1 | 0:03 |  |  |  | 0.084722
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER | [11 empty] | 0
132/33kV Grid S/S, Kantabanji
1 | Power Transformer | POWER | 3 | 0:56 | 1 | 0:03 | 1 | 0:10 |  |  |  | 0.047917
(i) | 40 MVA Transformer-1 | POWER | [9 empty] | 0
(ii) | 40 MVA Transformer-2 | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Kantabanj- Kantabanji RTSS | FEEDER | 49 | 1:31 | 38 | 4:01 | 29 | 3:15 | [5 empty] | 0.36597
|  |  |  | 1900-01-07 16:36 |  | 1900-01-21 03:57 |  | 1900-07-08 06:23
| Total |  |  |  | 1900-08-08 02:56 |  |  |  |  | 0 | 1900-01-10 18:48 | 1900-07-11 06:40 | 0 | 1900-01-15 01:28 | 1900-08-08 02:56
[10 empty] | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = [Duration of Trippings (Hr:Mn)]+[FORM P-3]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Bus Fault = SUM([FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)])

## P-3 Burla
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Burla Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33kV Grid S/S, Barapalli
1 | Power Transformer | POWER
(i) | 40 MVA Transformer 1 | POWER | 1 | 0:15 | 1 | 0:15 | 3 | 1:45 |  |  |  | 0.09375
(ii) | 20 MVA Transformer 2 | POWER | 1 | 0:15 | 0 | 0:00 | 3 | 1:47 |  |  |  | 0.084722
(iii) | 20 MVA Transformer 3 | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 0:24 |  |  |  | 0.016667
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Barpali- Bargarh New | FEEDER | 3 | 3:00 | 0 | 0:00 | 2 | 1:57 | [5 empty] | 0.20625
(ii) | 132 kV RTSS Dunguripali | FEEDER | 0 | 0:00 | 1 | 0:03 | 1 | 0:06 | [5 empty] | 0.00625
132/33KV Grid S/s Bhatli
1 | Power Transformer | POWER
(i) | 40MVA Transformer 1 | POWER | 3 | 2:23 | 3 | 11:19 | 2 | 1:29 |  |  |  | 0.63264
(ii) | 40MVA Transformer 2 | POWER | 4 | 4:16 | 5 | 6:14 | 1 | 0:51 |  |  |  | 0.47292
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Bargarh New- Bhatli Ckt-I | FEEDER | 5 | 3:42 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.15417
(ii) | 133 kV Bargarh New- Bhatli Ckt-II | FEEDER | 2 | 0:53 | 1 | 1:04 | 0 | 0:00 | [5 empty] | 0.08125
132/33KV Grid S/s Baragrh
1 | Power Transformer | POWER
(i) | 40MVA Transformer 1 | POWER | 3 | 2:23 | 5 | 1:33 | 0 | 0:00 |  |  |  | 0.16389
(ii) | 40MVA Transformer 2 | POWER | 4 | 4:16 | 5 | 11:25 | 5 | 7:01 |  |  |  | 0.94583
(iii) | 40MVA Transformer 3 | POWER | 4 | 2:50 | 0 | 0:00 | 1 | 0:07 |  |  |  | 0.12292
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Bargarh - Thuapali | FEEDER | 5 | 3:42 | 0 | 0:00 | 3 | 1:02 | [5 empty] | 0.19722
(ii) | 132kV Baragrh-Bargarh New | FEEDER | 2 | 0:53 | 0 | 0:00 | 1 | 0:44 | [5 empty] | 0.067361
(iii) | 132 kV Bargarh - ACC CKT-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(iv) | 132 kV Bargarh - ACC CKT-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
220/132/33kV GRID S/s Bargarh New
1 | Auto Transformer | AUTO
(i) | 160MVA AUTO-1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 100MVA AUTO-2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 0 | 0:00 | 8 | 3:06 | 6 | 3:14 |  |  |  | 0.26389
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220 KV Bargarh New- Katapali | FEEDER | 3 | 5:23 | 0 | 0:00 | 3 | 1:45 | [5 empty] | 0.29722
(ii) | 220 KV Bargarh New- New Bolangir | FEEDER | 1 | 1:14 | 1 | 1:05 | 0 | 0:00 | [5 empty] | 0.096528
(iii) | 132 KV Bargarh New - Ghens Ckt-I | FEEDER | 2 | 1:44 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.072222
(iv) | 132 KV Bargarh New - Ghens Ckt-II | FEEDER | 3 | 10:11 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.42431
132/33KV Grid S/s Ghess
1 | Power Transformer | POWER
(i) | 40MVA Transformer 1 | POWER | 0 | 0:00 | 6 | 18:22 | 2 | 3:15 |  |  |  | 0.90069
(ii) | 40MVA Transformer 2 | POWER | 0 | 0:00 | 5 | 12:42 | 2 | 3:20 |  |  |  | 0.66806
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
132/33KV Grid S/s Thuapali
1 | Power Transformer | POWER
(i) | 20MVA Transformer 1 | POWER | 2 | 0:43 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.029861
(ii) | 20MVA Transformer 2 | POWER | 1 | 0:31 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.021528
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
132/33KV Grid S/s Hirakud
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-2 | POWER | 7 | 1:43 | 2 | 0:32 | 0 | 0:00 |  |  |  | 0.09375
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Lapanga- Burla PH Ckt-I "T" at Hirakud | FEEDER | 11 | 31:42 | 0 | 0:00 | 11 | 36:48 | [5 empty] | 1900-01-01 20:30
(ii) | 132 KV Burla PH - Hirakud | FEEDER | 2 | 9:24 | 1 | 0:07 | 5 | 16:13 | [5 empty] | 1899-12-31 01:44
132/33KV Grid S/s Brajarajnagar
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Transformer-4 | POWER | 1 | 0:40 | 0 | 0:00 | 1 | 13:59 |  |  |  | 0.61042
(iv) | 20 MVA Transformer-5 | POWER | 6 | 0:37 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.025694
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
220/132/33kV GRID S/s Budhipadar
1 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 1 | 1:05 | 0 | 0:00 | 1 | 13:45 |  |  | 0.61806
(ii) | 160MVA Auto 2 | AUTO | 3 | 4:47 | 1 | 0:34 | 0 | 0:00 |  |  | 0.22292
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 3 | 0:39 | 1 | 21:26 |  |  |  | 0.92014
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 0:00 | 5 | 16:13 | 3 | 7:04 |  |  |  | 0.97014
3 | Bus Fault | BUS
(i) | 220 KV Main Bus-I | BUS | 0 | 0:00 | 1 | 0:49 | 1 | 0:42 |  |  |  |  | 0.063194
(ii) | 220 KV Main Bus-II | BUS | 0 | 0:00 | 2 | 1:22 | 2 | 1:22 |  |  |  |  | 0.11389
(iii) | 132 KV Main Bus | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220 KV Budhipadar-Lephirpada | FEEDER | 3 | 1:27 | 2 | 5:16 | 3 | 1:25 | [5 empty] | 0.33889
(ii) | 220 KV Budhipadar-Raigarh PG | FEEDER | 7 | 42:58 | 2 | 9:56 | 6 | 62:29 | [5 empty] | 1900-01-03 19:23
(iii) | 220 KV Budhipadar-Korba Ckt-I | FEEDER | 3 | 17:41 | 2 | 4:21 | 7 | 44:44 | [5 empty] | 1900-01-01 18:46
(iv) | 220 KV Budhipadar-Korba Ckt-II | FEEDER | 3 | 21:13 | 2 | 11:25 | 5 | 46:27 | [5 empty] | 1900-01-02 07:05
(v) | 220 KV Budhipadar-IB Ckt-I | FEEDER | 4 | 3:16 | 1 | 0:35 | 6 | 12:58 | [5 empty] | 0.70069
(vi) | 220 KV Budhipadar-IB Ckt-II | FEEDER | 2 | 13:27 | 2 | 2:28 | 4 | 7:23 | [5 empty] | 0.97083
(vii) | 220 KV Budhipadar-IB Ckt-III | FEEDER | 4 | 17:21 | 1 | 3:50 | 6 | 31:50 | [5 empty] | 1900-01-01 05:01
(viii) | 220 KV Budhipadar-IB Ckt-IV | FEEDER | 2 | 0:46 | 1 | 0:38 | 3 | 5:11 | [5 empty] | 0.27431
(ix) | 220 KV Budhipadar-Kuarnmunda | FEEDER | 2 | 1:43 | 3 | 14:50 | 5 | 44:26 | [5 empty] | 1900-01-01 12:59
(x) | 220 KV Budhipadar-Bamra | FEEDER | 1 | 1:08 | 2 | 1:12 | 4 | 19:52 | [5 empty] | 0.925
(xi) | 220 KV Budhipadar-Lapanga Ckt-I | FEEDER | 1 | 0:26 | 2 | 52:01 | 5 | 7:48 | [5 empty] | 1900-01-01 12:15
(xii) | 220 KV Budhipadar-Lapanga Ckt-II | FEEDER | 1 | 1:13 | 2 | 26:44 | 0 | 0:00 | [5 empty] | 1899-12-31 03:57
(xiii) | 220 KV Budhipadar-Bhushan Ckt-I | FEEDER | 0 | 0:00 | 1 | 10:17 | 1 | 0:25 | [5 empty] | 0.44583
(xiv) | 220 KV Budhipadar-Bhushan Ckt-II | FEEDER | 2 | 7:46 | 1 | 1:17 | 1 | 2:49 | [5 empty] | 0.49444
(xv) | 220 KV Budhipadar-SMC Unit-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xvi) | 220 KV Budhipadar-AAL Ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xvii) | 220 KV Budhipadar-AAL Ckt-II | FEEDER | 1 | 1:53 | 2 | 3:49 | 0 | 0:00 | [5 empty] | 0.2375
(xviii) | 220 KV Budhipadar-VAL Ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xix) | 220 KV Budhipadar-VAL Ckt-II | FEEDER | 0 | 0:00 | 1 | 0:32 | 0 | 0:00 | [5 empty] | 0.022222
(xx) | 132 KV Budhipadar- Sundergarh PG Ckt-I | FEEDER | 0 | 0:00 | 1 | 0:16 | 1 | 11:10 | [5 empty] | 0.47639
(xxi) | 132 KV Budhipadar- Sundergarh PG Ckt-II | FEEDER | 3 | 49:43 | 1 | 0:16 | 3 | 2:04 | [5 empty] | 1900-01-01 04:03
(xxii) | 132 KV Budhipadar- Kalunga | FEEDER | 24 | 35:15 | 3 | 7:34 | 28 | 118:37 | [5 empty] | 1900-01-05 17:26
(xxiii) | 132 KV Budhipadar- Bamra (formerly Rajgangpur) | FEEDER | 13 | 14:56 | 1 | 1:01 | 9 | 17:20 | [5 empty] | 1899-12-31 09:17
(xxv) | 132 KV Budhipadar-Jharsuguda Ckt-II | FEEDER | 1 | 0:58 | 0 | 0:00 | 2 | 20:43 | [5 empty] | 0.90347
(xxiv) | 132 KV Budhipadar-Lapanga | FEEDER | 4 | 19:44 | 1 | 29:25 | 5 | 90:15 | [5 empty] | 1900-01-04 19:24
(xxvi) | 132 KV Budhipadar-Jharsuguda Ckt-I | FEEDER | 1 | 0:57 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.039583
(xxvii) | 132 KV Budhipadar-Brajrajnagar(Remja) | FEEDER | 9 | 14:50 | 0 | 0:00 | 3 | 2:07 | [5 empty] | 0.70625
(xxviii) | 132 KV Budhipadar- MCLCkt-I | FEEDER | 5 | 9:05 | 0 | 0:00 | 7 | 34:54 | [5 empty] | 1899-12-31 19:59
(xxix) | 132 KV Budhipadar- Lakhanpur (Formerly MCL-II) | FEEDER | 9 | 43:34 | 0 | 0:00 | 10 | 29:58 | [5 empty] | 1900-01-02 01:32
(xxx) | 132 KV Budhipadar-MSP | FEEDER | 5 | 3:53 | 1 | 0:15 | 1 | 0:47 | [5 empty] | 0.20486
220/33KV Grid S/s Lephripada
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 1 | 0:57 | 0 | 0:00 | 2 | 3:12 |  |  |  | 0.17292
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220 KV Basundhara- Lephripada | FEEDER | 3 | 3:27 | 2 | 6:57 | 0 | 0:00 | [5 empty] | 0.43333
132/33KV Grid S/s Lakhanpur
1 | Power Transformer | POWER | 39 | 247:55 | 26 | 267:36 | 24 | 818:53 |  |  |  | 1900-02-23 14:24
(i) | 20 MVA Transformer-1 | POWER | [9 empty] | 0
(ii) | 20 MVA Transformer-2 | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | 13 | 1497:07 | 1 | 59:31 | 13 | 1927:12 | [5 empty] | 1900-05-24 03:50
(i) | 132 KV Brajrajnagar- Lakhanpur | FEEDER | [11 empty] | 0
132/33KV Grid S/s Jharsuguda
1 | Power Transformer | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(i) | 40 MVA Transformer-1 | POWER | [9 empty] | 0
(ii) | 40 MVA Transformer-2 | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Jharsuguda- RTSS Jharsuguda | FEEDER | 4 | 1:30 | 0 | 0:00 | 1 | 0:37 | [5 empty] | 0.088194
(ii) | 132 KV Jharsuguda-Ultratech | FEEDER | 2 | 3:44 | 0 | 0:00 | 1 | 0:40 | [5 empty] | 0.18333
132/33KV Grid S/s Kuchinda
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 9 | 3:56 | 2 | 0:54 | 1 | 17:51 |  |  |  | 0.94514
(ii) | 20 MVA Transformer-2 | POWER | 2 | 10:41 | 0 | 0:00 | 1 | 0:52 |  |  |  | 0.48125
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Rajgangpur/Kutra-Kuchinda | FEEDER | 7 | 35:19 | 8 | 82:48 | 11 | 51:04 | [5 empty] | 1900-01-06 01:11
(ii) | 132kV Kuchinda-SMC | FEEDER | 21 | 65:49 | 14 | 46:49 | 15 | 75:52 | [5 empty] | 1900-01-06 20:30
220/132/33kV GRID S/s Katapali
1 | Auto Transformer | AUTO
(i) | 100MVA AUTO-1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 100MVA AUTO-2 | AUTO | 0 | 0:00 | 2 | 490:50 | 0 | 0:00 |  |  | 1900-01-19 10:50
(iii) | 160MVA AUTO-3 | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 0:55 |  |  | 0.038194
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 6 | 2:59 | 1 | 0:02 | 3 | 0:58 |  |  |  | 0.16597
(ii) | 20 MVA Transformer-2 | POWER | 3 | 1:06 | 1 | 0:02 | 2 | 0:45 |  |  |  | 0.078472
(iii) | 40 MVA Transformer-3 | POWER | 2 | 0:29 | 1 | 0:03 | 2 | 0:48 |  |  |  | 0.055556
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220 KV Katapali-Lapanga Ckt- I | FEEDER | 5 | 21:38 | 1 | 0:35 | 2 | 3:33 | [5 empty] | 1899-12-31 01:46
(ii) | 220 KV Katapali-Lapanga Ckt- II | FEEDER | 9 | 61:05 | 2 | 15:59 | 3 | 4:17 | [5 empty] | 1900-01-02 09:21
(iii) | 220 KV Katapali-HINDACO Ckt- I | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 2:30 | [5 empty] | 0.10417
(iv) | 220 KV Katapali-HINDACO Ckt- II | FEEDER | 2 | 5:21 | 2 | 3:27 | 1 | 2:15 | [5 empty] | 0.46042
(v) | 220 KV Katapali-PGCIL (Bolangir) | FEEDER | 14 | 94:18 | 1 | 12:46 | 4 | 17:38 | [5 empty] | 1900-01-04 04:42
(vi) | 132 KV Katapali- Thuapali | FEEDER | 7 | 32:39 | 0 | 0:00 | 4 | 2:19 | [5 empty] | 1899-12-31 10:58
(vii) | 132 KV Katapali- Chiplima Ckt-I | FEEDER | 6 | 6:16 | 0 | 0:00 | 2 | 2:23 | [5 empty] | 0.36042
(viii) | 132 KV Katapali-Sambalpur | FEEDER | 2 | 2:11 | 1 | 0:05 | 2 | 3:14 | [5 empty] | 0.22917
(ix) | 132 KV Katapali - Burla Power house Ckt- I | FEEDER | 9 | 12:20 | 1 | 0:20 | 15 | 28:17 | [5 empty] | 1899-12-31 16:57
(x) | 132 KV Katapali- Chiplima Ckt-II | FEEDER | 16 | 87:26 | 1 | 0:05 | 3 | 14:02 | [5 empty] | 1900-01-03 05:33
(xi) | 132 KV Katapali - Burla Power house Ckt- II | FEEDER | 8 | 3:23 | 2 | 0:58 | 11 | 38:59 | [5 empty] | 1899-12-31 19:20
(xii) | 132 KV Katapali-Godhbhaga RTSS | FEEDER | 1 | 0:31 | 3 | 4:26 | 0 | 0:00 | [5 empty] | 0.20625
400/220/132/33KV Grid S/s Lapanga
1 | ICT | ICT
(i) | 315MVA ICT - 1 | ICT | 3 | 1:38 | 0 | 0:00 | 0 | 0:00 |  | 0.068056
(i) | 315MVA ICT - 2 | ICT | 2 | 1:21 | 2 | 9:32 | 0 | 0:00 |  | 0.45347
2 | Auto Transformer | AUTO
(i) | 160MVA Auto 1 | AUTO | 5 | 165:17 | 2 | 24:19 | 1 | 0:26 |  |  | 1900-01-06 22:02
(ii) | 160MVA Auto 2 | AUTO | 6 | 200:55 | 4 | 10:17 | 2 | 1:15 |  |  | 1900-01-07 20:27
3 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 3 | 2:38 | 1 | 0:04 | 0 | 0:00 |  |  |  | 0.1125
(i) | 20 MVA Transformer-2 | POWER | 5 | 14:18 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.59583
4 | Bus fault | BUS
(i) | 400KV Bus-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 400KV Bus-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
5 | Bus fault | BUS
(i) | 220KV Bus- I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(i) | 220KV Bus- II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
5 | Bus fault | BUS
(i) | 132KV Bus- I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(i) | 132KV Bus- II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
6 | EHT Feeder fault | FEEDER
(i) | 400KV Lapanga-IB Ckt-I | FEEDER | 4 | 23:44 | 0 | 0:00 | 1 | 2:09 | [5 empty] | 1899-12-31 01:53
(ii) | 400KV Lapanga-IB Ckt-II | FEEDER | 4 | 30:25 | 0 | 0:00 | 2 | 4:23 | [5 empty] | 1899-12-31 10:48
(iii) | 400KV Lapanga- Meramundali Ckt-I | FEEDER | 14 | 73:01 | 0 | 0:00 | 1 | 25:14 | [5 empty] | 1900-01-03 02:15
(iv) | 400KV Lapanga-Meramundali Ckt-II | FEEDER | 13 | 73:28 | 0 | 0:00 | 2 | 28:17 | [5 empty] | 1900-01-03 05:45
(v) | 400KV Lapanga-Sterlite Ckt-I | FEEDER | 3 | 0:24 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.016667
(vi) | 400KV Lapanga-Sterlite Ckt-II | FEEDER | 4 | 0:28 | 3 | 12:32 | 4 | 14:13 | [5 empty] | 1899-12-31 03:13
(vii) | 132 KV Lapanga-RTSS Rengali | FEEDER | 4 | 11:16 | 1 | 0:47 | 3 | 11:13 | [5 empty] | 0.96944
(viii) | 132 KV Lapanga-SMC | FEEDER | 1 | 5:10 | 1 | 4:39 | 4 | 22:13 | [5 empty] | 1899-12-31 08:02
(ix) | 132 KV Lapanga-Aryan Ispat | FEEDER | 13 | 52:54 | 3 | 22:36 | 3 | 4:20 | [5 empty] | 1900-01-02 07:50
(x) | 132 KV Lapanga-Jharsuguda | FEEDER | 6 | 8:26 | 1 | 2:58 | 6 | 33:01 | [5 empty] | 1899-12-31 20:25
(xi) | 132 KV Lapanga-Burla Ckt- II | FEEDER | 18 | 35:03 | 3 | 31:08 | 7 | 6:38 | [5 empty] | 1900-01-02 00:49
132/33KV Grid S/s Maneswar
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 4 | 8:22 | 13 | 75:10 | 4 | 0:48 |  |  |  | 1900-01-02 12:20
(ii) | 40 MVA Transformer-2 | POWER | 3 | 22:23 | 2 | 5:07 | 4 | 0:22 |  |  |  | 1899-12-31 03:52
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Maneswar-Rairakhol | FEEDER | 3 | 1:00 | 1 | 0:19 | 4 | 17:51 | [5 empty] | 0.79861
(ii) | 132 KV Maneswar- RTSS Maneswar | FEEDER | 0 | 0:00 | 1 | 0:35 | 1 | 0:26 | [5 empty] | 0.042361
132/33KV Grid S/s Rairakhol
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 3 | 0:40 | 0 | 0:00 | 1 | 0:23 |  |  |  | 0.04375
(ii) | 12.5 MVA Transformer-2 | POWER | 2 | 0:45 | 1 | 1:57 | 0 | 0:00 |  |  |  | 0.1125
(iii) | 12.5 MVA Transformer-3 | POWER | 7 | 1:15 | 5 | 2:47 | 11 | 2:33 |  |  |  | 0.27431
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Rairakhol-Boinda | FEEDER | 1 | 0:14 | 1 | 0:33 | 9 | 17:44 | [5 empty] | 0.77153
(ii) | 132 KV Rairakhol- RTSS Rairakhol | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Sambalpur
1 | Power Transformer | POWER
(i) | 31.5 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 31.5 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 9:34 | Bucholz relay & OSR relay covered to protect from moisture ingress due to rain. |  |  | 0.39861
(iv) | 40 MVA Transformer-4 | POWER | 3 | 94:57 | 0 | 0:00 | 0 | 0:00 |  |  |  | 1900-01-02 22:57
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Burla-Sambalpur | FEEDER | 6 | 19:40 | 1 | 0:37 | 4 | 90:21 | Tripping due to DC tower of 132KV SBP-BurlaPH & 132KV SBP-SDRI collapse at loc No. LILO 14, erection done within short duration to resume supply |  |  |  |  | 1900-01-03 14:38
(ii) | 132kV Sambalpur-ShyamDRI Feeder | FEEDER | 9 | 97:44 | 0 | 0:00 | 8 | 94:25 | [5 empty] | 1900-01-07 00:09
(iii) | 132kV Sambalpur-Maneswar Feeder | FEEDER | 3 | 1:17 | 0 | 0:00 | 4 | 4:32 | [5 empty] | 0.24236
220/132/33kV GRID S/s Kuarnmunda
1 | Auto Transformer | AUTO
(i) | 160MVA AUTO-1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA AUTO-2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS | 1 | 1:14 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0.051389
4 | EHT Feeder Fault | FEEDER
(i) | 132 KV Kuarnmunda-Chhend | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 20:07 | [5 empty] | 0.83819
(ii) | 132 KV Kuarnmunda-Shree Ganesh Metaliks | FEEDER | 0 | 0:00 | 0 | 0:00 | 3 | 13:53 | [5 empty] | 0.57847
220/132/33kV GRID S/s Bamra
1 | Auto Transformer | AUTO
(i) | 160MVA AUTO-1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 160MVA AUTO-2 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS | 1 | 1:14 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0.051389
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Bamra-Tarkera | FEEDER | 6 | 5:36 | 4 | 3:20 | 5 | 4:43 | [5 empty] | 0.56875
(ii) | 132kV Bamra-Budhipadar | FEEDER | 12 | 31:26 | 1 | 1:01 | 10 | 15:09 | [5 empty] | 1899-12-31 23:36
(iii) | 132kV Bamra-Rajgangpur | FEEDER | 6 | 24:01 | 1 | 0:39 | 10 | 37:47 | [5 empty] | 1900-01-01 14:27
(iv) | 132kV Bamra RTSS 1 | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(v) | 132kV Bamra RTSS 2 | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kv Grid S/S, Rajgangpur
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 4 | 1:47 |  |  |  | 0.074306
(ii) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 4 | 1:26 |  |  |  | 0.059722
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 4 | 2:59 |  |  |  | 0.12431
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Rajgangpur- Tarkera Ckt- I | FEEDER | 9 | 21:56 | 1 | 0:57 | 0 | 0:00 | [5 empty] | 0.95347
(ii) | 132KV Rajgangpur- Tarkera Ckt- II | FEEDER | 9 | 24:00 | 0 | 0:00 | 4 | 26:28 | [5 empty] | 1900-01-01 02:28
(iii) | 132KV Rajgangpur- Shiva Cement (kutra) | FEEDER | 24 | 19:08 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.79722
(iv) | 132KV Rajgangpur- Railway Ckt-I | FEEDER | 3 | 2:48 | 0 | 0:00 | 5 | 1:35 | [5 empty] | 0.18264
(v) | 132KV Rajgangpur- Railway Ckt-II | FEEDER | 1 | 1:09 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.047917
(vi) | 132KV Rajgangpur - OCL | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(vii) | 132KV Rajgangpur - OISL | FEEDER | 1 | 0:29 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.020139
132/33kv Grid S/S, Sundargarh
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 3 | 1:17 | 0 | 0:00 |  |  |  | 0.053472
(ii) | 20 MVA Transformer-2 | POWER | 11 | 22:40 | 5 | 3:11 | 1 | 0:36 |  |  |  | 1899-12-31 02:27
(iii) | 20 MVA Transformer-3 | POWER | 3 | 1:11 | 1 | 0:15 | 0 | 0:00 |  |  |  | 0.059722
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
132/33kv Grid S/S Kalunga
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 3 | 2:03 | 2 | 2:19 | 2 | 1:56 |  |  |  | 0.2625
(ii) | 40 MVA Transformer-2 | POWER | 3 | 2:04 | 5 | 3:11 | 0 | 0:00 |  |  |  | 0.21875
(iii) | 40 MVA Transformer-3 | POWER | 3 | 2:04 | 2 | 2:27 | 3 | 4:47 |  |  |  | 0.3875
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Kalunga-Tarkera | FEEDER | 1 | 4:28 | 11 | 186:41 | 6 | 47:38 | [5 empty] | 1900-01-08 22:47
220/33kv Grid S/S Barkote
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 2 | 1:12 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.05
(ii) | 40 MVA Transformer-2 | POWER | 3 | 1:45 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.072917
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220kv Barkote-Deogarh | FEEDER | 2 | 0:24 | 0 | 0:00 | 1 | 0:15 | [5 empty] | 0.027083
(ii) | 220kv Barkote-Bonai | FEEDER | 2 | 0:34 | 0 | 0:00 | 2 | 0:30 | [5 empty] | 0.044444
220/33kv Grid S/S Bonai
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:18 | 2 | 0:53 |  |  |  | 0.049306
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 KV Bonai - Tarkera | FEEDER | 0 | 0:00 | 1 | 0:29 | 4 | 18:31 | [5 empty] | 0.79167
(ii) | 220 KV Bonai - RTSS Bimlagarh | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 14:35 | [5 empty] | 0.60764
132/33kv Grid S/S, Chhend
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 1 | 0:12 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0083333
(ii) | 40 MVA Transformer-2 | POWER | 1 | 4:40 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.19444
(iii) | 40 MVA Transformer-3 | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 1:09 |  |  |  | 0.047917
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Chhend-Tarkera ckt-I | FEEDER | 0 | 0:00 | 1 | 1:49 | 1 | 4:42 | [5 empty] | 0.27153
(ii) | 132kV Chhend-Tarkera ckt-II | FEEDER | 0 | 0:00 | 1 | 1:30 | 1 | 5:19 | [5 empty] | 0.28403
(iii) | 132kV Nuagaon Traction | FEEDER | 1 | 3:19 | 1 | 0:03 | 3 | 6:59 | [5 empty] | 0.43125
220/33kv Grid S/S Deogarh
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 0:14 | 2 | 0:34 |  |  |  | 0.033333
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:14 | 3 | 6:41 |  |  |  | 0.28819
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 KV Rengali- Deogarh | FEEDER | 0 | 0:00 | 0 | 0:00 | 3 | 27:39 | [5 empty] | 1899-12-31 03:39
132/33 kV S/S, Rourkela
1 | Power Transformer | POWER
(i) | 35MVA Transformer 1 | POWER | 0 | 0:00 | 2 | 27:14 | 0 | 0:00 |  |  |  | 1899-12-31 03:14
(ii) | 35 MVA Transformer 2 | POWER | 6 | 2:10 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.090278
(iii) | 35MVA Transformer 3 | POWER | 8 | 2:26 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.10139
(iv) | 40MVA Transformer 4 | POWER | 10 | 5:07 | 3 | 6:49 | 14 | 61:49 |  |  |  | 1900-01-02 01:45
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kv Rourkela-Tarkera ckt-I | FEEDER | 0 | 0:00 | 2 | 1:43 | 2 | 2:25 | [5 empty] | 0.17222
(ii) | 132kv Rourkela-Tarkera ckt-II | FEEDER | 0 | 0:00 | 3 | 2:52 | 2 | 2:32 | [5 empty] | 0.225
(iii) | 132kv Rourkela-Tarkera ckt-III | FEEDER | 0 | 0:00 | 2 | 2:45 | 2 | 1:34 | [5 empty] | 0.17986
(iv) | 132kv Rourkela-Joda (Nalda) | FEEDER | 12 | 29:50 | 6 | 14:38 | 27 | 7:56 | [5 empty] | 1900-01-01 04:24
220/132kv Grid S/S Tarkera
1 | Auto Transformer | AUTO
(i) | 100MVA Auto Transformer-I | AUTO | 1 | 0:45 | 0 | 0:00 | 0 | 0:00 |  |  | 0.03125
(ii) | 100MVA Auto Transformer-II | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(iii) | 100MVA Auto Transformer-III | AUTO | 1 | 7:04 | 2 | 12:05 | 0 | 0:00 |  |  | 0.79792
(iv) | 100MVA Auto Transformer-IV | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220kv Tarkera-Kuarnmunda | FEEDER | 1 | 0:53 | 1 | 0:35 | 1 | 8:20 | [5 empty] | 0.40833
(ii) | 220kv Tarkera-Rengali | FEEDER | 1 | 0:53 | 2 | 13:31 | 3 | 30:19 | [5 empty] | 1899-12-31 20:43
(iii) | 220kV Tarkera- RSP Ckt-I | FEEDER | 1 | 21:13 | 1 | 0:57 | 1 | 22:47 | [5 empty] | 1899-12-31 20:57
(iv) | 220kV Tarkera- RSP Ckt-II | FEEDER | 1 | 2:05 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.086806
(v) | 220kV Tarkera- RSP Ckt-III | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(vi) | 220kV Tarkera- RSP Ckt-IV | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(vii) | 220kV Tarkera- Bisra PGCIL Ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 1:31 | [5 empty] | 0.063194
(viii) | 220kV Tarkera- Bisra PGCILCkt-II | FEEDER | 1 | 54:51 | 1 | 4:25 | 1 | 3:48 | [5 empty] | 1900-01-01 15:04
(ix) | 132kV Tarkera- RSP Ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(x) | 132kV Tarkera- RSP Ckt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
|  |  |  | 1900-06-09 17:29 |  | 1900-03-13 21:01 |  | 1900-07-08 18:54 |  | 0.52153 | 1900-02-06 22:19 | 1900-03-22 04:36 | 0.27986 | 1900-10-30 11:15 | 1901-03-01 09:24
| Total |  |  |  | 1901-03-01 09:24 |  |  |  |  | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = SUM(M5:[Power Trf, row above])
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
ICT = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
ICT = SUM(K5:[ICT, row above])
Duration of Trippings (Hr:Mn) = SUM(E5:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G5:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I5:[FORM P-3, row above])

## P-3 Chainpal
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Chainpal Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33KV Grid S/s Angul
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 5 | 1:43 | 0 | 0:00 | 2 | 1:14 |  |  |  | 0.12292
(ii) | 40 MVA Transformer-II | POWER | 5 | 5:58 | 0 | 0:00 | 2 | 1:12 |  |  |  | 0.29861
(iii) | 20 MVA Transformer-III | POWER | 6 | 2:12 | 0 | 0:00 | 2 | 1:16 |  |  |  | 0.14444
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Angul- MCL Ckt-I | FEEDER | 7 | 58:16 | 2 | 1:02 | 4 | 3:02 | [5 empty] | 1900-01-01 14:20
(ii) | 132KV Angul- MCL Ckt-II | FEEDER | 6 | 27:46 | 1 | 1:14 | 2 | 1:55 | [5 empty] | 1899-12-31 06:55
(iii) | 132KV Angul- Chainpal | FEEDER | 6 | 7:18 | 2 | 0:13 | 4 | 2:29 | [5 empty] | 0.41667
(iv) | 132KV Angul- TTPS | FEEDER | 3 | 15:17 | 1 | 0:20 | 3 | 3:09 | [5 empty] | 0.78194
132/33KV Grid S/s Boinda
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 1 | 0:22 | 1 | 1:05 | 0 | 0:00 |  |  |  | 0.060417
(ii) | 12.5 MVA Transformer-II | POWER | 1 | 0:19 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.013194
(iii) | 12.5 MVA Transformer-III | POWER | 1 | 0:19 | 0 | 0:00 | 2 | 0:49 |  |  |  | 0.047222
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Angul-Boinda | FEEDER | 2 | 16:19 | 0 | 0:00 | 6 | 1:45 | [5 empty] | 0.75278
(ii) | 132 kV RTSS Boinda | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kV GRID S/s Chainpal
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-1 | POWER | 0 | 0:00 | 2 | 1:12 | 6 | 4:02 |  |  |  | 0.21806
(ii) | 40 MVA Transformer-2 | POWER | 1 | 3:29 | 2 | 2:06 | 6 | 4:56 |  |  |  | 0.43819
(iii) | 20 MVA Transformer-3 | POWER | 0 | 0:00 | 2 | 1:09 | 5 | 2:53 |  |  |  | 0.16806
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV TTPS - Chainpal Ckt - I | FEEDER | 0 | 0:00 | 0 | 0:00 | 3 | 9:03 | [5 empty] | 0.37708
(ii) | 132 kV TTPS - Chainpal Ckt- II | FEEDER | 9 | 10:14 | 2 | 1:19 | 3 | 18:18 | [5 empty] | 1899-12-31 05:51
(iii) | 132 KV Chainpal-Global-TFL Feeder | FEEDER | 3 | 3:19 | 1 | 0:27 | 4 | 2:44 | [5 empty] | 0.27083
(iv) | 132 kV Chainpal - Meramundali Ckt-I | FEEDER | 1 | 0:18 | 3 | 0:32 | 1 | 2:14 | [5 empty] | 0.12778
(v) | 132 kV Chainpal - Meramundali Ckt-II | FEEDER | 1 | 0:18 | 2 | 0:21 | 2 | 2:12 | [5 empty] | 0.11875
(vi) | 132 kV Chainpali-RTSS Talcher | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 1:21 | [5 empty] | 0.05625
220/33kV Grid S/s, Rengali
1 | Power Transformer | POWER
(i) | 20 MVA Transformer I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
(i) | 220 kV BUS-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 220 kV BUS-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
3 | EHT Feeder Fault | FEEDER
(i) | 220KV Rengali-PGCIL Ckt-I | FEEDER | 7 | 14:10 | 1 | 0:45 | 3 | 27:54 | [5 empty] | 1899-12-31 18:49
(ii) | 220KV Rengali-PGCIL Ckt-II | FEEDER | 1 | 1:39 | 1 | 0:45 | 1 | 1:00 | [5 empty] | 0.14167
(iii) | 220KV Rengali- Rengali PH Ckt-I | FEEDER | 0 | 0:00 | 7 | 39:01 | 2 | 2:37 | [5 empty] | 1899-12-31 17:38
(iv) | 220KV Rengali- Rengali PH Ckt-II | FEEDER | 0 | 0:00 | 2 | 1:40 | 1 | 1:07 | [5 empty] | 0.11597
132/33KV Grid s/s Dhenkanal
1 | Power Transformer | POWER
(i) | 40MVA Transformer I | POWER | 4 | 0:59 | 0 | 0:00 | 4 | 1:58 |  |  |  | 0.12292
(ii) | 40MVA Transformer II | POWER | 1 | 1:18 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.054167
(iii) | 40MVA Transformer III | POWER | 1 | 0:08 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0055556
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Meramundali-Dhenkanal | FEEDER | 1 | 53:36 | 2 | 0:58 | 3 | 2:34 | [5 empty] | 1900-01-01 09:08
(ii) | 132KV Dhenkanal-Khuntuni | FEEDER | 7 | 15:01 | 4 | 1:18 | 4 | 50:13 | [5 empty] | 1900-01-01 18:32
(iii) | 132KV Dhenkanal-Khajuriakata-Nuapatna T Line | FEEDER | 9 | 6:29 | 3 | 0:48 | 8 | 1:24 | [5 empty] | 0.36181
(iv) | 132KV Dhenkanal- RTSS Joranda | FEEDER | 5 | 2:31 | 5 | 5:29 | 4 | 1:08 | [5 empty] | 0.38056
132/33 kV Grid S/S, Kalarangi
1 | Power Transformer | POWER
(i) | 12.5 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 12.5 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 20 MVA Power Transformer - III | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Goda- Kalarangi | FEEDER | 0 | 0 | 1 | 2:42 | 1 | 1:03 | [5 empty] | 0.15625
(ii) | 132kV Kalarangi - Duburi | FEEDER | 3 | 2:56 | 3 | 4:34 | 2 | 2:16 | [5 empty] | 0.40694
132/33KV Grid S/s KamakhyaNagar
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 1 | 0:13 | 1 | 0:16 |  |  |  | 0.020139
(ii) | 12.5 MVA Transformer-II | POWER | 2 | 11:16 | 0 | 0:00 | 1 | 0:18 |  |  |  | 0.48194
(iii) | 12.5 MVA Transformer-III | POWER | 3 | 7:06 | 0 | 0:00 | 1 | 0:18 |  |  |  | 0.30833
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV OPCL - Kamakhyanagar | FEEDER | 3 | 1:22 | 1 | 0:23 | 3 | 3:10 | [5 empty] | 0.20486
(ii) | 132kV Kamakhyanagar - Goda | FEEDER | 2 | 0:58 | 3 | 3:39 | 5 | 1:54 | [5 empty] | 0.27153
(iii) | 132kV Kamakhyanagar-RTSS Kamakhyanagar | FEEDER | 2 | 1:37 | 4 | 1:09 | 0 | 0:00 | [5 empty] | 0.11528
132/33KV Grid S/s Khajuriakata
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 5 | 1:13 |  |  |  | 0.050694
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 0:23 |  |  |  | 0.015972
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kv Meramundali-KhajuriaKata | FEEDER | 3 | 16:37 | 3 | 6:44 | 5 | 31:00 | [5 empty] | 1900-01-01 06:21
(ii) | 132kv KhajuriaKata-Nuapatna | FEEDER | 16 | 8:17 | 2 | 0:35 | 13 | 2:32 | [5 empty] | 0.475
| 132/33 kV Grid S/s, Kharagprasad | FEEDER
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 7 | 40:29 | 3 | 10:28 |  |  |  | 1900-01-01 02:57
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Kharagprasad-NBVL Ckt-I | FEEDER | 1 | 0:47 | 5 | 25:58 | 5 | 15:15 | [5 empty] | 1899-12-31 18:00
(ii) | 132KV Kharagprasad-NBVL Ckt-II | FEEDER | 0 | 0:00 | 3 | 24:12 | 3 | 15:33 | [5 empty] | 1899-12-31 15:45
(iii) | 132KV Kharagprasad-Meramundali Ckt-I | FEEDER | 0 | 0:00 | 3 | 24:09 | 1 | 3:24 | [5 empty] | 1899-12-31 03:33
(iv) | 132KV Kharagprasad-Meramundali Ckt-II | FEEDER | 1 | 4:26 | 3 | 23:54 | 2 | 16:23 | [5 empty] | 1899-12-31 20:43
(v) | 132KV Kharagprasad- Meramundali RTSS | FEEDER | 0 | 0:00 | 3 | 24:07 | 3 | 50:07 | [5 empty] | 1900-01-02 02:14
(vi) | 132KV Kharagprasad-MGM | FEEDER | 3 | 28:06 | 4 | 42:32 | 3 | 8:45 | [5 empty] | 1900-01-02 07:23
(vii) | 132KV Kharagprasad-SGEL | FEEDER | 4 | 2:11 | 4 | 42:19 | 3 | 7:45 | [5 empty] | 1900-01-01 04:15
220/132/33kV GRID S/s Goda
1 | Auto Transformer | AUTO
(i) | 160MVA AUTO-I | AUTO | 2 | 2:57 | 0 | 0:00 | 0 | 0:00 |  |  | 0.12292
(ii) | 160MVA AUTO-II | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER |  |  | 1 | 0:13 | 1 | 0:12 |  |  |  | 0.017361
(ii) | 40 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
3 | Bus Fault | BUS | 1 | 0:43 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0.029861
4 | EHT Feeder Fault | FEEDER
(i) | 220 KV Goda- Meramundali (B) | FEEDER | 8 | 27:06 | 0 | 0:00 | 2 | 4:07 | [5 empty] | 1899-12-31 07:13
(ii) | 220 KV Goda- Duburi | FEEDER | 3 | 1:53 | 1 | 0:55 | 1 | 20:18 | [5 empty] | 0.9625
| 132/33 kV Grid S/s, Gondia | FEEDER
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV TTPS- Gondia | FEEDER | 18 | 16:03 | 14 | 5:35 | 18 | 12:46 | [5 empty] | 1899-12-31 10:24
(ii) | 132KV Gondia- Jabamayee Ferro Alloys | FEEDER | 13 | 4:36 | 3 | 4:40 | 9 | 336:00 | [5 empty] | 1900-01-13 09:16
400/220/132kV Grid S/S, Meramundali
1 | ICT | ICT
(i) | 315 MVA ICT-1 | ICT | 1 | 0:21 | 1 | 3:02 | 0 | 0:00 |  | 0.14097
(ii) | 315 MVA ICT-2 | ICT | 1 | 1:55 | 0 | 0:00 | 0 | 0:00 |  | 0.079861
2 | Auto Transformer | AUTO
(i) | 100MVA Auto 1 | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
(ii) | 100MVA Auto 2 | AUTO | 1 | 12:59 | 0 | 0:00 | 5 | 20:08 |  |  | 1899-12-31 09:07
(iii) | 100MVA Auto 3 | AUTO | 1 | 1:49 | 0 | 0:00 | 0 | 0:00 |  |  | 0.075694
3 | Bus fault | BUS | [10 empty] | 0
(i) | 400KV Bus-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 400KV Bus-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | Bus fault | BUS
(i) | 220KV Bus- I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(i) | 220KV Bus- II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
5 | Bus fault | BUS
(i) | 132KV Bus- I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
6 | EHT Feeder Fault | FEEDER
(i) | 400 KV Meramundali- New Duburi Ckt- I | FEEDER | 1 | 251:30 | 1 | 7:23 | 18 | 111:43 | [5 empty] | 1900-01-14 10:36
(ii) | 400 KV Meramundali- New Duburi Ckt- II | FEEDER | 3 | 279:18 | 2 | 0:31 | 13 | 46:24 | [5 empty] | 1900-01-12 14:13
(iii) | 400 KV Meramundali- Bolangir PG | FEEDER | 1 | 4:23 | 0 | 0:00 | 3 | 1:43 | [5 empty] | 0.25417
(iv) | 400 KV Meramundali- Kaniha Ckt- II | FEEDER | 3 | 5:04 | 2 | 10:02 | 2 | 19:08 | [5 empty] | 1899-12-31 10:14
(v) | 400 KV Meramundali- Kaniha Ckt- I | FEEDER | 1 | 2:47 | 1 | 5:38 | 1 | 3:35 | [5 empty] | 0.5
(vi) | 400 KV Meramundali- Meramundali (B) | FEEDER | 2 | 4:13 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.17569
(vii) | 400 KV Meramundali-JSPLCkt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 8:40 | [5 empty] | 0.36111
(viii) | 400 KV Meramundali-JSPLCkt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(ix) | 220 KV Meramundali- Kaniha Ckt- I | FEEDER | 2 | 57:52 | 0 | 0:00 | 1 | 1:22 | [5 empty] | 1900-01-01 11:14
(x) | 220 KV Meramundali- Kaniha Ckt- II | FEEDER | 2 | 4:16 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.17778
(xi) | 220 KV Meramundali-TTPS Ckt-I | FEEDER | 2 | 6:50 | 1 | 1:21 | 0 | 0:00 | [5 empty] | 0.34097
(xi) | 220 KV Meramundali-TTPS Ckt-II | FEEDER | 4 | 27:01 | 1 | 1:21 | 1 | 3:43 | [5 empty] | 1899-12-31 08:05
(xii) | 220 KV Meramundali- NALCO Ckt-I | FEEDER | 1 | 0:57 | 0 | 0:00 | 1 | 2:44 | [5 empty] | 0.15347
(xiii) | 220 KV Meramundali- NALCO Ckt-II | FEEDER | 1 | 1:35 | 0 | 0:00 | 1 | 3:14 | [5 empty] | 0.20069
(xiv) | 220 KV Meramundali- Meramundali (B) (previuosly Goda) | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xv) | 220 KV Meramundali- Meramundali (B) (previuosly Duburi) | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xvi) | 220 KV Meramundali- Narsinghpur | FEEDER | 3 | 8:48 | 2 | 21:50 | 1 | 2:33 | [5 empty] | 1899-12-31 09:11
(xvii) | 220 KV Meramundali- TATA BSL Ckt- I | FEEDER | 1 | 4:57 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.20625
(xviii) | 220 KV Meramundali- TATA BSL Ckt- II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xix) | 132 KV Meramundali- BRG | FEEDER | 3 | 7:13 | 10 | 2:28 | 1 | 1:26 | [5 empty] | 0.46319
(xx) | 132 KV Meramundali- RML FAD | FEEDER | 2 | 6:39 | 1 | 0:05 | 0 | 0:00 | [5 empty] | 0.28056
(xxi) | 132 KV Meramundali- RML DSP | FEEDER | 1 | 0:09 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.00625
400/220/132kV Grid S/S, Meramundali (B)
1 | ICT | ICT
(i) | 500 MVA ICT-1 | ICT | 1 | 0:21 | 0 | 0:00 | 1 | 1:27 |  | 0.075
(ii) | 500 MVA ICT-2 | ICT | 1 | 1:55 | 1 | 10:01 | 2 | 5:32 |  | 0.72778
2 | Bus fault | BUS | [10 empty] | 0
3 | EHT Feeder Fault | FEEDER
(i) | 400 KV Meramundali (B)- GMR | FEEDER | 1 | 24:10 | 0 | 0:00 | 1 | 2:15 | [5 empty] | 1899-12-31 02:25
(ii) | 400 KV Meramundali (B)- Duburi | FEEDER | 4 | 9:03 | 0 | 0:00 | 3 | 3:15 | [5 empty] | 0.5125
|  |  |  | 1900-02-14 10:20 |  | 1900-01-15 20:28 |  | 1900-02-07 02:47 |  | 1899-12-31 00:34 | 1899-12-31 13:53 | 1900-01-03 17:04 | 0.029861 | 1900-04-04 01:21 | 1900-04-11 09:35
| Total |  |  |  | 1900-04-11 09:35 |  |  |  |  | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
ICT = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
ICT = SUM(K5:[ICT, row above])
Duration of Trippings (Hr:Mn) = SUM(E5:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G5:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I5:[FORM P-3, row above])
No. of Trippings = [Duration of Trippings (Hr:Mn), row above]+[Duration of Trippings (Hr:Mn), row above]+[FORM P-3, row above]

## P-3 Cuttack
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Cuttack Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33KV Grid S/s Choudwar
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-2 | POWER | 0 | 0:00 | 2 | 1:37 | 2 | 1:31 |  |  |  | 0.13056
(ii) | 20 MVA Transformer-3 | POWER | 1 | 1:25 | 2 | 1:29 | 1 | 1:35 |  |  |  | 0.18681
(iii) | 40 MVA Transformer-4 | POWER | 1 | 12:28 | 0 | 0:00 | 1 | 8:02 |  |  |  | 0.85417
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Choudwar-ICCL | FEEDER | 3 | 1:10 | 0 | 0:00 | 1 | 5:11 | [5 empty] | 0.26458
(ii) | 132KV Choudwar-TS Alloys |  | 7 | 16:25 | 2 | 0:32 | 9 | 12:16 | [5 empty] | 1899-12-31 05:13
(iii) | Choudwar-Kendrapara Road RTSS |  | 3 | 0:26 | 2 | 0:13 | 0 | 1:09 | [5 empty] | 0.075
(iv) | 132KV Choudwar-Bidanasi |  | 5 | 4:28 | 3 | 0:16 | 11 | 37:20 | [5 empty] | 1899-12-31 18:04
(v) | 132KV TS Alloys-Ultratech |  | 0 | 0:00 | 2 | 0:00 | 5 | 15:01 | [5 empty] | 0.62569
(vi) | 132KV Aarti-Ultratech |  | 1 | 0:22 | 0 | 0:00 | 3 | 1:46 | [5 empty] | 0.088889
(vii) | 132KV Aarti-Nuapatna |  | 2 | 25:15 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 1899-12-31 01:15
(viii) | 132KV TS Alloys-Aarti |  | 11 | 24:26 | [9 empty] | 1899-12-31 00:26
(ix) | 132 KV ICCL-Khuntuni |  | 7 | 3:03 | 1 | 0:04 | 3 | 33:12 | [5 empty] | 1899-12-31 12:19
(x) | 132 KV Brajabiharipur -BPPL |  | 3 | 4:04 | 2 | 1:58 | 3 | 2:11 | [5 empty] | 0.34236
132/33KV Grid S/s Mania
1 | Power Transformer | POWER | 1 | 0:33 | 0 | 0:00 | 2 | 1:02 |  |  |  | 0.065972
(i) | 12.5 MVA Transformer-1 | POWER | [9 empty] | 0
(ii) | 20 MVA Transformer-2 | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | ICCL-Mania Feeder-I | FEEDER | 2 | 5:56 | 3 | 10:43 | 0 | 0:00 | [5 empty] | 0.69375
(ii) | Mania-OCL Feeder-II | FEEDER | 1 | 0:21 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.014583
132/33KV Grid S/s Nuapatna
1 | Power Transformer | POWER | 4 | 9:51 | 11 | 7:18 | 16 | 2:57 |  |  |  | 0.8375
(i) | 20 MVA Transformer-I | POWER
(ii) | 40 MVA Transformer-II | POWER
(iii) | 12.5 MVA Transformer-III | POWER
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | [11 empty] | 0
132/33KV Grid S/s Salipur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-II | POWER | 1 | 28:37 | 0 | 0:00 | 0 | 0:00 |  |  |  | 1899-12-31 04:37
(iii) | 20 MVA Transformer-III | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV ICCL-Salipur | FEEDER | 9 | 74:30 | 1 | 20:24 | 1 | 1:03 | [5 empty] | 1900-01-02 23:57
(ii) | 132 KV OCL-Salipur | FEEDER | 8 | 30:56 | 0 | 0:00 | 1 | 17:06 | [5 empty] | 1900-01-01 00:02
(iii) | 132 KV Kendrapada-Salipur | FEEDER | 3 | 42:13 | 1 | 0:21 | 1 | 0:35 | [5 empty] | 1899-12-31 19:09
132/33KV Grid S/s Khuntuni
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:32 |  |  |  | 0.022222
(ii) | 40 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Khuntuni-ICCL | FEEDER | 0 | 0:00 | 2 | 0:24 | 4 | 1:19 | [5 empty] | 0.071528
(i) | 132 kV Khuntuni-Shree Cement | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
220/33KV Grid S/s Narasinghpur
1 | Power Transformer | POWER | 1 | 86:05 | 1 | 0:22 | 1 | 13:42 |  |  |  | 1900-01-03 04:09
(i) | 40 MVA Transformer-I | POWER | [9 empty] | 0
(ii) | 20 MVA Transformer-II | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER | 8 | 11:27 | 3 | 25:36 | 3 | 3:19 | [5 empty] | 1899-12-31 16:22
220/132/33kV GRID S/s Bidanasi
1 | Auto Transformer | AUTO
(i) | 100MVA Auto-I | AUTO | 2 | 3:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0.125
(ii) | 100MVA Auto-II | AUTO | [6 empty] | Under B/D since 05.10.2022 |  | 0
(iii) | 160MVA Auto-III | AUTO | 1 | 0:21 | 0 | 0:00 | 0 | 0:00 |  |  | 0.014583
2 | Power Transformer | POWER
(i) | 63 MVA Transformer-I | POWER | 1 | 0:03 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0020833
(ii) | 63 MVA Transformer-II | POWER | 2 | 0:05 | 1 | 0:08 | 0 | 0:00 |  |  |  | 0.0090278
(iii) | 40 MVA Transformer-III | POWER | 2 | 0:05 | 3 | 0:14 | 1 | 0:27 |  |  |  | 0.031944
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220 kV Mendhasal-Bidanasi Ckt-I | FEEDER | 2 | 1:43 | 0 | 0:00 | 4 | 29:19 | [5 empty] | 1899-12-31 07:02
(ii) | 220 kV Mendhasal-Bidanasi Ckt-II | FEEDER | 5 | 9:37 | 1 | 0:22 | 2 | 2:24 | [5 empty] | 0.51597
(iii) | 132 kV Bidanasi-Chowdwar | FEEDER | 2 | 2:13 | 3 | 0:18 | 4 | 158:21 | [5 empty] | 1900-01-05 16:52
220/132/33KV Grid S/s Cuttack
1 | Auto Transformer | AUTO
(i) | 160MVA Auto - I | AUTO | 1 | 2:41 | 1 | 22:09 | 0 | 0:00 |  |  | 1899-12-31 00:50
(ii) | 100MVA Auto - II | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 3 | 0:45 | 2 | 0:06 | 1 | 0:12 |  |  |  | 0.04375
(ii) | 40 MVA Transformer-II | POWER | 3 | 0:46 | 1 | 0:04 | 1 | 0:15 |  |  |  | 0.045139
(iii) | 40 MVA Transformer-III | POWER | 2 | 0:33 | 1 | 0:28 | 2 | 1:15 |  |  |  | 0.094444
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 220 kV Bidanasi-Cuttack-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 3:28 | [5 empty] | 0.14444
(ii) | 220 KV Bidanasi-Cuttack-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(iii) | 132 KV Cuttack- Phulnakhara | FEEDER | 4 | 19:41 | 1 | 0:08 | 1 | 7:56 | [5 empty] | 1899-12-31 03:45
(iv) | 132 KV Cuttack – Jagatsinghpur | FEEDER | 7 | 9:21 | 4 | 21:18 | 1 | 0:33 | [5 empty] | 1899-12-31 07:12
132/33KV Grid S/s Jagatsinghpur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 1 | 0:14 | 1 | 0:04 | 2 | 0:34 |  |  |  | 0.036111
(ii) | 20 MVA Transformer-II | POWER | 1 | 0:14 | 1 | 0:04 | 3 | 0:53 | 20 MVA TRF-II was replaced by 40 MVA TRF-II on 24.07.2024. |  |  | 0.049306
(ii) | 40 MVA Transformer-II | POWER |  |  |  |  | 1 | 10:00 |  |  |  | 0.41667
(iii) | 40 MVA Transformer-III | POWER | 1 | 0:14 | 1 | 0:04 | 1 | 10:00 |  |  |  | 0.42917
2 | Bus Fault | BUS | [10 empty] | 0:00
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Tirtol-Jagatsinghpur Line | FEEDER | 6 | 6:41 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.27847
(ii) | 132KV Jagatsinghpur-Gorekhnath Line | FEEDER | 1 | 0:30 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.020833
220/33KV Grid S/s Godisahi
1 | Power Transformer | POWER
(i) | 63 MVA Transformer-I | POWER | 3 | 12:27 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.51875
(ii) | 63 MVA Transformer-II | POWER | 3 | 12:27 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.51875
2 | Bus Fault | BUS | [10 empty] | 0:00
3 | EHT Feeder Fault | FEEDER
132/33KV Grid S/s Phulanakhara
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | 20 MVA TRF-I was replaced by 40 MVA on 31.07.2024 |  |  | 0
(i) | 40 MVA Transformer-I | POWER |  |  |  |  | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 1 | 0:16 | 1 | 0:31 |  |  |  | 0.032639
(iii) | 40 MVA Transformer-III | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Bhubaneswar-Phulnakhara | FEEDER | 4 | 3:51 | 1 | 0:17 | 3 | 2:43 | [5 empty] | 0.28542
132/33KV Grid S/s Brajbiharipur
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 0 | 0:00 | 1 | 1:46 | 0 | 0:00 |  |  |  | 0.073611
(ii) | 40 MVA Transformer-II | POWER | 2 | 4:50 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.20139
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Bidanasi- Brajabiharipur | FEEDER | 1 | 3:05 | 0 | 0:00 | 1 | 13:09 | [5 empty] | 0.67639
(ii) | 132KV Brajabiharipur- BPPL | FEEDER | 3 | 4:04 | 2 | 22:00 | 3 | 2:11 | [5 empty] | 1899-12-31 04:15
132/33KV Grid S/s Chandikhole
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 8 | 1:59 | 5 | 0:46 | 35 | 4:13 |  |  |  | 0.29028
(ii) | 20 MVA Transformer-II | POWER | 8 | 1:43 | 4 | 0:34 | 40 | 6:44 |  |  |  | 0.37569
(iii) | 20 MVA Transformer-III | POWER | 7 | 1:13 | 4 | 0:34 | 32 | 5:02 |  |  |  | 0.28403
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER | [11 empty] | 0
132/33KV Grid S/s Kendrapara
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-II | POWER | 1 | 0:30 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.020833
(ii) | 40 MVA Transformer- IV | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Kendrapara-Marshaghai | FEEDER | 3 | 0:42 | 5 | 8:50 | 4 | 5:27 | [5 empty] | 0.62431
(ii) | 132 kV Kendrapara-M/S RAMCO | FEEDER | 8 | 13:38 | 5 | 9:58 | 4 | 2:40 | [5 empty] | 1899-12-31 02:16
(iii) | 132 kV Kendrapara-Chandikhole | FEEDER | 6 | 11:01 | 4 | 41:27 | 3 | 36:04 | [5 empty] | 1900-01-02 16:32
(iv) | 132 kV Kendrapara-Pattamundai | FEEDER | 4 | 1:42 | 4 | 1:57 | 4 | 3:11 | [5 empty] | 0.28472
132/33KV Grid S/s Marshaghai
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 1 | 1:08 | 0 | 0:00 | 2 | 0:34 |  |  |  | 0.070833
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:38 |  |  |  | 0.026389
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV RTSS Kendrapada | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Olavar
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 1 | 0:27 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.01875
(ii) | 12.5 MVA Transformer-II | POWER | 1 | 0:24 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.016667
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Olaver-Chandabali Ckt-I fdr | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(ii) | 132KV Olaver-Chandabali Ckt-II fdr | FEEDER | 1 | 0:35 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.024306
132/33KV Grid S/s Tirtol
1 | Power Transformer | POWER | 1 | 11:35 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.48264
(i) | 40 MVA Transformer-I | POWER
(ii) | 40 MVA Transformer-II | POWER
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Tirtol-Jagatsinghpur Fdr | FEEDER | 2 | 4:15 | 0 | 0:00 | 1 | 0:07 | [5 empty] | 0.18194
220/132/33kV GRID S/s Paradeep
1 | Auto Transformer | AUTO
(i) | 100MVA Auto-I | AUTO | 0 | 0:00 | 0 | 0:00 | 2 | 4:34 |  |  | 0.19028
(ii) | 160MVA Auto-II | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 0:18 |  |  | 0.0125
(iii) | 160MVA Auto-III | AUTO | 1 | 19:23 | 0 | 0:00 | 1 | 0:24 |  |  | 0.82431
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 1 | 0:21 | 0 | 0:00 |  |  |  | 0.014583
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 20 MVA Transformer-III | POWER | [6 empty] | DEAD |  |  | 0
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220kV New Duburi-Paradeep ckt-I | FEEDER | 6 | 2:17 | 5 | 6:53 | 7 | 8:56 | [5 empty] | 0.75417
(ii) | 220kV New Duburi-Paradeep ckt-II | FEEDER | 2 | 1:34 | 2 | 2:00 | 5 | 5:48 | [5 empty] | 0.39028
(iii) | 220kV Paradeep- IOCL | FEEDER | 1 | 1:26 | 0 | 0:00 | 1 | 0:18 | [5 empty] | 0.072222
(iv) | 220kV Paradeep- ESSAR ckt- I | FEEDER | 3 | 1:16 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.052778
(v) | 220kV Paradeep- ESSAR ckt- II | FEEDER | 2 | 0:29 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.020139
(vi) | 132KV Paradeep- PPT ckt-I | FEEDER | 0 | 0:00 | 1 | 10:50 | 0 | 0:00 | [5 empty] | 0.45139
(vii) | 132KV Paradeep- PPT ckt-II | FEEDER | 1 | 3:15 | 5 | 5:00 | 0 | 0:00 | [5 empty] | 0.34375
(viii) | 132KV Paradeep- PPL ckt-I | FEEDER | 0 | 0:00 | 7 | 21:15 | 1 | 0:08 | [5 empty] | 0.89097
(ix) | 132KV Paradeep- PPL ckt-II | FEEDER | 0 | 0:00 | 6 | 21:05 | 3 | 13:15 | [5 empty] | 1899-12-31 10:20
(x) | 132KV Paradeep- IFFCO ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 6 | 4:19 | [5 empty] | 0.17986
(xi) | 132KV Paradeep- IFFCO ckt-II | FEEDER | 1 | 0:52 | 0 | 0:00 | 2 | 3:19 | [5 empty] | 0.17431
(xii) | 132KV Paradeep- Marshaghai | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(xiii) | 132KV Paradeep- Kendrapara ckt-II | FEEDER | 2 | 1:25 | 0 | 0:00 | 4 | 5:13 | [5 empty] | 0.27639
(xiv) | 132KV Paradeep- Tirtol | FEEDER | 1 | 0:08 | 1 | 0:20 | 1 | 0:19 | [5 empty] | 0.032639
(xv) | 132KV Paradeep- RTSS Siju | FEEDER | 3 | 1:35 | 1 | 0:11 | 0 | 0:00 | [5 empty] | 0.073611
132/33KV Grid S/s Rajnagar
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 3 | 3:00 | 3 | 1:58 | 1 | 0:16 |  |  |  | 0.21806
(ii) | 20 MVA Transformer-II | POWER | 1 | 0:32 | 3 | 15:51 | 1 | 13:47 |  |  |  | 1899-12-31 06:10
2 | Bus Fault | BUS | [10 empty] | 0:00
3 | EHT Feeder fault | FEEDER
132/33KV Grid S/s Pattamundai
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 1 | 0:12 | 1 | 0:11 | 1 | 0:10 |  |  |  | 0.022917
(ii) | 20 MVA Transformer-II | POWER | 1 | 0:12 | 1 | 106:00 | 1 | 0:10 |  |  |  | 1900-01-03 10:22
(iii) | 20 MVA Transformer-III | POWER | 1 | 0:12 | 1 | 0:10 | 1 | 0:10 |  |  |  | 0.022222
2 | Bus Fault | BUS | [10 empty] | 0:00
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Pattamundai- Olaver Ckt I | FEEDER | 0 | 0:00 | 2 | 5:33 | 1 | 15:47 | [5 empty] | 0.88889
(ii) | 132 KV Pattamundai- Olaver Ckt II | FEEDER | 0 | 0:00 | 1 | 5:00 | 0 | 0:00 | [5 empty] | 0.20833
(iii) | 132 KV Pattamundai- Rajnagar Ckt- I | FEEDER | 0 | 0:00 | 2 | 2:50 | 1 | 0:50 | [5 empty] | 0.15278
(iv) | 132 KV Pattamundai- Rajnagar Ckt- II | FEEDER | 0 | 0:00 | 1 | 2:26 | 1 | 0:44 | [5 empty] | 0.13194
|  |  |  | 1900-01-22 20:12 |  | 1900-01-16 05:03 |  | 1900-01-21 20:25 |  | 0 | 1900-01-01 04:50 | 1900-01-16 12:26 | 0 | 1900-02-12 04:24 | 1900-03-03 21:40
| Total |  |  |  | 1900-03-03 21:40 |  |  |  |  | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = [Duration of Trippings (Hr:Mn)]+[FORM P-3]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = SUM(O4:[EHT Feeder Fault, row above])
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Auto Trf = SUM(L4:[Auto Trf, row above])
Duration of Trippings (Hr:Mn) = SUM(E4:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G4:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I4:[FORM P-3, row above])
ICT = SUM(K4:[ICT, row above])
Bus Fault = SUM(N4:[Bus Fault, row above])
No. of Trippings = [Duration of Trippings (Hr:Mn), row above]+[Duration of Trippings (Hr:Mn), row above]+[FORM P-3, row above]

## P-3 Jajpur Road
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Jajpur Road Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
132/33 kV Grid S/S, Anandpur
1 | Power Transformer | POWER
(i) | 12.5 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 2:32 |  |  |  | 0.10556
(ii) | 12.5 MVA Power Transformer - II | POWER | 1 | 18:10 | 1 | 13:20 | 1 | 1:26 |  |  |  | 1899-12-31 08:56
(iii) | 20 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 5:58 |  |  |  | 0.24861
2 | Bus fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Jajpur Road-Anandpur ckt-I | FEEDER | 6 | 3:47 | 4 | 1:22 | 1 | 0:46 | [5 empty] | 0.24653
(ii) | 132 KV Jajpur Road-Anandpur ckt-II | FEEDER | 2 | 1:49 | 4 | 1:36 | 2 | 1:50 | [5 empty] | 0.21875
220/132/33 kV Grid S/S, Duburi
1 | Auto Transformer | AUTO
(i) | 160 MVA Auto Transformer - I | AUTO | 1 | 2:00 | 1 | 1:54 | 0 | 0:00 |  |  | 0.1625
(ii) | 160 MVA Auto Transformer - II | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 4:18 | Upgradation of Auto transformer - II from 100MVA to 160MVA continued from date 27.07.21 to Dt:- 03.10.2022 |  | 0.17917
(iii) | 100 MVA Auto Transformer - III | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 9:57 |  |  | 0.41458
2 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 2 | 0:19 | 0 | 0:00 | 6 | 9:37 |  |  |  | 0.41389
(ii) | 40 MVA Power Transformer - II | POWER | [6 empty] | SHUTDOWN FROM 12.12.2022 |  |  | 0
3 | Bus fault (220 KV) | BUS
4 | Bus fault (132 KV) | BUS
5 | EHT Feeder Fault | FEEDER
(i) | 220 KV Duburi- New Duburi Ckt-I | FEEDER | 1 | 1:29 | 0 | 0:00 | 2 | 8:25 | [5 empty] | 0.4125
(ii) | 220 KV Duburi- New Duburi Ckt-II | FEEDER | 1 | 3:23 | 0 | 0:00 | 1 | 1:38 | [5 empty] | 0.20903
(iii) | 220 KV Duburi- NINL | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(iv) | 132 KV Duburi- Jabamayee Ferro Alloys | FEEDER | 1 | 3:00 | 0 | 0:00 | 3 | 3:39 | [5 empty] | 0.27708
(v) | 132 KV Duburi- RTSS Jakhapura | FEEDER | 4 | 0:45 | 3 | 0:54 | 4 | 9:03 | [5 empty] | 0.44583
(vi) | 132 KV Duburi- BRPL | FEEDER | 1 | 2:13 | 3 | 34:36 | 0 | 0:00 | [5 empty] | 1899-12-31 12:49
(vii) | 132 KV Duburi- Mishrilal | FEEDER | 0 | 0:00 | 0 | 0:00 | 3 | 4:30 | [5 empty] | 0.1875
(viii) | 132 KV Duburi- BC Mohanty | FEEDER | 2 | 2:01 | 1 | 8:29 | 1 | 1:07 | [5 empty] | 0.48403
(ix) | 132 KV Duburi- JSW | FEEDER | 0 | 0:00 | 1 | 0:31 | 0 | 0:00 | [5 empty] | 0.021528
132/33 kV Grid S/S, Jajpur Road
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 0 | 0:00 | 1 | 0:10 | 2 | 4:37 |  |  |  | 0.19931
(ii) | 40 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 40 MVA Power Transformer - III | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
(i) | 132 kV BUS-I | BUS | 1 | 0:29 | 0 | 0:00 | 1 | 0:57 |  |  |  |  | 0.059722
(ii) | 132 kV BUS-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Jajpur Road-Chandikhole | FEEDER | 12 | 33:17 | 1 | 10:44 | 2 | 1:48 | [5 empty] | 1899-12-31 21:49
(ii) | 132kV Jajpur Road-Kendrapara | FEEDER | 11 | 24:52 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 1899-12-31 00:52
132/33 kV Grid S/S, Jajpur Town
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 2 | 0:18 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0125
(ii) | 20 MVA Power Transformer - II | POWER | 1 | 0:19 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.013194
(iii) | 40 MVAPower Transformer - III | POWER | 1 | 0:23 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.015972
2 | Bus fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Jajpur Road-Jajpur Town |  | 6 | 17:31 | 1 | 4:42 | 7 | 12:03 | [5 empty] | 1899-12-31 10:16
132 kV Switching S/S, BC Mohanty
1 | Auto Transformer | AUTO
2 | Power Transformer | POWER
3 | Bus fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 132KV BC Mohanty- Daitari | FEEDER | 3 | 10:18 | 0 | 0:00 | 1 | 4:57 | [5 empty] | 0.63542
(ii) | 132KV BC Mohanty- RTSS Tomka | FEEDER | 3 | 1:00 | 2 | 0:10 | 1 | 0:31 | [5 empty] | 0.070139
400/220/33 kV Grid S/S, New Duburi
1 | ICT | ICT
| ICT-I | ICT | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  | 0
| ICT-II | ICT | 0 | 0:00 | 1 | 13:31 | 0 | 0:00 |  | 0.56319
2 | Power Transformers | POWER
(i) | 20 MVA Power Transformer - I | POWER | 0 | 0:00 | 1 | 1:18 | 0 | 0:00 |  |  |  | 0.054167
3 | Bus Fault |  | 0 | 0:00 | 0 | 0:00 | 1 | 20:24 |  |  |  |  | 0.85
4 | EHT Feeder Fault | FEEDER
(i) | 400 KV New Duburi- Baripada PG | FEEDER | 2 | 0:39 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.027083
(ii) | 400 KV New Duburi- Pandiabil PG | FEEDER | 2 | 3:59 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.16597
(iii) | 400 KV New Duburi- Tata Steel ckt-I | FEEDER | 1 | 0:59 | 2 | 5:16 | 0 | 0:00 | [5 empty] | 0.26042
(iv) | 400 KV New Duburi- Tata Steel ckt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(v) | 220 KV New Duburi- Jindal Ckt-I | FEEDER | 0 | 0:00 | 1 | 7:31 | 3 | 16:07 | [5 empty] | 0.98472
(vi) | 220 KV New Duburi- Jindal Ckt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 203:45 | [5 empty] | 1900-01-07 11:45
(vii) | 220 KV New Duburi- Rohit | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(viii) | 220 KV New Duburi- VISA | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 2:51 | [5 empty] | 0.11875
(ix) | 220 KV New Duburi- Maithan | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 1:27 | [5 empty] | 0.060417
(x) | 220 KV New Duburi- Emami Cement | FEEDER | 1 | 3:03 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.12708
220/132/33 kV Grid S/S, Balasore
1 | Auto Transformer | AUTO
(i) | 160 MVA Auto- I | AUTO | 0 | 0:00 | 2 | 6:40 | 0 | 0:00 |  |  | 0.27778
(ii) | 160 MVA Auto- II | AUTO | 4 | 9:15 | 0 | 0:00 | 0 | 0:00 |  |  | 0.38542
(iii) | 160 MVA Auto- III | AUTO | 1 | 1:40 | 0 | 0:00 | 0 | 0:00 |  |  | 0.069444
2 | Power Transformer | POWER
(i) | 63 MVA Transformer-I | POWER | 1 | 9:08 | 1 | 0:25 | 2 | 0:33 |  |  |  | 0.42083
(ii) | 63 MVA Transformer-II | POWER | 1 | 8:08 | 1 | 0:17 | 2 | 0:38 |  |  |  | 0.37708
(iii) | 40 MVA Transformer-III | POWER | 2 | 14:05 | 1 | 0:09 | 3 | 3:52 |  |  |  | 0.75417
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220 kV Balasore- Balimuda (Dhamra) | FEEDER | 11 | 52:01 | 3 | 24:57 | 0 | 0:00 | [5 empty] | 1900-01-02 04:58
(ii) | 220 kV Balasore-Bhadrak | FEEDER | 1 | 1:39 | 3 | 7:47 | 2 | 1:34 | [5 empty] | 0.45833
(iii) | 220 kV Balasore-PGCIL-1 | FEEDER | 1 | 0:42 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.029167
(iv) | 220 kV Balasore-PGCIL-2 | FEEDER | 3 | 20:14 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.84306
(v) | 132 kV Balasore-Basta | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(vi) | 132 kV Balasore-Chandipur | FEEDER | 3 | 5:50 | 2 | 2:57 | 2 | 3:39 | [5 empty] | 0.51806
(vii) | 132 kV Balasore-Balasore Alloys | FEEDER | 4 | 3:11 | 1 | 8:37 | 1 | 0:58 | [5 empty] | 0.53194
(viii) | 132 kV Balasore-Birla-Tyres | FEEDER | 1 | 23:19 | 1 | 8:37 | 1 | 1:22 | [5 empty] | 1899-12-31 09:18
(ix) | 132 kV Balasore-Traction | FEEDER | 4 | 0:31 | 6 | 2:00 | 6 | 1:13 | [5 empty] | 0.15556
(x) | 132 kV Balasore-Somnathpur | FEEDER | 3 | 0:44 | 1 | 0:05 | 0 | 0:00 | [5 empty] | 0.034028
132/33 kV Grid S/S, Basta
1 | Power Transformer | POWER
(i) | 20 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 12.5 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(iii) | 20 MVA Power Transformer - III | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Basta- Jaleswar Feeder | FEEDER | 2 | 10:06 | 2 | 6:18 | 2 | 2:31 | [5 empty] | 0.78819
132/33 kV Grid S/S, Bhograi
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 15:16 |  |  |  | 0.63611
(ii) | 40 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Bhogarai- Kuchei PG | FEEDER | 5 | 8:47 | 4 | 7:37 | 4 | 2:18 | [5 empty] | 0.77917
(ii) | 132KV Bhogarai- Jaleswar | FEEDER | 2 | 0:54 | 5 | 3:43 | 1 | 4:28 | [5 empty] | 0.37847
132/33 kV Grid S/S, Jaleswar
1 | Power Transformer | POWER
(i) | 31.5 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 22:00 | 1 | 0:33 |  |  |  | 0.93958
(ii) | 31.5 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 23:00 | 1 | 34:56 |  |  |  | 1900-01-01 09:56
(iii) | 12.5 MVA Power Transformer - III | POWER | 0 | 0:00 |  |  |  |  | Burned and Out of service from dt.11.03.24 |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Kuchei PG- Jaleswar | FEEDER | 5 | 31:36 | 2 | 7:32 | 5 | 15:00 | [5 empty] | 1900-01-01 06:08
(ii) | 132 KV Jaleswar- Jaleswar RTSS | FEEDER | 0 | 0:00 | 2 | 1:47 | 2 | 0:16 | [5 empty] | 0.085417
132/33 kV Grid S/S, Somanathpur
1 | Power Transformer | POWER
(i) | 12.5 MVA Power Transformer - I | POWER | 4 | 1:11 | 3 | 2:40 | 6 | 10:40 |  |  |  | 0.60486
(ii) | 12.5 MVA Power Transformer - II | POWER | 8 | 12:45 | 3 | 2:50 | 4 | 6:13 |  |  |  | 0.90833
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132KV Somanathpur- EMAMI | FEEDER | 4 | 28:03 | 3 | 2:38 | 5 | 12:03 | [5 empty] | 1899-12-31 18:44
(ii) | 132KV Somanathpur- Stork Ferro | FEEDER | 4 | 53:00 | 3 | 2:44 | 1 | 3:10 | [5 empty] | 1900-01-01 10:54
132/33 kV Grid S/S, Soro
1 | Power Transformer | BUS
(i) | 20 MVA Power Transformer - I | POWER | 3 | 0:32 | 2 | 0:14 | 0 | 0:00 |  |  |  | 0.031944
(ii) | 20 MVA Power Transformer - II | POWER | 8 | 8:40 | 3 | 1:34 | 1 | 0:44 |  |  |  | 0.45694
(iii) | 40 MVA Power Transformer - III | POWER | 3 | 0:23 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.015972
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Soro - Chandipur | FEEDER | 6 | 8:12 | 1 | 2:54 | 7 | 8:09 | [5 empty] | 0.80208
(ii) | 132 kV Soro - Bhadrak | FEEDER | 1 | 2:28 | 2 | 4:48 | 1 | 1:20 | [5 empty] | 0.35833
132/33 kV Grid S/S, Bangiriposhi
1 | Power Transformer | POWER
(i) | 12.5 MVA Power Transformer - I | POWER | 5 | 4:20 | 5 | 4:20 | 0 | 0:00 |  |  |  | 0.36111
(ii) | 12.5 MVA Power Transformer - II | POWER | 3 | 2:39 | 3 | 2:39 | 0 | 0:00 |  |  |  | 0.22083
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132Kv Kuchie PG-Bangiriposi | FEEDER | 3 | 3:44 | 3 | 3:44 | 3 | 12:23 | [5 empty] | 0.82708
(ii) | 132Kv Bangiriposi-Rairangpur | FEEDER | 4 | 3:32 | 4 | 3:32 | 7 | 33:29 | [5 empty] | 1899-12-31 16:33
132/33 kV Grid S/S, Baripada
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 3 | 2:47 | 0 | 0:00 | 9 | 4:17 |  |  |  | 0.29444
(ii) | 40 MVA Power Transformer - II | POWER | 3 | 2:52 | 2 | 1:33 | 9 | 4:17 |  |  |  | 0.3625
(iii) | 40 MVA Power Transformer - III | POWER | 2 | 0:38 | 0 | 0:00 | 9 | 19:29 |  |  |  | 0.83819
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Baripada-Kuchei PG | FEEDER | 4 | 18:07 | 1 | 0:21 | 7 | 7:29 | [5 empty] | 1899-12-31 01:57
(ii) | 132kV Baripada-Betanoti | FEEDER | 9 | 18:05 | 1 | 0:30 | 8 | 5:49 | [5 empty] | 1899-12-31 00:24
132/33 kV Grid S/S, Udala
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 40 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:29 |  |  |  | 0.020139
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132Kv Udala- Balasore | FEEDER | 6 | 9:49 | 0 | 0:00 | 5 | 11:19 | [5 empty] | 0.88056
132/33 kV Grid S/S, Betanati
1 | Power Transformer | POWER
(i) | 20 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:02 |  |  |  | 0.0013889
(ii) | 40 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Betanati- Udala | FEEDER | 3 | 1:10 | 0 | 0:00 | 8 | 6:05 | [5 empty] | 0.30208
132/33 kV Grid S/S, Karanjia
1 | Power Transformer | POWER
(i) | 12.5 MVA Power Transformer - I | POWER | 0 | 0:00 | 1 | 12:43 | 0 | 0:00 |  |  |  | 0.52986
(ii) | 12.5 MVA Power Transformer - II | POWER | 0 | 0:00 | 1 | 1:17 | 0 | 0:00 |  |  |  | 0.053472
(iii) | 20 MVA Power Transformer - Iii | POWER | 1 | 8:21 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.34792
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132kV Polasponga - Karanjia | FEEDER | 1 | 30:31 | 0 | 0:00 | 8 | 34:39 | [5 empty] | 1900-01-01 17:10
(ii) | 132KV Karanjia-Dhenkikote | FEEDER | 3 | 1:18 | 1 | 0:22 | 2 | 0:29 | [5 empty] | 0.089583
132/33 kV Grid S/S, Rairangpur
1 | Power Transformer | POWER
(i) | 20 MVA Power Transformer - I | POWER | 1 | 0:25 | 1 | 12:50 | 4 | 2:25 |  |  |  | 0.65278
(ii) | 12.5 MVA Power Transformer - II | POWER | 1 | 0:35 | 0 | 0:00 | 6 | 3:47 |  |  |  | 0.18194
(ii) | 20 MVA Power Transformer - III | POWER | 2 | 1:09 | 0 | 0:00 | 2 | 4:03 |  |  |  | 0.21667
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 kV Rairangpur - Karanjia | FEEDER | 4 | 6:38 | 4 | 23:20 | 3 | 0:34 | [5 empty] | 1899-12-31 06:32
220/132/33 kV Grid S/S, Bhadrak
1 | Auto Transformer | AUTO
(i) | 100 MVA Auto- I | AUTO | 0 | 0:00 | 3 | 27:17 | 0 | 0:00 |  |  | 1899-12-31 03:17
(ii) | 160 MVA Auto- II | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 3:42 |  |  | 0.15417
(iii) | 160 MVA Auto- III | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0
2 | Power Transformer | POWER
(i) | 63 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 2:54 |  |  |  | 0.12083
(ii) | 63 MVA Transformer-II | POWER | 1 | 2:43 | 0 | 0:00 | 3 | 4:40 |  |  |  | 0.30764
(iii) | 63 MVA Transformer-III | POWER | 0 | 0:00 | 0 | 0:00 | 4 | 7:57 |  |  |  | 0.33125
3 | Bus Fault | BUS
(i) | 220 kV Main Bus-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 220 kV Main Bus-Ii | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(iii) | 132 kV Main Bus In New S/Y | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(iv) | 132 kV Transfer Bus In New S/Y | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(v) | 132 kV Main Bus In Old S/Y | BUS | 0 | 0:00 | 0 | 0:00 | 1 | 2:40 |  |  |  |  | 0.11111
(vi) | 132 kV Transfer Bus In Old S/Y | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER | [11 empty] | 0
(i) | 220 KV Bhadrak-New Duburi | FEEDER | 3 | 20:49 | 0 | 0:00 | 5 | 35:43 | [5 empty] | 1900-01-01 08:32
(ii) | 132 KV Bhadrak-DPCL-I | FEEDER | 3 | 3:09 | 0 | 0:00 | 4 | 4:11 | [5 empty] | 0.30556
(iii) | 132 KV Bhadrak DPCL-II | FEEDER | 0 | 0:00 | 1 | 1:19 | 4 | 3:46 | [5 empty] | 0.21181
(iv) | 132 KV Bhadrak-Jajpur Town | FEEDER | 2 | 1:46 | 0 | 0:00 | 4 | 3:54 | [5 empty] | 0.23611
(v) | 132 KV Bhadrak- Facor | FEEDER | 2 | 1:32 | 2 | 0:23 | 7 | 5:50 | [5 empty] | 0.32292
(vi) | 132 KV Bhadrak- Facor power | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 5:06 | [5 empty] | 0.2125
(vii) | 132 KV Bhadrak-Traction | FEEDER | 6 | 0:33 | 4 | 1:04 | 6 | 17:39 | [5 empty] | 0.80278
(viii) | 132 KV Bhadrak-Agarpada | FEEDER | 0 | 0:00 | 1 | 6:57 | 0 | 0:00 | [5 empty] | 0.28958
132/33 kV Grid S/S, Agarpada
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 2 | 6:13 | 1 | 0:45 | 2 | 6:13 |  |  |  | 0.54931
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER
(i) | 132 KV Agarpada-Anandapur Feeder | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33 kV GIS, Chandbali
1 | Power Transformer | POWER
(i) | 40 MVA Power Transformer - I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(i) | 20 MVA Power Transformer - II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder Fault | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33KV Grid S/s Barbil
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 0 | 0:00 | 2 | 0:37 | 4 | 0:49 |  |  |  | 0.059722
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 0:00 | 2 | 5:45 | 4 | 0:49 |  |  |  | 0.27361
(iii) | 20 MVA Transformer-3 | POWER | 0 | 0:00 | 2 | 0:54 | 2 | 0:32 |  |  |  | 0.059722
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Barbil- Bolani | FEEDER | 4 | 5:45 | 1 | 0:08 | 4 | 0:49 | [5 empty] | 0.27917
(ii) | 132 KV Barbil- Kamando Steel Plant (KSP) | FEEDER | 6 | 25:13 | 1 | 0:08 | 3 | 1:49 | [5 empty] | 1899-12-31 03:10
220/132/33kV GRID S/s Joda
1 | Auto Transformer | AUTO
(i) | 100MVA Auto 1 | AUTO | 1 | 0:11 | 0 | 0:00 | 0 | 0:00 |  |  | 0.0076389
(ii) | 100MVA Auto 2 | AUTO | 2 | 1:27 | 0 | 0:00 | 0 | 0:00 |  |  | 0.060417
(iii) | 100MVA Auto 3 | AUTO | 4 | 2:40 | 0 | 0:00 | 0 | 0:00 |  |  | 0.11111
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-IV | POWER | 3 | 0:26 | 0 | 0:00 | 1 | 0:39 |  |  |  | 0.045139
(iii) | 20 MVA Transformer-V | POWER | 1 | 0:12 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0083333
(iv) | 40 MVA Transformer-VI | POWER | 1 | 0:12 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.0083333
(v) | 15 MVA Transformer-VII | POWER | 1 | 0:30 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.020833
3 | Bus Fault | BUS
4 | EHT Feeder Fault | FEEDER
(i) | 220 kV Joda- Telkoi | FEEDER | 9 | 4:33 | 3 | 3:16 | 4 | 2:51 | [5 empty] | 0.44444
(ii) | 220 kV Joda- TTPS Ckt-II | FEEDER | 8 | 7:10 | 4 | 6:37 | 4 | 5:26 | [5 empty] | 0.80069
(iii) | 220 kV Joda- JSPL | FEEDER | 3 | 3:14 | 0 | 2:16 | 4 | 4:49 | [5 empty] | 0.42986
(iv) | 220 kV Joda- R.C.PUR | FEEDER | 19 | 88:26 | 4 | 1027:27 | 16 | 74:55 | [5 empty] | 1900-02-17 14:48
(v) | 220 kV Joda- TSIL | FEEDER | 1 | 0:14 | 1 | 16:14 | 2 | 0:23 | [5 empty] | 0.70208
(vi) | 220 kV Joda- Tata Steel | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(viii) | 132 kV Joda- Barbil | FEEDER | 3 | 1:25 | 0 | 0:00 | 3 | 1:04 | [5 empty] | 0.10347
(ix) | 132 kV Joda- Palasponga | FEEDER | 6 | 8:00 | 3 | 42:01 | 8 | 20:33 | [5 empty] | 1900-01-01 22:34
(x) | 132 kV Joda- FAP Joda | FEEDER | 1 | 0:20 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.013889
(xi) | 132 kV Joda- RTSS Banaspani | FEEDER | 5 | 1:22 | 22 | 1:40 | 15 | 1:44 | [5 empty] | 0.19861
(xii) | 132 kV Joda- Kenduposi | FEEDER | 7 | 17:05 | 0 | 0:00 | 4 | 11:52 | [5 empty] | 1899-12-31 04:57
132/33KV Grid S/s Polasponga
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 3 | 0:42 | 0 | 0:00 | 3 | 1:20 |  |  |  | 0.084722
(ii) | 20 MVA Transformer-2 | POWER | 2 | 0:31 | 0 | 0:00 | 1 | 0:36 |  |  |  | 0.046528
(iii) | 40 MVA Transformer-3 | POWER | 3 | 0:58 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.040278
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 KV Palasponga- Keonjhar RTSS | FEEDER | 11 | 0:31 | 12 | 0:32 | 37 | 1:42 | [5 empty] | 0.11458
(ii) | 132 KV Palasponga- ESSAR Steel | FEEDER | 1 | 0:12 | 0 | 0:00 | 4 | 16:57 | [5 empty] | 0.71458
(iii) | 132 KV MSP-Palasponga- Karanjia | FEEDER | 2 | 30:31 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 1899-12-31 06:31
132/33KV Grid S/s Dhenkikote
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
220/33KV GIS Keonjhar
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 18 | 9:44 |  |  |  | 0.40556
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220 kV Keonjhar -PGCIL Ckt-I | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(ii) | 220 kV Keonjhar -PGCIL Ckt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
220/33KV GSS Telkoi
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 3 | 7:53 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.32847
(ii) | 20 MVA Transformer-2 | POWER | 4 | 1:12 | 2 | 0:27 | 0 | 0:00 |  |  |  | 0.06875
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220 kV Telkoi-TTPS | FEEDER | 8 | 9:28 | 2 | 2:42 | 12 | 9:22 | [5 empty] | 0.89722
|  |  |  | 1900-02-02 10:55 |  | 1900-03-01 12:34 |  | 1900-02-05 01:44
| Total |  |  |  | 1900-05-12 01:13 |  |  |  |  | 0.56319 | 1900-01-01 23:01 | 1900-01-15 20:03 | 1899-12-31 00:30 | 1900-04-20 16:08 | 1900-05-12 01:13
[10 empty] | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Auto Trf = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
ICT = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Duration of Trippings (Hr:Mn) = SUM(E5:[Duration of Trippings (Hr:Mn), row above])
Duration of Trippings (Hr:Mn) = SUM(G5:[Duration of Trippings (Hr:Mn), row above])
FORM P-3 = SUM(I5:[FORM P-3, row above])

## P-3 Jeypore
Licencee : OPTCL |  |  | OERC |  |  |  |  | FORM P-3
Sl. No. | Jeypore Circle | Category | First six months of the previous year (04/23 to 09/23) |  | Last six months of the previous year (10/23 to 03/24) |  | First six months of the current year (04/24 to 09/24) |  | Steps proposed to reduce such trippings | ICT | Auto Trf | Power Trf | Bus Fault | EHT Feeder Fault
|  |  | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn) | No. of Trippings | Duration of Trippings (Hr:Mn)
Jeypore CIRCLE
132/33kV Grid S/S, Dabugaon
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 1 | 1:50 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.076389
(ii) | 12.5 MVA Transformer-II | POWER | 1 | 1:50 | 1 | 0:08 | 0 | 0:00 |  |  |  | 0.081944
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Tentulikhunti- Dabugaon | FEEDER | 5 | 3:12 | 2 | 5:53 | 4 | 5:12 | [5 empty] | 0.59514
(ii) | 132KV Dabugaon- Jayapatna | FEEDER | 2 | 19:37 | 2 | 4:05 | 1 | 0:11 | [5 empty] | 0.99514
220/132/33 kV Grid S/S, Jayanagar
1 | Auto Transformer | AUTO
(i) | 160MVA Auto-I | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0:00
(ii) | 160MVA Auto-II | AUTO | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  | 0:00
2 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:40 |  |  |  | 0.027778
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:40 |  |  |  | 0.027778
(iii) | 20 MVA Transformer-III | POWER | 0 | 0:00 | 1 | 7:22 | 1 | 0:40 |  |  |  | 0.33472
(iv) | 20 MVA Transformer-IV | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 1:44 |  |  |  | 0.072222
3 | Bus Fault | BUS
(i) | BUS-I | BUS | 2 | 0:56 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0.038889
(ii) | BUS-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220KV Jayanagar- Balimela Ckt-I | FEEDER | 3 | 2:42 | 1 | 0:34 | 0 | 0:00 | [5 empty] | 0.13611
(ii) | 220KV Jayanagar- Balimela Ckt-II | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 0:08 | [5 empty] | 0.0055556
(iii) | 220KV Jayanagar- Balimela Ckt-III | FEEDER | 1 | 0:24 | 1 | 3:20 | 2 | 0:49 | [5 empty] | 0.18958
(iv) | 220KV Jayanagar- Upper Kolab Ckt-I | FEEDER | 1 | 3:41 | 0 | 0:00 | 1 | 2:55 | [5 empty] | 0.275
(v) | 220KV Jayanagar- Upper Kolab Ckt-II | FEEDER | 1 | 2:08 | 0 | 0:00 | 1 | 2:57 | [5 empty] | 0.21181
(vi) | 220KV Jayanagar- Jeypore PGCIL Ckt-I | FEEDER | 1 | 0:34 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.023611
(vii) | 220KV Jayanagar- Jeypore PGCIL Ckt-II | FEEDER | 1 | 0:16 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.011111
(viii) | 220KV Jayanagar- Jeypore PGCIL Ckt-III | FEEDER | 1 | 0:18 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.0125
(ix) | 220KV Jayanagar- Jeypore PGCIL Ckt-IV | FEEDER | 0 | 0:00 | 0 | 0:00 | 1 | 2:09 | [5 empty] | 0.089583
(x) | 220KV Jayanagar- Laxmipur Ckt-I | FEEDER | 4 | 5:25 | 2 | 3:17 | 6 | 12:33 | [5 empty] | 0.88542
(xi) | 220KV Jayanagar- Laxmipur Ckt-II | FEEDER | 2 | 16:31 | 1 | 16:07 | 3 | 6:49 | [5 empty] | 1899-12-31 15:27
(xii) | 132KV Jayanagar- Podagada | FEEDER | 2 | 0:25 | 0 | 0:00 | 5 | 0:53 | [5 empty] | 0.054167
(xiii) | 132KV Jayanagar- Tentulikhunti | FEEDER | 6 | 2:42 | 2 | 8:48 | 3 | 3:06 | [5 empty] | 0.60833
(xiv) | 132KV Jayanagar- Boriguma | FEEDER | 1 | 21:10 | 0 | 0:00 | 3 | 0:36 | [5 empty] | 0.90694
(xv) | 132KV Jayanagar- Machkund | FEEDER | 4 | 8:26 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.35139
(xvi) | 132KV Jayanagar- Sunabeda | FEEDER | 6 | 2:00 | 0 | 0:00 | 6 | 67:16 | [5 empty] | 1900-01-01 21:16
(xvii) | 132KV Jayanagar- Damanjodi | FEEDER | 0 | 0:00 | 0 | 0:00 | 2 | 0:23 | [5 empty] | 0.015972
(xviii) | 132KV Jayanagar- Traction | FEEDER | 9 | 7:12 | 6 | 1:27 | 5 | 2:54 | [5 empty] | 0.48125
(xix) | 132KV Jayanagar- Meenakshi | FEEDER | 2 | 2:39 | 3 | 0:41 | 4 | 2:36 | [5 empty] | 0.24722
132/33kV Grid S/S, Sunabeda
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 1 | 0:06 | 0 | 0:00 | 3 | 1:01 |  |  |  | 0.046528
(ii) | 12.5 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 1:02 |  |  |  | 0.043056
(iii) | 20 MVA Transformer-III | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 1:04 |  |  |  | 0.044444
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Sunabeda- HAL | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
(ii) | 132KV Sunabeda- Damanjodi | FEEDER | 0 | 0:00 | 1 | 0:25 | 0 | 0:00 | [5 empty] | 0.017361
(iii) | 132KV Sunabeda- Pottangi | FEEDER | 0 | 0:00 | 0 | 0:00 | 3 | 3:12 | [5 empty] | 0.13333
132/33kV Grid S/S, Tentulikhunti
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 7 | 2:09 | 1 | 0:10 | 7 | 2:09 |  |  |  | 0.18611
(ii) | 20 MVA Transformer-II | POWER | 5 | 1:16 | 1 | 1:10 | 5 | 1:16 |  |  |  | 0.15417
(iii) | 12.5 MVA Transformer-III | POWER | 8 | 2:19 | 0 | 0:00 | 8 | 2:19 |  |  |  | 0.19306
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Tentulikhunti- Nabarangpur feeder | FEEDER | 4 | 2:59 | 0 | 0:00 | 4 | 2:59 | [5 empty] | 0.24861
(ii) | 132KV Tentulikhunti- Solar feeder | FEEDER | 0 | 0:00 | 2 | 1:54 | 0 | 0:00 | [5 empty] | 0.079167
132/33kV Grid S/S, Nabarangpur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Nabarangpur- Boriguma feeder | FEEDER | 3 | 6:27 | 1 | 0:29 | 0 | 0:00 | [5 empty] | 0.28889
132/33kV Grid S/S, Borigumma
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER |  |  |  |  | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
132/33kV Grid S/S, Pottangi
1 | Power Transformer | POWER
(i) | 20 MVA Transformer- I | POWER | 2 | 0:32 | 0 | 0:00 | 12 | 2:31 |  |  |  | 0.12708
(i) | 12.5 MVA Transformer- II | POWER | 2 | 0:32 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.022222
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Podagada -Pottangi | FEEDER | 1 | 0:31 | 6 | 2:56 | 8 | 2:55 | [5 empty] | 0.26528
132/33kV Grid S/S, Umerkote
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-1 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:20 |  |  |  | 0.013889
(ii) | 20 MVA Transformer-2 | POWER | 0 | 0:00 | 0 | 0:00 | 1 | 0:20 |  |  |  | 0.013889
(iii) | 40 MVA Transformer-3 | POWER |  |  |  |  | 0 | 0:00 |  |  |  | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Dabugaon - Umerkote | FEEDER | 2 | 0:51 | 2 | 0:55 | 1 | 0:18 | [5 empty] | 0.086111
132/33kV Grid S/S, Podagada
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 1 | 0:47 | 2 | 0:39 |  |  |  | 0.059722
(ii) | 12.5 MVA Transformer-II | POWER | 0 | 0:00 | 1 | 0:22 | 6 | 3:30 |  |  |  | 0.16111
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132KV Rayagada- Podagada | FEEDER | 28 | 37:17 | 1 | 37:29 | 18 | 11:38 | [5 empty] | 1900-01-02 14:24
220/33kV Grid S/S, Balimela
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 3 | 1:41 | 4 | 67:07 | 3 | 9:43 |  |  |  | 1900-01-02 06:31
(ii) | 20 MVA Transformer-II | POWER | 3 | 1:49 | 6 | 21:17 | 10 | 308:34 |  |  |  | 1900-01-12 19:40
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | 0 | 0:10 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.0069444
(i) | 220 kV OHPC Incomer -I | FEEDER | [11 empty] | 0
(ii) | 220 kV OHPC/ Jayanagar Incomer -II | FEEDER | [11 empty] | 0
220/33kV Grid S/S, Malkangiri
1 | Power Transformer | POWER
(i) | 40 MVA Transformer-I | POWER | 1 | 0:20 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.013889
(ii) | 40 MVA Transformer-II | POWER | 1 | 0:20 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0.013889
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | 3 | 3:59 | 3 | 0:51 | 2 | 3:23 | [5 empty] | 0.34236
(i) | 220 kV Malkangiri-Kalimela | FEEDER | [11 empty] | 0
(ii) | 220 kV Malkangiri- Govindpalli | FEEDER | [11 empty] | 0
220/33kV Grid S/S, Kalimela
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 5 | 2:46 | 3 | 1:48 | 3 | 5:22 |  |  |  | 0.41389
(ii) | 20 MVA Transformer-II | POWER | 3 | 2:40 | 2 | 0:45 | 4 | 9:00 |  |  |  | 0.51736
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | 2 | 5:29 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0.22847
(i) | 220 kV Balimela -Kalimela | FEEDER | [11 empty] | 0
220/33kV Grid S/S, Govindpalli
1 | Power Transformer | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(i) | 20 MVA Transformer-I | POWER | [9 empty] | 0
(ii) | 20 MVA Transformer-II | POWER | [9 empty] | 0
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220 kV Balimela- Jayanagar Ckt-I "T" connection | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kV Grid S/S, Akhusingh
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 7 | 1:54 | 4 | 50:32 | 0 | 0:00 |  |  |  | 1900-01-01 04:26
(ii) | 12.5 MVA Transformer-2 | POWER | 7 | 1:54 | 2 | 34:35 | 1 | 26:15 |  |  |  | 1900-01-01 14:44
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | [11 empty] | 0
(i) | 132kV Akhusingh- Rayagada | FEEDER | 50 | 35:06 | 36 | 7:42 | 97 | 31:52 | [5 empty] | 1900-01-02 02:40
(ii) | 132kV Akhusingh- Paralakhemundi | FEEDER | 3 | 0:27 | 0 | 0:00 | 2 | 0:12 | [5 empty] | 0.027083
(iii) | 132kV Akhusingh- Mohana | FEEDER | 1 | 0:03 | 8 | 1:23 | 24 | 50:32 | [5 empty] | 1900-01-01 03:58
(iv) | 132kV Akhusingh- Gunupur | FEEDER | 7 | 6:56 | 21 | 27:03 | 17 | 3:43 | [5 empty] | 1899-12-31 13:42
220/33kV Grid S/S, Laxmipur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  | 0
(ii) | 20 MVA Transformer-II | POWER | 1 | 0:17 | 0 | 0:00 | 1 | 1:23 |  |  |  | 0.069444
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | [11 empty] | 0
(i) | 220kV Laxmipur- NALCO(Damanjodi) Ckt-I | FEEDER | 0 | 0:00 | 4 | 5:44 | 2 | 0:35 | [5 empty] | 0.26319
(ii) | 220kV Laxmipur- NALCO(Damanjodi) Ckt-II | FEEDER | 0 | 0:00 | 2 | 1:08 | 1 | 0:18 | [5 empty] | 0.059722
(iii) | 220kV Laxmipur- Aditya Alumina Ckt-I | FEEDER | 4 | 3:29 | 3 | 34:26 | 1 | 65:54 | [5 empty] | 1900-01-03 07:49
(iv) | 220kV Laxmipur- Aditya Alumina Ckt-II | FEEDER | 2 | 3:16 | 2 | 3:52 | 0 | 0:00 | [5 empty] | 0.29722
(v) | 220kV Laxmipur- RTSS Laxmipur | FEEDER | 0 | 0:00 | 2 | 1:25 | 1 | 0:25 | [5 empty] | 0.076389
220/33kV Grid S/S, Kasipur
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-II | POWER | 0 | 0:00 | 1 | 1:14 | 1 | 0:18 |  |  |  | 0.063889
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 220kV Jayapatna- Kasipur | FEEDER | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 | [5 empty] | 0
132/33kV Grid S/S, Muniguda
1 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER |  |  | 0 | 0:00 | 1 | 0:12 |  |  |  | 0.0083333
(ii) | 12.5 MVA Transformer-II | POWER | 1 | 0:31 | 0 | 0:00 | 1 | 0:12 |  |  |  | 0.029861
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132 kV Muniguda - Vedant(Lanjigarh) | FEEDER | 0 | 0:00 | 1 | 0:08 | 0 | 0:00 | [5 empty] | 0.0055556
(ii) | 132 kV Muniguda- Bissamcuttack RTSS | FEEDER | 17 | 0:34 | 16 | 0:33 | 63 | 1:44 | [5 empty] | 0.11875
132/33kV Grid S/S, Parlakhemundi
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-1 | POWER | 0 | 0:00 | 1 | 0:10 | 0 | 0:00 |  |  |  | 0:10
(ii) | 12.5 MVA Transformer-2 | POWER | 0 | 0:00 | 1 | 0:10 | 0 | 0:00 |  |  |  | 0:10
(iii) | 12.5 MVA Transformer-3 | POWER | 2 | 0:18 | 1 | 1:11 | 0 | 0:00 |  |  |  | 1:29
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER | [11 empty] | 0
132/33kV Grid S/S, Rayagada
1 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 3 | 0:31 |  |  |  | 0:31
(ii) | 12.5 MVA Transformer-II | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 0:23 |  |  |  | 0:23
(iii) | 20 MVA Transformer-III | POWER | 2 | 0:09 | 0 | 0:00 | 2 | 0:22 |  |  |  | 0:31
2 | Bus Fault | BUS
3 | EHT Feeder fault | FEEDER
(i) | 132kV Rayagada- RTSS Rayagada | FEEDER | 0 | 0:00 | 0 | 0:00 | 60 | 2:56 | [5 empty] | 0.12222
220/132/33 kV Grid S/S, Gunupur
1 | Auto Transformer | AUTO
(i) | 160MVA Auto- I | AUTO | 1 | 23:28 | 1 | 0:37 | 1 | 2:10 |  |  | 1899-12-31 02:15
(ii) | 160MVA Auto- II | AUTO | 1 | 23:28 | 1 | 1:03 | 0 | 0:00 |  |  | 1899-12-31 00:31
2 | Power Transformer | POWER
(i) | 20 MVA Transformer-I | POWER | 0 | 0:00 | 0 | 0:00 | 2 | 23:52 |  |  |  | 23:52
(ii) | 20 MVA Transformer-II | POWER | 1 | 15:27 | 0 | 0:00 | 2 | 8:52 |  |  |  | 24:19
3 | Bus Fault | BUS
(i) | 220kV Bus-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 220kV Bus-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER
(i) | 132kV RTSS Palasingi | FEEDER | 3 | 1:06 | 5 | 1:13 | 1 | 0:24 | [5 empty] | 0.11319
220/132/33 kV Grid S/S, Therubali
1 | Auto Transformer | AUTO
(i) | 100MVA Auto- I | AUTO | 0 | 0:00 | 1 | 20:33 | 2 | 19:07 |  |  | 1899-12-31 15:40
(ii) | 100MVA Auto- II | AUTO | 1 | 0:14 | 0 | 0:00 | 0 | 0:00 |  |  | 0.0097222
(ii) | 160MVA Auto- III | AUTO | 0 | 0:00 | 0 | 0:00 | 1 | 2:34 |  |  | 0.10694
2 | Power Transformer | POWER
(i) | 12.5 MVA Transformer-I | POWER | 1 | 1:33 | 1 | 366:17 | 0 | 0:00 |  |  |  | 367:50
(ii) | 12.5 MVA Transformer-II | POWER | 3 | 16:27 | 0 | 0:00 | 0 | 0:00 |  |  |  | 16:27
3 | Bus Fault | BUS
(i) | 220kV Bus-I | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
(ii) | 220kV Bus-II | BUS | 0 | 0:00 | 0 | 0:00 | 0 | 0:00 |  |  |  |  | 0
4 | EHT Feeder Fault | FEEDER
(i) | 220kV Therubali-Gunupur Feeder | FEEDER | 10 | 26:55 | 2 | 6:22 | 3 | 6:17 | [5 empty] | 1899-12-31 15:34
(ii) | 220kV Therubali-Bhanjanagar (Ckt-I) | FEEDER | 14 | 15:05 | 2 | 3:34 | 11 | 41:24 | [5 empty] | 1900-01-01 12:03
(iii) | 220kV Therubali-Bhanjanagar (Ckt-II) | FEEDER | 14 | 11:03 | 3 | 56:50 | 12 | 8:44 | [5 empty] | 1900-01-02 04:37
(iv) | 220kV Therubali-Indravati (Ckt-I) | FEEDER | 7 | 47:47 | 0 | 0:00 | 3 | 3:01 | [5 empty] | 1900-01-01 02:48
(v) | 220kV Therubali-Indravati (Ckt-II) | FEEDER | 5 | 58:55 | 3 | 19:56 | 3 | 1:37 | [5 empty] | 1900-01-02 08:28
(vi) | 220kV Therubali-Indravati (Ckt-III) | FEEDER | 5 | 79:44 | 0 | 0:00 | 5 | 6:58 | [5 empty] | 1900-01-02 14:42
(vii) | 220kV Therubali-Kasipur | FEEDER | 2 | 27:24 | 1 | 1:08 | 2 | 1:39 | [5 empty] | 1899-12-31 06:11
(viii) | 220kV Therubali-Laxmipur (Ckt-I) | FEEDER | 4 | 11:12 | 3 | 3:51 | 7 | 9:55 | [5 empty] | 1899-12-31 00:58
(ix) | 220kV Therubali-Laxmipur (Ckt-II) | FEEDER | 4 | 92:01 | 2 | 4:14 | 8 | 17:11 | [5 empty] | 1900-01-03 17:26
(x) | 220kV Therubali-U.Kolab | FEEDER | 9 | 130:45 | 5 | 5:08 | 12 | 76:25 | [5 empty] | 1900-01-07 20:18
(xi) | 132kV Therubali-Rayagada | FEEDER | 3 | 2:13 | 2 | 30:50 | 3 | 28:40 | [5 empty] | 1900-01-01 13:43
(xii) | 132kV J.K.Paper | FEEDER | 1 | 2:04 | 1 | 5:22 | 0 | 0:00 | [5 empty] | 0.30972
(xiii) | 132kV IMFA Ltd | FEEDER | 2 | 2:15 | 1 | 5:35 | 0 | 0:00 | [5 empty] | 0.32639
(xiv) | 132kV Therubali-Muniguda | FEEDER | 4 | 8:37 | 2 | 53:43 | 1 | 1:16 | [5 empty] | 1900-01-01 15:36
(xv) | 132kV RTSS Bhalumaska | FEEDER | 1 | 0:40 | 1 | 8:09 | 4 | 1:34 | [5 empty] | 0.43264
|  |  |  | 1900-02-02 15:28 |  | 1900-02-07 19:48 |  | 1900-02-07 01:53 |  | 0 | 1900-01-02 21:14 | 1900-02-10 20:39 | 0.038889 | 1900-03-06 18:20 | 1900-04-22 13:09
| Total |  |  |  |  | 1900-04-22 13:09 |  |  |  | ICT | AUTO | POWER TRF | BUS FAULT | FEEDER FAULT
Formulas:
Power Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Power Trf = SUM(M5:[Power Trf, row above])
EHT Feeder Fault = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
EHT Feeder Fault = SUM(O5:[EHT Feeder Fault, row above])
Bus Fault = [Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]+[FORM P-3]
Bus Fault = SUM(N5:[Bus Fault, row above])
Auto Trf = [FORM P-3]+[Duration of Trippings (Hr:Mn)]+[Duration of Trippings (Hr:Mn)]
Auto Trf = SUM(L5:[Auto Trf, row above])
ICT = SUM(K5:[ICT, row above])