## ANNEXURE IV
99.9782 |  | TRANSMISSION SYSTEM OUTAGE DATA
PERIOD : 2024-25
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) / ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) / (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
400KV LINES
1 | 400 kV Indravati - Indravati PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.97 | 8760 | 100% | 0 | 69554.4
2 | 400kV Lapanga -IBTPS Ckt- I |  |  |  |  | 0.16319 | 6 | 30 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 24.491 | 8760 | 99.93% | 318.383 | 429082.32
|  | 13.06.24 | 19:20 | 13.06.24 | 20:51 | 1:31 | 3 | 2 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-20.72KA IL2-0.375KA IL3-0.39KA DIST-1.5KM
|  | 01.06.24 | 20:50 | 01.06.24 | 23:14 | 2:24 | 3 | 28 | [5 empty] | At Lapanga end: Distance Protection
3 | 400kV Lapanga -IBTPS Ckt- II |  |  |  |  | 0.11944 | 3 | 28 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 24.491 | 8760 | 99.96% | 169.8043 | 429082.32
|  | 01.06.24 | 20:57 | 01.06.24 | 23:49 | 2:52 | 3 | 28 | [5 empty] | At Lapanga end: Distance Protection, MAIN RELAY-1:- FAULT LOOP-L1-E ZONE-1 IL1-21.86KA IL2-0.47KA IL3-0.60KA DIST-1.516KM
4 | 400kV Meramundali -New Duburi Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
5 | 400kV Meramundali -New Duburi Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 96.6 | 8760 | 100% | 0 | 1692432
6 | 400kV Meramundali -Lapanga Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
7 | 400kV Meramundali -Lapanga Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 199.25 | 8760 | 100% | 0 | 3490860
8 | 400kV Lapanga-Vedant Ckt- I (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
9 | 400kV Lapanga-Vedant Ckt- II (Both on DC & MC) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17 | 8760 | 100% | 0 | 297840
10 | 400kV Meramundali -Mendhasal Ckt- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
11 | 400kV Meramundali -Mendhasal Ckt- II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.451 | 8760 | 100% | 0 | 1759901.52
12 | 400 kV Meramundali - JSPL Ckt- I |  |  |  |  | 0.70625 | 27 | 45 | [7 empty] | 37.916 | 8760 | 99.68% | 2104.338 | 664288.32
|  | 19.12.24 | 13:27 | 19.12.24 | 14:40 | 1:13 | 1 | 13 | [5 empty] | At Meramundali end: E/F At JSPL end: B-N, Ib- 6.13kA, Dist- 50.2km
|  | 25.01.25 | 05:13 | 25.01.25 | 5:40 | 0:27 | 0 | 27 | [5 empty] | At Meramundali end: Y-B-N, Zone 2, Dist- 40.1km, Iy- 11.15kA, Ib- 9.6kA
|  | 25.01.25 | 06:49 | 25.01.25 | 13:36 | 6:47 | 6 | 47 | [5 empty] | At Meramundali end: Y-N, Zone 1, Dist- 30.8km, Iy- 10.37kA
|  | 26.01.25 | 06:06 | 26.01.25 | 14:36 | 8:30 | 7 | 18 | [5 empty] | At Meramundali end: Distance Protection, Main 1: R-G, Ir -10.02 kA , 31.4 KM,,Main21: R-G, Ir -10.02 kA , 31.4 KM,
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
13 | 400 kV Meramundali - JSPL Ckt- II |  |  |  |  | 0.71111 | 26 | 32 | [7 empty] | 37.916 | 8760 | 99.7% | 2012.0757 | 664288.32
|  | 25.01.25 | 05:13 | 25.01.25 | 13:38 | 8:25 | 7 | 14 | [5 empty] | At Meramundali end: B-N, Zone 2, Dist- 37.2km, Ib- 6.81kA
|  | 26.01.25 | 04:21 | 26.01.25 | 5:07 | 0:46 | 0 | 46 | [5 empty] | At Meramundali end: Distance Protection, Remote end:Ir-9.47 kA,Iy-1.21 kA,Ib-3.74 kA,13.03 kM
|  | 26.01.25 | 05:31 | 26.01.25 | 13:24 | 7:53 | 6 | 32 | [5 empty] | At Meramundali end: Distance Protection, Main1: R-G, Ir - 7.52 kA , 30.7 KM,,Main 2 : Y-G, Iy-10.98 kA,26.4 KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
14 | 400kV Rengali - Kuchei PG-Kolaghat |  |  |  |  | 0.066667 | 1 | 13 | [7 empty] | 241.5 | 8760 | 99.99% | 587.65 | 4231080
|  | 19.12.24 | 13:27 | 19.12.24 | 15:03 | 1:36 | 1 | 13 | [5 empty] | AAt Meramundali end: E/F At JSPL end: B-N, Ib- 7.45kA, Dist- 23.3km
1196.886
220KV LINES
15 | 220kV Atri-Pandiabil Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
16 | 220kV Pandiabil-Samagara Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
17 | 220kV Atri-Pandiabil Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 26.7 | 8760 | 100% | 0 | 233892
18 | 220kV Pandiabil-Samagara Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.9 | 8760 | 100% | 0 | 402084
19 | 220kV Pandiabil- Pratapsasan Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.688 | 8760 | 100% | 0 | 268826.88
20 | 220kV Pandiabil- Pratapsasan Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.688 | 8760 | 100% | 0 | 268826.88
21 | 220kV Balasore- Bhadrak |  |  |  |  | 0.065278 | 1 | 23 | [7 empty] | 67.95 | 8760 | 99.98% | 93.9975 | 595242
|  | 12.05.24 | 14:58 | 12.05.24 | 16:10 | 1:12 | 1 | 1 | [5 empty] | At Bhadrak end: Remote End Tripping,IL1-1876.15A, IL2-417.31A,IL3-850.12A, IN-915.85A At Balasore end: Distance Protection,Main-I: Dist R-ph, Optd,Zone-2,Zone-3,Auto reclose lock out OPTD,fault distance-115.35KM, fault current-Ir=1876.151A, Iy=417.328 A, Ib=850.123A,In-915.858A.
|  | 17.09.24 | 10:20 | 17.09.24 | 10:42 | 0:22 | 0 | 22 | [5 empty] | At Balasore end: Distance Protection, Main-I:Dist Y-ph Optd,Zone-3,Auto reclose lockout, Dist-117.87 KM, fault current-Ir=443.978A, Iy=1566.214 A, Ib=378.893A,In-789.678A
22 | 220kV Balimela-Jayanagar Ckt-I |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 92.072 | 8760 | 100% | 12.2763 | 806550.72
|  | 02.06.24 | 20:39 | 02.06.24 | 20:47 | 0:08 | 0 | 8 | [5 empty] | At Jayanagar end: Distance Protection,R-G, Zone-1, dist=77.17km, Ir=1.693KA
23 | 220kV Balimela-Jayanagar Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 92.072 | 8760 | 100% | 0 | 806550.72
24 | 220kV Balimela-Jayanagar Ckt-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 93.46 | 900 | 100% | 0 | 84114
25 | 220kV Balimela-Govindpalli |  |  |  |  | 0 | 0 | 0 | [7 empty] | 37.04 | 7860 | 100% | 0 | 291134.4
26 | 220kV Govindpalli-Jayanagar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59.53 | 7860 | 100% | 0 | 467905.8
27 | 220kV Balimela-Kalimela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 55.15 | 8760 | 100% | 0 | 483114
28 | 220kV Kalimela-Malkangiri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.76 | 8760 | 100% | 0 | 339537.6
29 | 220kV Balimela-Malkangiri Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.41 | 8760 | 100% | 0 | 196311.6
30 | 220kV Balimela PH -Balimela |  |  |  |  | 0.0055556 | 0 | 16 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 0.2 | 8760 | 100% | 0.053333 | 1752
|  | 02.06.24 | 20:39 | 02.06.24 | 20:47 | 0:08 | 0 | 16 | [5 empty] | At Jayanagar end: Distance Protection,R-G, Zone-1, dist=77.17km, Ir=1.693KA
31 | 220kV Balimela PH -Upper Sileru |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.76 | 8760 | 100% | 0 | 216897.6
32 | 220kV Barkote-Bonai |  |  |  |  | 0.03125 | 0 | 45 | [7 empty] | 55.807 | 8760 | 99.99% | 41.8552 | 488869.32
|  | 21.05.24 | 18:32 | 21.05.24 | 19:05 | 0:33 | 0 | 33 | [5 empty] | At Rengali end: SOTFB-N phase, AR lockout, Ir= 207 A, Iy=1.48 kA, Ib= 87 kA
|  | 17.06.24 | 11:05 | 17.06.24 | 11:17 | 0:12 | 0 | 12 | [5 empty] | At Barkote end: Remote End Tripping
33 | 220kV Bonai-Tarkera |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 47.467 | 8760 | 100% | 10.2845 | 415810.92
|  | 17.06.24 | 11:05 | 17.06.24 | 11:18 | 0:13 | 0 | 13 | [5 empty] | At Tarkera end: O/C, Ib- 1.381kA
34 | 220kV Bonai-RTSS Bimlagarh |  |  |  |  | 0.031944 | 0 | 46 | [7 empty] | 20.218 | 8760 | 99.99% | 15.5005 | 177109.68
|  | 21.05.24 | 18:32 | 21.05.24 | 19:05 | 0:33 | 0 | 33 | [5 empty] | At Rengali end: SOTFB-N phase, AR lockout, Ir= 207 A, Iy=1.48 kA, Ib= 87 kA
|  | 17.06.24 | 11:05 | 17.06.24 | 11:18 | 0:13 | 0 | 13 | [5 empty] | At Tarkera end: O/C, Ib- 1.381kA
35 | 220kV Bhanjanagar-Narasinghpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 87.17 | 8760 | 100% | 0 | 763609.2
36 | 220kV Narasinghpur- Meramundali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 87.17 | 8760 | 100% | 0 | 763609.2
37 | 220kV Bhanjanagar-Meramundali |  |  |  |  | 0 | 0 | 0 | [7 empty] | 134.14 | 8760 | 100% | 0 | 1175066.4
38 | 220kV Bhanjanagar-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 136.47 | 8760 | 100% | 0 | 1195477.2
39 | 220kV Bhanjanagar-Nayagarh |  |  |  |  | 0 | 0 | 0 | [7 empty] | 69 | 8760 | 100% | 0 | 604440
40 | 220kV Nayagarh-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 68.58 | 8760 | 100% | 0 | 600760.8
41 | 220kV Bidanasi -Mendhasal Ckt-I |  |  |  |  | 0.016667 | 0 | 24 | [7 empty] | 15 | 8760 | 100% | 6 | 131400
|  | 19.04.24 | 12:21 | 19.04.24 | 12:45 | 0:24 | 0 | 24 | [5 empty] | At Bidanasi end: Y-B, Zone 1, Dist- 14.62km, Iy- 1.33kA, Ib- 2.33kA At Mendhasal end: Y-B, Zone 1, Dist-24.8km, Iy- 1.26kA, Ib- 5.35kA
42 | 220kV Bidanasi -Godisahi |  |  |  |  | 0.088194 | 0 | 25 | [7 empty] | 4.32 | 8760 | 100% | 1.8 | 37843.2
|  | 19.04.24 | 12:14 | 19.04.24 | 14:21 | 2:07 | 0 | 25 | [5 empty] | Y-B, Dist- 14.62km, Iy- 1.38kA, Ib- 2.33kA
43 | 220kV Godisahi -Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.754 | 8760 | 100% | 0 | 94205.04
44 | 220kV Bidanasi -Cuttack Ckt-I |  |  |  |  | 0.092361 | 0 | 24 | [7 empty] | 9.3 | 8760 | 100% | 3.72 | 81468
|  | 19.04.24 | 12:21 | 19.04.24 | 14:34 | 2:13 | 0 | 24 | [5 empty] | Remote end Tripping 220kV Bidanasi-Cuttack CKT I & II H/T at Cuttack end due to overloading and alternate power supply availed from Phulnakharaa end.
45 | 220kV Bidanasi -Cuttack Ckt-II |  |  |  |  | 0.092361 | 0 | 24 | [7 empty] | 9.3 | 8760 | 100% | 3.72 | 81468
|  | 19.04.24 | 12:21 | 19.04.24 | 14:34 | 2:13 | 0 | 24 | [5 empty] | Remote end Tripping 220kV Bidanasi-Cuttack CKT I & II H/T at Cuttack end due to overloading and alternate power supply availed from Phulnakharaa end.
46 | 220kV Bisra PG-Tarkera Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
47 | 220kV Bisra PG-Tarkera Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.335 | 8760 | 100% | 0 | 134334.6
48 | 220kV Budhipadar-Aditya Aluminium Ckt.-I |  |  |  |  | 0.16389 | 15 | 27 | [7 empty] | 20.507 | 8760 | 99.82% | 316.8331 | 179641.32
|  | 05.06.24 | 4:35 | 05.06.24 | 5:20 | 0:45 | 0 | 45 | [5 empty] | H/T for restoration of power supply
|  | 13.06.24 | 19:11 | 13.06.24 | 20:11 | 1:00 | 1 | 0 | [5 empty] | Busbar Protection relay tripped.
|  | 26.03.25 | 12:41 | 26.03.25 | 14:52 | 2:11 | 1 | 42 | [5 empty] | At Budhipadar end: Y-B, Iy- 12.06kA, Ib- 12.12kA, Dist- 13.85km At AAL end: Y-B, Zone 1, Iy- 5.485kA, Ib- 0.362kA, Dist- 5.841km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
49 | 220kV Budhipadar-Aditya Aluminium Ckt.-II |  |  |  |  | 0.18264 | 14 | 56 | [7 empty] | 20.507 | 8760 | 99.83% | 306.2379 | 179641.32
|  | 13.06.24 | 19:11 | 13.06.24 | 20:10 | 0:59 | 0 | 59 | [5 empty] | Busbar Protection relay tripped.
|  | 12.03.25 | 11:57 | 12.03.25 | 13:39 | 1:42 | 0 | 15 | [5 empty] | At Budhipadar end: Y-B, Zone 2, Dist- 19.93km, Iy- 9.776kA, Ib- 9.777kA At AAL end: Y-B, Zone 2, Dist- 0.03km, Iy- 12.96kA, Ib- 1.65kA
|  | 26.03.25 | 12:41 | 26.03.25 | 14:23 | 1:42 | 1 | 42 | [5 empty] | At Budhipadar end: B-N, Ir- 1.03kA, Iy- 1.22kA, Ib- 7.967kA, Dist- 12.05km At AAL end: B-N, Zone 1, Ir- 1.033kA, Iy- 1.222kA, Ib- 8.804kA, Dist- 6.863km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
50 | 220kV Budhipadar-Lephripada |  |  |  |  | 0.11042 | 13 | 49 | [7 empty] | 30.744 | 8760 | 99.84% | 424.7796 | 269317.44
|  | 19.05.24 | 11:35 | 19.05.24 | 11:53 | 0:18 | 0 | 18 | [5 empty] | At Budhipadar end:O/C,At Budhipadar end:D/P 1(MiCOM P444): F.L:Cph-N, zone1, F.D=17.15 km, F. Dur=111.7ms, Ia=40.41 A, Ib=59.29 A, Ic=2.58 kA, F.R=44.12 ohm, RTT=0ms
|  | 03.05.24 | 14:50 | 03.05.24 | 15:17 | 0:27 | 0 | 27 | [5 empty] | At Budhipadar end: O/C (B Ph), Zone 1, Dist- 7.6km, Ib- 4.89kA
|  | 05.06.24 | 04:12 | 05.06.24 | 6:06 | 1:54 | 1 | 4 | [5 empty] | Started phase-BC-N, tripped phase- ABC,zone-4,FD=-6.722KM,Ia-629.4A,Ib-955.9A,Ic-799.5A,fault duration-327.5ms
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
51 | 220kV Lephripada-Basundhara |  |  |  |  | 0.18125 | 16 | 21 | [7 empty] | 15.2 | 8760 | 99.81% | 248.52 | 133152
|  | 19.05.24 | 11:35 | 19.05.24 | 11:53 | 0:18 | 0 | 18 | [5 empty] | At Budhipadar end:O/C,At Budhipadar end:D/P 1(MiCOM P444): F.L:Cph-N, zone1, F.D=17.15 km, F. Dur=111.7ms, Ia=40.41 A, Ib=59.29 A, Ic=2.58 kA, F.R=44.12 ohm, RTT=0ms
52 |  | 03.05.24 | 14:50 | 03.05.24 | 15:17 | 0:27 | 0 | 27 | [5 empty] | At Budhipadar end: O/C (B Ph), Zone 1, Dist- 7.6km, Ib- 4.89kA
|  | 2024-10-11 | 12:48 | 2024-10-11 | 16:24 | 3:36 | 3 | 36 | [5 empty] | At Lephripada end: Y-B Ph, Zone 1, Dist- 11.7km, Iy- 5.81kA, Ib- 5.79kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
53 | 220kV Budhipadar-IbTPS Ckt-I |  |  |  |  | 0.15694 | 16 | 4 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.82% | 417.7333 | 227760
|  | 13.06.24 | 19:11 | 13.06.24 | 21:46 | 2:35 | 1 | 42 | [5 empty] | Busbar Protection relay operated
|  | 16.06.24 | 3:34 | 16.06.24 | 3:47 | 0:13 | 0 | 26 | [5 empty] | R-N, Zone 1, Dist- 17.2km, Ir- 6.6kA
|  | 05.06.24 | 04:12 | 05.06.24 | 5:10 | 0:58 | 1 | 56 | [5 empty] | D/P 1- Fault loop-L2 to E, Dist- 7km, IL1-2.13KA, IL2-2.5Kamp, IL3-2.16kA,
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
54 | 220kV Budhipadar-IbTPS Ckt-II |  |  |  |  | 0.19444 | 16 | 16 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 26 | 8760 | 99.81% | 422.9333 | 227760
|  | 01.06.24 | 19:32 | 01.06.24 | 19:51 | 0:19 | 0 | 38 | [5 empty] | At Budhipadar end: D/P operated, F.L=R-N, F.D=9.17 km, Ia=11.13kA, Ib=636A, Ic=190.6 A, F. Resistance=1.27ohm, Zone1, F. Duration=76.69ms
|  | 13.06.24 | 19:11 | 13.06.24 | 21:38 | 2:27 | 1 | 42 | [5 empty] | Busbar Protection relay operated
|  | 05.06.24 | 04:12 | 05.06.24 | 6:06 | 1:54 | 1 | 56 | [5 empty] | Started phase-BC-N, tripped phase- ABC,zone-4,FD=-6.722KM,Ia-629.4A,Ib-955.9A,Ic-799.5A,fault duration-327.5ms
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
55 | 220kV Budhipadar-IbTPS Ckt-III |  |  |  |  | 0.71042 | 3 | 38 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.96% | 92.214 | 222328.8
|  | 01.06.24 | 19:30 | 01.06.24 | 20:21 | 0:51 | 1 | 42 | [5 empty] | At Budhipadar end: D/P operated, F.L=R-N, F.D=12 km, Ia=9.93kA Ib=491.2A, Ic=160.7 A, F. Resistance=1.57ohm Zone1, F. Duration=63.27ms
|  | 05.06.24 | 04:12 | 05.06.24 | 20:24 | 16:12 | 1 | 56 | [5 empty] | D/P 1-Zone-1, IL1-0A, IL2-309.8Amp, IL3-137.1A, Fault Duration-15.04ms, D/P 2- Fault loop-L1toE, Zone-1, IL1-0.14Ka, IL2-0Kamp, IL3- 0kA, Dist-6Km.
56 | 220kV Budhipadar-IbTPS Ckt-IV |  |  |  |  | 0.14583 | 3 | 38 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 25.38 | 8760 | 99.96% | 92.214 | 222328.8
|  | 13.06.24 | 19:11 | 13.06.24 | 20:46 | 1:35 | 1 | 42 | [5 empty] | Busbar Protection relay operated
|  | 05.06.24 | 04:12 | 05.06.24 | 6:07 | 1:55 | 1 | 56 | [5 empty] | D/P 1:-started phase BC-N, tripped phase-ABC,-Zone-4, Trip Phase-BCN, Dist.-1.36km,IL1-694.9A,IL2-971Amp, IL3-898.4 A
57 | 220kV Budhipadar-Raigarh Ckt-I |  |  |  |  | 1899-12-31 01:51 | 1 | 7 | [7 empty] | 60 | 8760 | 99.99% | 67 | 525600
|  | 13.06.24 | 19:11 | 14.06.24 | 45457.9049 | 21:43 | 0 | 51 | [5 empty] | At Budhipadar end: Over Current, D/P 1(MICOM P444)- F.D- 1.104km, IA-20.97ka,IB-931.7a, IC- 266.0a,F.dur-524.9ms D/P 2(SIEMENS 7SA52)- F.L-L1`-E, pu time-521ms,F.D-1.2km ,IL1-21.49ka, IL2-0.9KA,IL3-0.2KArn R-phase limb of the CB burst.
|  | 05.06.24 | 04:12 | 05.06.24 | 8:20 | 4:08 | 0 | 16 | [5 empty] | At Budhipadar end: O/C (Y-B), Zone 4, Dist- -2.648km, Iy- 3.398kA, Ib- 3kA
58 | 220kV Budhipadar-Korba Ckt-II |  |  |  |  | 0.34792 | 13 | 34 | [7 empty] | 60 | 8760 | 99.85% | 814 | 525600
|  | 01.06.24 | 19:36 | 01.06.24 | 20:03 | 0:27 | 0 | 27 | [5 empty] | At Budhipadar end: D/P operated: F.L=R-N R-Phase CB Blast at Korba end. F.D=71.77 km, Ia=2.336kA Ib=176.83A, Ic=189.21A, In-2.353KA, Zone1, F. Duration=66.69ms At Korba end: D/P operated, F.L=R-N F.D=103.7 km, Ia=1.712kA Zone1, F. Resistance=7.8ohm
|  | 05.06.24 | 04:12 | 05.06.24 | 8:21 | 4:09 | 0 | 16 | [5 empty] | At Budhipadar end: O/C (Y-B), Zone 4, Dist- -2.098km, Iy- 1.68kA, Ib- 1.487kA At Korba end): B-N, Zone 2, Dist- 201km, Ib- 0.94kA
|  | 13.06.24 | 19:11 | 13.06.24 | 22:56 | 3:45 | 0 | 51 | [5 empty] | BB Protection & D/P 1- AR Block,IL1-793.7A,IL2- 265.98,IL3-204.3A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
59 | 220kV Budhipadar-Lapanga Ckt-I |  |  |  |  | 0.029167 | 0 | 42 | [7 empty] | 20 | 8760 | 99.99% | 14 | 175200
|  | 05.06.24 | 04:12 | 05.06.24 | 4:54 | 0:42 | 0 | 42 | [5 empty] | D/P 1:-started phase ABC-N, tripped phase-ABC,Zone-4, Fault Duration-302.5ms,Dist.1.912km,IL1-1.17KA, IL2-4.452KAmp, IL3-3.944KA,
60 | 220kV Budhipadar-Lapanga Ckt-II |  |  |  |  | 0.061806 | 1 | 29 | [7 empty] | 20 | 8760 | 99.98% | 29.6667 | 175200
|  | 13.06.24 | 19:11 | 13.06.24 | 19:46 | 0:35 | 0 | 35 | [5 empty] | Busbar Protection relay tripped.
|  | 05.06.24 | 04:12 | 05.06.24 | 5:06 | 0:54 | 0 | 54 | [5 empty] | D/P1-started phase-ABC-N, tripped phase-ABC,Zone-4,Dist.-2.3km,IL1-1.18KA,IL2-4.08KAmp, IL3-3.6KA, /DP-2 FL-L2-L3,Fault Duration-310.8 ms,Zone-4,IL1-1.18KA, IL24.08KA, IL3-3.61KA
61 | 220kV Budhipadar-SMC (Unit-II) Feeder Ckt-I |  |  |  |  | 0.097917 | 0 | 53 | [7 empty] | 13.424 | 8760 | 99.99% | 11.8579 | 117594.24
|  | 05.06.24 | 4:35 | 05.06.24 | 6:56 | 2:21 | 0 | 53 | [5 empty] | H/T for restoration of power supply
62 | 220kV Budhipadar-SMC (Unit-II) Feeder Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.424 | 8760 | 100% | 0 | 117594.24
63 | 220kV Budhipadar-Bhusan Ckt-I |  |  |  |  | 0.085417 | 14 | 2 | [7 empty] | 14.92 | 8760 | 99.84% | 209.3773 | 130699.2
|  | 02.05.24 | 13:10 | 02.05.24 | 13:35 | 0:25 | 0 | 25 | [5 empty] | At Budhipadar end: E/F (B Ph), Zone 2, Dist- 12.97km, Ib- 8.855kA
|  | 05.06.24 | 4:35 | 05.06.24 | 5:17 | 0:42 | 0 | 42 | [5 empty] | H/T for restoration of power supply
|  | 13.06.24 | 19:11 | 13.06.24 | 20:07 | 0:56 | 0 | 55 | [5 empty] | At Budhipadar end: Over Current,(At Budhipadar end):D/P(MICOM P444):F.L- C-N,zone 1, F.D-1.37km,IL1-182.2A,il2-377.7A,il3-5.971ka,F.R-306.7mohm,F.dur-40ms
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
64 | 220kV Budhipadar-Bhusan Ckt II |  |  |  |  | 0.48056 | 14 | 2 | [7 empty] | 14.92 | 8760 | 99.84% | 209.3773 | 130699.2
|  | 02.05.24 | 13:06 | 02.05.24 | 15:55 | 2:49 | 0 | 25 | [5 empty] | At Budhipadar end: E/F (B Ph), Zone 2, Dist- 15.07km, Ib- 11.14kA
|  | 13.06.24 | 19:09 | 13.06.24 | 23:05 | 3:56 | 0 | 55 | [5 empty] | At Budhipadar end: Over Current, D/P(MICOM P444) F.L- ABC, F.D- 977.5m, IA-25.99ka,IB-350.5a, IC- 354.0A,F.dur-51.07m. SOTF
|  | 05.06.24 | 4:35 | 05.06.24 | 9:22 | 4:47 | 0 | 42 | [5 empty] | H/T for restoration of power supply
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
65 | 220kV Chandaka -Mendhasal Ckt-I |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 19 | 8760 | 100% | 6.0167 | 166440
|  | 18.06.24 | 15:29 | 18.06.24 | 15:48 | 0:19 | 0 | 19 | [5 empty] | At Chandaka end: Y-N, Zone 1, Dist-3.6km, Iy- 3.79kA
66 | 220kV Chandaka- Mendhasal ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.9 | 8760 | 100% | 0 | 174324
67 | 220kV Chandaka- Kantabada |  |  |  |  | 0.14375 | 15 | 22 | [7 empty] | 8.5 | 8760 | 99.82% | 130.6167 | 74460
|  | 18.06.24 | 15:29 | 18.06.24 | 15:49 | 0:20 | 0 | 20 | [5 empty] | At Chandaka end: Distance Protection,L2-E, ZONE-NA, D= NA, 472.8A, 2.14KA, 251.7A, AR LOCKOUT SHOT
|  | 2024-10-05 | 11:05 | 2024-10-05 | 11:49 | 0:44 | 0 | 39 | [5 empty] | At Chandaka end: Distance Protection,Remote end TrippingA-N, Zone 1, 9.864KM, I1=4.439KA, I2=45.39A, I3=73.93A, AR WAS DISABLED,A-N, Z-1, 14.1KM, 2.6KA
|  | 13.03.25 | 14:06 | 13.03.25 | 16:29 | 2:23 | 2 | 23 | [5 empty] | At Chandaka end: R-N, Zone 1, Dist- 13.73km, Ir- 9.91kA, A/R unsuccessful
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
68 | 220kV Kantabada- Mendhasal |  |  |  |  | 0.12639 | 3 | 2 | [7 empty] | 12.8 | 8760 | 99.97% | 38.8267 | 112128
|  | 2024-10-05 | 11:05 | 2024-10-05 | 11:44 | 0:39 | 0 | 39 | [5 empty] | At Mendhasal end: Distance Protection, Zone 1 trip,Ia= 2.68KA, Dist= 14.1KM At Chandaka end: Zone 1 trip,Ia= 4.439KA, Dist= 9.8KM rnrn
|  | 13.03.25 | 14:06 | 13.03.25 | 16:29 | 2:23 | 2 | 23 | [5 empty] | At Chandaka end: R-N, Zone 1, Dist- 13.73km, Ir- 9.91kA, A/R unsuccessful
69 | 220kV Chandaka- Chandaka (B) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.1 | 8760 | 100% | 0 | 876
70 | 220kV Chandaka (B)-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.96 | 8760 | 100% | 0 | 166089.6
71 | 220kV Duburi-New Duburi Ckt - I |  |  |  |  | 0.38819 | 14 | 8 | [7 empty] | 6.38 | 8760 | 99.84% | 90.1707 | 55888.8
|  | 12.08.24 | 15:56 | 12.08.24 | 19:58 | 4:02 | 0 | 25 | [5 empty] | At Duburi end: Y-B Ph, Dist- 4.897km, Iy-2.45kA, Ib- 2.337kA
|  | 18.08.24 | 14:45 | 18.08.24 | 19:08 | 4:23 | 0 | 49 | [5 empty] | At Duburi end: Dist Protection,DP Relay :-,Started phase - C N,Fault Duration -346.4 ms,System Frequency - 50.04 Hz,Ia =94.67 Amp ,Ib- 136.0 Amp ,Ic= 2.893 kAmp,Van =120.2 KV ,Vbn =118.7 KV ,Vcn =19.18 KV,Back up Relay :-,Pick up -543 ms,Trip time -450 ms,B-ph ,E/F
|  | 21.12.24 | 03:50 | 21.12.24 | 4:44 | 0:54 | 0 | 54 | [5 empty] | At Duburi end: O/C (Y-N), Iy- 1.97kA At New Duburi end: No tripping
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
72 | 220kV Duburi-New Duburi Ckt - II |  |  |  |  | 0.14097 | 14 | 8 | [7 empty] | 6.38 | 8760 | 99.84% | 90.1707 | 55888.8
|  | 12.08.24 | 15:56 | 12.08.24 | 17:34 | 1:38 | 0 | 25 | [5 empty] | At New Duburi end: Iy- 2.417kA, Ib- 2.337kA, Dist- 4.89km At Duburi end: Y-B Ph, Zone 1, Dist- 5.812km, Iy- 0.091kA, Ib- 2.533kA
|  | 18.08.24 | 14:45 | 18.08.24 | 15:34 | 0:49 | 0 | 49 | [5 empty] | At Duburi end: O/C,Back up Relay :-,pick up - 535 ms,Trip Time - 447 ms
|  | 21.12.24 | 03:50 | 21.12.24 | 4:46 | 0:56 | 0 | 54 | [5 empty] | At Duburi end: O/C (Y-N), Iy- 2.09kA At New Duburi end: Bus bar Relay & 96 Relay OPTD
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
73 | 220kV Duburi-NINL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6 | 8760 | 100% | 0 | 52560
74 | 220kV Indravati PH-Therubali Ckt-I |  |  |  |  | 0.084028 | 0 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 28.7333 | 755112
|  | 06.06.24 | 18:31 | 06.06.24 | 20:32 | 2:01 | 0 | 20 | [5 empty] | At Therubali end: YN,Z1,0.33KM,Iy=4.8KA No tripping at Indravati end.
75 | 220kV Indravati PH-Therubali Ckt-II |  |  |  |  | 0.0375 | 0 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 86.2 | 8760 | 100% | 28.7333 | 755112
|  | 06.06.24 | 18:31 | 06.06.24 | 19:25 | 0:54 | 0 | 20 | [5 empty] | At Indravati end: YN,Z-2,108.4KM,Iy=614.1A
76 | 220kV Indravati PH-Therubali Ckt-III |  |  |  |  | 0.0375 | 0 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 91 | 8760 | 100% | 30.3333 | 797160
|  | 06.06.24 | 18:31 | 06.06.24 | 19:25 | 0:54 | 0 | 20 | [5 empty] | At Indravati end: YN,Z-2,121.3KM,Iy=564.1A
77 | 220kV Indravati PH-Jayapatna |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.3 | 8760 | 100% | 0 | 169068
78 | 220kV Jayapatna-Kasipur |  |  |  |  | 0.028472 | 1 | 41 | [7 empty] | 39.5 | 8760 | 99.98% | 66.4917 | 346020
|  | 03.05.24 | 17:39 | 03.05.24 | 18:20 | 0:41 | 1 | 41 | [5 empty] | At Jayapatna end: SOTF, O/C (B-Ph) & E/F, Zone-2 ,Dist- 37km, Ib- 3.05kA
79 | 220kV Kasipur-Therubali |  |  |  |  | 0.067361 | 1 | 51 | [7 empty] | 66.7 | 8760 | 99.98% | 123.395 | 584292
|  | 03.05.24 | 17:39 | 03.05.24 | 18:20 | 0:41 | 1 | 41 | [5 empty] | At Therubali end: B-N, Zone 2, Dist- 61.45km, Ib- 2.821kA
|  | 06.06.24 | 18:31 | 06.06.24 | 19:27 | 0:56 | 0 | 10 | [5 empty] | At Kasipur end: YN,Z-2,46.4KM,Iy=464.7A
80 | 220kV Jayanagar-Jeypore PG Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
81 | 220kV Jayanagar-Jeypore PG Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
82 | 220kV Jayanagar-Jeypore PG Ckt-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
83 | 220kV Jayanagar-Jeypore PG Ckt-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.73 | 8760 | 100% | 0 | 67714.8
84 | 220kV Jayanagar-Laxmipur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
85 | 220kV Jayanagar-Laxmipur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 65 | 8760 | 100% | 0 | 569400
86 | 220kV JSPL-Jamsedpur DVC |  |  |  |  | 1900-01-01 | 2 | 46 | [7 empty] | 20.8 | 8760 | 99.97% | 57.5467 | 182208
|  | 03.05.24 | 12:32 | 03.05.24 | 15:18 | 1900-01-01 | 2 | 46 | [5 empty] | At Joda end: E/F At Jamshedpur end: Y Ph, Zone 2, Dist- 147km,Iy- 0.77kA
87 | 220kV Joda-RCPur |  |  |  |  | 0.06875 | 1 | 39 | [7 empty] | 15.5 | 8760 | 99.98% | 25.575 | 135780
|  | 20.06.24 | 22:27 | 20.06.24 | 23:01 | 0:34 | 0 | 34 | [5 empty] | At Joda end: Distance Protection,Relay at Joda end: DP relay Main-1: Zone -01 , Dist-33.92Km, Tripped phase- CN, Fault Current :Ia- 271.5A , Ib-565.3A, Ic-2794A DP Main-II: Zone -01,Trip ph- CGT ,Dist -31.38Km , Fault current : Ia- 263A, Ib-572A, Ic-2965A At Ramchandrapur end: DP relay Main-1: Zone -01 ,Dist-86.4Km, Fault Current : Ic-2120A
|  | 20.06.24 | 23:03 | 20.06.24 | 45464.0056 | 1:05 | 1 | 5 | [5 empty] | At Joda end: Distance Protection,Relay at Joda end: DP relay Main-1: A/R lockout shot, SOTF, Zone -01 ,Dist-14.13Km, Tripped phase- CN, Fault Current :Ia- 466.8A ,Ib-236.3A, Ic-4192A DP Main-II: Zone -01,Trip ph- CGT , Dist -13.38Km , Fault current : Ia- 223A, Ib-700A, Ic-4268A At Ramchandrapur end: DP relay Main-1:Zone -01 ,Dist-104.7Km
88 | 220kV Joda-JSPL |  |  |  |  | 0.11528 | 2 | 46 | [7 empty] | 21 | 8760 | 99.97% | 58.1 | 183960
|  | 03.05.24 | 12:32 | 03.05.24 | 15:18 | 2:46 | 2 | 46 | [5 empty] | At Joda end: E/F At Jindal end: Y Ph, Iy- 0.718kA
89 | 220kV Joda-TSLPL (formerly TSIL) |  |  |  |  | 0.10139 | 14 | 26 | [7 empty] | 7.3 | 8760 | 99.84% | 105.3633 | 63948
|  | 20.05.24 | 11:44 | 20.05.24 | 11:57 | 0:13 | 0 | 13 | [5 empty] | At Joda end: Earth Fault,220kV Joda-TSIL feeder tripped only at Joda end with following relay indication.At Joda end:- Back upFault loop- C-N, Ia-27.96A, Ib-28.20A, Ic-29.37A
|  | 10.11.24 | 12:38 | 10.11.24 | 13:10 | 0:32 | 0 | 32 | [5 empty] | At Joda end: B/U operated only Fault Current :Ia-25.74A ,Ib-164.1A, Ic-104.6A At TSIL end: B/U relay operated only. Fault Current :Ia-12.78A ,Ib-126.7A, Ic-65.37A
|  | 6.12.24 | 11:27 | 6.12.24 | 11:57 | 0:30 | 0 | 30 | [5 empty] | At Joda end: O/C & E/F, Ib- 0.272kA At TSIL end: O/C & E/F, Ib- 0.072kA
|  | 6.12.24 | 13:40 | 6.12.24 | 14:14 | 0:34 | 0 | 34 | [5 empty] | At Joda end: O/C & E/F, Ib- 0.526kA At TSIL end: O/C & E/F, Ib- 0.088kA
|  | 15.01.25 | 8:43 | 15.01.25 | 9:15 | 0:32 | 0 | 32 | [5 empty] | At Joda end: B/U Relay: O/C&E/F Fault Current :Ia-40A ,Ib-50A, Ic-90A
|  | 23.01.25 | 22:14 | 23.01.25 | 22:19 | 0:05 | 0 | 5 | [5 empty] | At Joda end: B/U Relay: O/C&E/F Fault Current :Ia-27.44A ,Ib-26.64A, Ic-27.93A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
90 | 220kV Katapalli- HINDALCO Ckt-I |  |  |  |  | 0.031944 | 0 | 13 | [7 empty] | 10 | 8760 | 100% | 2.1667 | 87600
|  | 29.08.24 | 06:57 | 29.08.24 | 7:43 | 0:46 | 0 | 13 | [5 empty] | At Lapanga end: R-N, Zone 3, Dist- 95.33km, Ir- 2.442kA
91 | 220kV Katapalli- HINDALCO Ckt-II |  |  |  |  | 0.031944 | 0 | 13 | [7 empty] | 10 | 8760 | 100% | 2.1667 | 87600
|  | 29.08.24 | 06:57 | 29.08.24 | 7:43 | 0:46 | 0 | 13 | [5 empty] | At Lapanga end: R-N, Zone 3, Dist- 95.33km, Ir- 2.442kA
92 | 220kV Katapalli- Bargarh New |  |  |  |  | 0.075 | 13 | 16 | [7 empty] | 52.035 | 8760 | 99.84% | 690.331 | 455826.6
|  | 23.05.24 | 19:14 | 23.05.24 | 19:35 | 0:21 | 0 | 21 | [5 empty] | At Bargarh New end: Earth Fault,IA-0.09kA, IB-0.25kA,IC-0.21kA
|  | 29.08.24 | 06:57 | 29.08.24 | 8:15 | 1:18 | 0 | 46 | [5 empty] | At Bargarh New end: Dist Protection,Earth Fault, Ia-1.385kA, Ib-451A, Ic-98.19A
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
93 | 220kV Bargarh New- New Bolangir |  |  |  |  | 0.0048611 | 0 | 7 | [7 empty] | 65.885 | 8760 | 99.85% | 7.6866 | 577152.6
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
94 | 220kV Katapalli- Bolangir PG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 118.45 | 8760 | 100% | 0 | 1037622
95 | 220kV Bolangir PG- New Bolangir Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
96 | 220kV New Bolangir- Kesinga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 83.356 | 8760 | 100% | 0 | 730198.56
97 | 220kV Bolangir PG- Kesinga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 80.596 | 8760 | 100% | 0 | 706020.96
98 | 220kV Bolangir PG- New Bolangir Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.7 | 8760 | 100% | 0 | 23652
99 | 220kV Keonjhar PG - Keonjhar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
100 | 220kV Keonjhar PG - Keonjhar Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15 | 8760 | 100% | 0 | 131400
101 | 220kV Kuchei PG-Balasore Ckt I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
102 | 220kV Kuchei PG-Balasore Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 76.859 | 8760 | 100% | 0 | 673284.84
103 | 220kV Lapanga-Katapali Ckt-I |  |  |  |  | 0.12153 | 0 | 46 | [7 empty] | 49.72 | 8760 | 99.99% | 38.1187 | 435547.2
|  | 29.08.24 | 06:57 | 29.08.24 | 9:52 | 2:55 | 0 | 46 | [5 empty] | At Lapanga end: R-N, Zone 3, Dist- 95.01km, Ir- 2.439kA At Katapali end: O/C
104 | 220kV Lapanga-Katapali Ckt-II |  |  |  |  | 0.031944 | 0 | 46 | [7 empty] | 49.72 | 8760 | 99.99% | 38.1187 | 435547.2
|  | 29.08.24 | 06:57 | 29.08.24 | 7:43 | 0:46 | 0 | 46 | [5 empty] | At Lapanga end: R-N, Zone 3, Dist- 95.33km, Ir- 2.442kA
105 | 220kV Laxmipur - Therubali ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59 | 8760 | 100% | 0 | 516840
106 | 220kV Laxmipur - Therubali ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59 | 8760 | 100% | 0 | 516840
107 | 220kV Laxmipur - Utkal Alumina (Aditya) ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
108 | 220kV Laxmipur - Utkal Alumina (Aditya) ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.04 | 8760 | 100% | 0 | 271910.4
109 | 220kV Laxmipur - NALCO ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 8760 | 100% | 0 | 324032.4
110 | 220kV Laxmipur - NALCO ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 36.99 | 8760 | 100% | 0 | 324032.4
111 | 220kV Laxmipur - Laxmipur RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.45 | 8760 | 100% | 0 | 21462
112 | 220kV Meramundali-Bhusan (Tata BSL) Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
113 | 220kV Meramundali-Bhusan (Tata BSL) Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.4 | 8760 | 100% | 0 | 21024
114 | 220kV Meramundali-Duburi |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 95.556 | 8760 | 100% | 30.2594 | 837070.56
|  | 12.08.24 | 15:56 | 12.08.24 | 16:15 | 0:19 | 0 | 19 | [5 empty] | At Meramundali B end: Dist Protection
115 | 220kV Meramundali-Meramundali(B)-Duburi 'T' Connection |  |  |  |  | 0.013194 | 0 | 19 | [7 empty] | 0.658 | 8760 | 100% | 0.20837 | 5764.08
|  | 12.08.24 | 15:56 | 12.08.24 | 16:15 | 0:19 | 0 | 19 | [5 empty] | At Meramundali B end: Dist Protection
116 | 220kV Meramundali-Goda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 70.97 | 8760 | 100% | 0 | 621697.2
117 | 220kV Goda-Duburi |  |  |  |  | 0.060417 | 1 | 16 | [7 empty] | 36.69 | 8760 | 99.99% | 46.474 | 321404.4
|  | 05.05.24 | 12:05 | 05.05.24 | 13:32 | 1:27 | 1 | 16 | [5 empty] | At Goda end: O/C, Ir- 0.396kA, Iy- 0.408kA, Ib- 0.334kA
118 | 220kV Meramundali-Meramundali(B)-Goda 'T' Connection |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.658 | 8760 | 100% | 0 | 5764.08
119 | 220kV NALCO-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
120 | 220kV NALCO-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.465 | 8760 | 100% | 0 | 100433.4
121 | 220kV Narendrapur-Atri Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
122 | 220kV Atri-Mendhasal Ckt-I |  |  |  |  | 0.10417 | 0 | 40 | [7 empty] | 24.85 | 8760 | 99.99% | 16.5667 | 217686
|  | 29.09.24 | 15:47 | 29.09.24 | 18:17 | 2:30 | 0 | 40 | [5 empty] | At Mendhasal end: Distance Protection,IY=9.5kA, Distance=5.1KM, ZONE- 1
123 | 220kV Narendrapur-Atri Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 150.35 | 8760 | 100% | 0 | 1317066
124 | 220kV Narendrapur-Tata Gopalpur Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.1 | 8760 | 100% | 0 | 70956
125 | 220kV Narendrapur-Tata Gopalpur Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 8.1 | 8760 | 100% | 0 | 70956
126 | 220kV Atri-Infocity-II Ckt-II |  |  |  |  | 0.98958 | 0 | 56 | [7 empty] | 21.3 | 8760 | 99.99% | 19.88 | 186588
|  | 28.04.24 | 17:54 | 28.04.24 | 19:15 | 1:21 | 0 | 16 | [5 empty] | At Atri end: Y-N, Zone 1, Dist- 0.739km, Iy- 10.71kA
|  | 29.09.24 | 15:47 | 30.09.24 | 14:11 | 22:24 | 0 | 40 | [5 empty] | At Infocity -II end: Earth Fault,with following fault current indications:- Ir- 22.29A, Iy- 200A, Ib- 5.028KA At Atri end: Distance Protection,DP relay operated, B phase-N, IR= 22.29 A, IY= 200 A, IB= 5.20 kA, Zone-1, Distance= 13.2 km
127 | 220kV Infocity-II-Mendhasal |  |  |  |  | 0.022917 | 0 | 33 | [7 empty] | 5.47 | 8760 | 99.99% | 3.0085 | 47917.2
|  | 29.09.24 | 15:47 | 29.09.24 | 16:20 | 0:33 | 0 | 33 | [5 empty] | At Infocity -II end: Earth Fault,Earth Fault with fault current Indication IR 0.08KA IY 1.85KA IB 8.4KA
128 | 220kV New Duburi -Dhamara |  |  |  |  | 0.14236 | 14 | 20 | [7 empty] | 125.881 | 8760 | 99.84% | 1804.2943 | 1102717.56
|  | 12.08.24 | 15:56 | 12.08.24 | 17:14 | 1:18 | 0 | 25 | [5 empty] | B-N, Zone 4, Ir- 0304kA, Iy- 0.13kA, Ib- 0.831kA
|  | 18.08.24 | 14:45 | 18.08.24 | 15:33 | 0:48 | 0 | 48 | [5 empty] | At New Duburi end: Dist Protection
|  | 21.12.24 | 03:50 | 21.12.24 | 5:09 | 1:19 | 1 | 7 | [5 empty] | At New Duburi end: Bus bar Relay & 96 Relay OPTD
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
129 | 220kV Dhamara -Balasore |  |  |  |  | 0 | 0 | 0 | [7 empty] | 85.995 | 8760 | 100% | 0 | 753316.2
130 | 220kV New Duburi -Bhadrak |  |  |  |  | 0.10417 | 13 | 39 | [7 empty] | 73.798 | 8760 | 99.84% | 1007.3427 | 646470.48
|  | 12.05.24 | 14:58 | 12.05.24 | 15:49 | 0:51 | 0 | 51 | [5 empty] | At Bhadrak end: Remote End Tripping,IL1-2.05KA,IL2-0.41KA, IL3-0.83KA
|  | 12.08.24 | 15:56 | 12.08.24 | 17:12 | 1:16 | 0 | 25 | [5 empty] | At Bhadrak end: Zone 2, O/C (B Ph), Ib-1.497kA, Dist- 67.34km
|  | 17.09.24 | 10:20 | 17.09.24 | 10:43 | 0:23 | 0 | 23 | [5 empty] | At New Duburi end: E/F ( Y Ph), Zone 3, Dist- 110.8km, Iy- 2.15kA At Bhadrak end: R-Y Ph, Zone 1, Dist- 35.3km, Ir- 5.63kA, Iy- 5.35kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
131 | 220kV New Duburi-Paradeep Ckt-I |  |  |  |  | 0.35833 | 18 | 57 | [7 empty] | 113.433 | 1236 | 98.47% | 2149.5554 | 140203.188
|  | 20.06.24 | 12:41 | 20.06.24 | 12:46 | 0:05 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,O/C R,Y,B , Ir= 750 A , Iy= 1.02 kA , Ib= 1.18 kA
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
|  | 18.08.24 | 14:45 | 18.08.24 | 21:28 | 6:43 | 6 | 8 | [5 empty] | At New Duburi end: Zone 1 IL1-7.09kA IL2-6.9kA IL3-1.4kA Dist-0.2km At Paradeep end: O/C,Due to CT burst of jindal ckt II at New duburi end
|  | 27.12.24 | 22:32 | 27.12.24 | 23:00 | 0:28 | 0 | 19 | [5 empty] | At New Duburi end: No indication At Paradeep end: O/C (R-Y-B), Zone 4, Dist- 0km, Ir- 1.65kA, Iy- 1.513kA, Ib- 1.582kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
132 | 220kV New Duburi-Balichandrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 55.54 | 7524 | 100% | 0 | 417882.96
133 | 220kV Balichandrapur- Paradeep |  |  |  |  | 0 | 0 | 0 | [7 empty] | 57.45 | 7524 | 100% | 0 | 432253.8
134 | 220kV New Duburi-Paradeep Ckt-II |  |  |  |  | 0.20972 | 13 | 56 | [7 empty] | 113.433 | 8760 | 99.84% | 1580.4998 | 993673.08
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:17 | 1:21 | 0 | 25 | [5 empty] | At New Duburi end: Bus Bar Protection, Dist- 111.6km, Ir- 0.312kA, Iy- 0.195kA, Ib- 0.506kA At Paradeep end: O/C (B Ph), Zone 2, Dist- 111.6km, Ir- 0.392kA, Iy- 0.574kA, Ib- 0.941kA
|  | 21.12.24 | 03:50 | 21.12.24 | 5:14 | 1:24 | 1 | 7 | [5 empty] | At New Duburi end: Bus bar Relay & 96 Relay OPTD
|  | 27.12.24 | 22:32 | 27.12.24 | 22:55 | 0:23 | 0 | 19 | [5 empty] | At New Duburi end: Dist- 147.8km, Ir- 1.98kA, Iy- 1.97kA, Ib- 1.99kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
135 | 220kV Paradeep - IOCL Ckt |  |  |  |  | 0.15139 | 12 | 53 | [7 empty] | 6 | 8760 | 99.85% | 77.3 | 52560
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.07.24 | 03:33 | 12.07.24 | 3:56 | 0:23 | 0 | 23 | [5 empty] | At Paradeep end: E/F (B-N), Zone 1, Dist- 2.72km, Ib- 9.16kA
|  | 12.08.24 | 15:56 | 12.08.24 | 17:17 | 1:21 | 0 | 25 | [5 empty] | At New Duburi end: Bus Bar Protection, Dist- 111.6km, Ir- 0.312kA, Iy- 0.195kA, Ib- 0.506kA At Paradeep end: O/C (B Ph), Zone 2, Dist- 111.6km, Ir- 0.392kA, Iy- 0.574kA, Ib- 0.941kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
136 | 220kV Paradeep - ESSAR Steel Ckt -I |  |  |  |  | 0.13542 | 0 | 30 | [7 empty] | 8.868 | 8760 | 99.99% | 4.434 | 77683.68
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:17 | 1:21 | 0 | 25 | [5 empty] | At New Duburi end: Bus Bar Protection, Dist- 111.6km, Ir- 0.312kA, Iy- 0.195kA, Ib- 0.506kA At Paradeep end: O/C (B Ph), Zone 2, Dist- 111.6km, Ir- 0.392kA, Iy- 0.574kA, Ib- 0.941kA
137 | 220kV Paradeep - ESSAR Steel Ckt -II |  |  |  |  | 0.13542 | 0 | 30 | [7 empty] | 8.868 | 8760 | 99.99% | 4.434 | 77683.68
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:17 | 1:21 | 0 | 25 | [5 empty] | At New Duburi end: Bus Bar Protection, Dist- 111.6km, Ir- 0.312kA, Iy- 0.195kA, Ib- 0.506kA At Paradeep end: O/C (B Ph), Zone 2, Dist- 111.6km, Ir- 0.392kA, Iy- 0.574kA, Ib- 0.941kA
138 | 220kV Rengali PH-Nalco-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 71.337 | 8760 | 100% | 0 | 624912.12
139 | 220kV Rengali GD-Rengali PG -I |  |  |  |  | 1899-12-31 00:29 | 1 | 22 | [7 empty] | 0.4 | 8760 | 99.98% | 0.54667 | 3504
|  | 21.05.24 | 18:08 | 22.05.24 | 18:37 | 1899-12-31 00:29 | 1 | 22 | [5 empty] | At Rengali end: Distance Protection,DP operated, Zone 4, Dist= 0.2 km. Ir=0.42 kA, Iy=2.87 kA, Ib=0.38 kA
140 | 220kV Rengali GD-Rengali PG -II |  |  |  |  | 0.036111 | 1 | 22 | [7 empty] | 0.4 | 8760 | 99.98% | 0.54667 | 3504
|  | 21.05.24 | 18:08 | 21.05.24 | 19:00 | 0:52 | 1 | 22 | [5 empty] | At Rengali end: Distance Protection,ABCN Phase, Zone-3, Distance=0.1 km, Ir=0.48kA Iy=2.92kA Ib=0.34kA
141 | 220kV Rengali GD-Chandiposh (T)-Tarkera - II |  |  |  |  | 0.022917 | 0 | 33 | [7 empty] | 162.08 | 8760 | 99.99% | 89.144 | 1419820.8
|  | 21.05.24 | 18:32 | 21.05.24 | 19:05 | 0:33 | 0 | 33 | [5 empty] | At Rengali end: SOTFB-N phase, AR lockout, Ir= 207 A, Iy=1.48 kA, Ib= 87 kA
142 | 220kV Rengali GD-Deogarh |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 54.8 | 8760 | 100% | 13.7 | 480048
|  | 21.05.24 | 18:08 | 21.05.24 | 18:23 | 0:15 | 0 | 15 | [5 empty] | At Barkote end: Remote End Tripping,Distance Protection Fault, Zone-II, Fault Distance= 94.4KM, Fault Current(IL1=0.16KA, IL2=0.12KA, IL3=0.04KA)
143 | 220kV Deogarh-Barkote |  |  |  |  | 0.010417 | 0 | 15 | [7 empty] | 23.2 | 8760 | 100% | 5.8 | 203232
|  | 21.05.24 | 18:08 | 21.05.24 | 18:23 | 0:15 | 0 | 15 | [5 empty] | At Barkote end: Remote End Tripping,Distance Protection Fault, Zone-II, Fault Distance= 94.4KM, Fault Current(IL1=0.16KA, IL2=0.12KA, IL3=0.04KA)
144 | 220kV Rengali PH-Rengali GD -I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
145 | 220kV Rengali PH-Rengali GD -II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 5 | 8760 | 100% | 0 | 43800
146 | 220kV Rengali PH -STPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 29.5 | 8760 | 100% | 0 | 258420
147 | 220kV STPS (Kaniha)-TTPS |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 34.5 | 8760 | 100% | 0 | 302220
148 | 220kV STPS (Kaniha)-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
149 | 220kV STPS (Kaniha)-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 42.52 | 8760 | 100% | 0 | 372475.2
150 | 220kV Tarkera-Kuarnmunda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 30.47 | 8760 | 100% | 0 | 266917.2
151 | 220kV Kuarnmunda-Budhipadar |  |  |  |  | 0.93819 | 15 | 20 | [7 empty] | 111.4 | 8760 | 99.82% | 1708.1333 | 975864
|  | 22.05.24 | 12:29 | 22.05.24 | 12:43 | 0:14 | 0 | 14 | [5 empty] | At Budhipadar end: O/C,At Budhipadar end:D/P Operated (MiCom P444): FL= Bph-E, F.D=87.1 km, F. Dur= 413.6 ms, Ia=181.6 A, Ib=271.8 A, Ic=1.437 kA, F.R= 61.26 Ohm, Zone2
|  | 05.06.24 | 4:35 | 05.06.24 | 5:37 | 1:02 | 1 | 2 | [5 empty] | H/T for restoration of power supply
|  | 20.06.24 | 16:56 | 20.06.24 | 18:15 | 1:19 | 1 | 19 | [5 empty] | D/P(MICOM P444): F.L- C-N, ZONE 1, F.D-5.3km,IL1-43.05A,IL2-44.07A,IL3-17.89ka,F.dur-71.44ms D/P(Siemens 7SA52): F.L- L3-N, ZONE 1, F.D-5.3km,IL1-0.04KA,IL2-0.05KA,IL3-18.41ka
|  | 06.09.24 | 17:09 | 07.09.24 | 13:05 | 19:56 | 0 | 45 | [5 empty] | At Budhipadar end: Over Current,DP1 (MiCOM P444):- F.L=B-n, Zone1, F.D=61.3 km, F.Du=71.74 ms, Ia=504 A, Ib=3.144 kA, Ic= 436.6 A, DP2 (MiCOM 7SA52):- F.L=L2-E, Zone1, F.D=59[59.7%] km, F.Du=71.74 ms, Ia=0.2 KA, Ib=2.92 kA, Ic= 0.31 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
152 | 220kV Tarkera-Bamra |  |  |  |  | 0.14861 | 1 | 35 | [7 empty] | 70.2 | 8760 | 99.98% | 111.15 | 614952
|  | 01.06.24 | 19:30 | 01.06.24 | 22:03 | 2:33 | 1 | 30 | [5 empty] | At Tarkera end: Distance Protection, DP MAIN1: DIST= 57.475 KM, LOOP=L1-N, ZONE-2, IL1=2644.49 A, IN= 2668.91 A DP MAIN2 : DIST=57.97 KM, ZONE-2, LOOP : A-N, IA= 2.487 A, MT OPERATED
|  | 03.06.24 | 20:04 | 03.06.24 | 21:05 | 1:01 | 0 | 5 | [5 empty] | At Tarkera end: Distance Protection,DP1 :- ZONE-2, DIST=54.63 KM, LOOP :- A-N, IA=2.72 KA, IB=781.3 A, IC=202.4 A, FAULT RESISTANCE=1.814 OHM,DP2 :- ZONE-2, DIST=62.969 KM, LOOP :- L1-N, IL1=2.706 KA, IL2=776.06 A, IL3=186.74 A At Bamra end: Distance Protection,D.P-1, Fault Loop- L1-N, Zone- 1, Distance-401.5MTR, F.D- 53.27ms, RTT=79.91ms, Ia=4.387KA, Ib=770.6A, Ic=217.6 D.P-2, Fault Loop- L1-N, Zone- 1, Distance- 0.6KM, Ia= 4697.800A, Ib= 780.121A, Ic=206.781A, In=5176.955A
153 | 220kV Bamra-Budhipadar |  |  |  |  | 0.36042 | 14 | 41 | [7 empty] | 51.5 | 8760 | 99.83% | 756.1917 | 451140
|  | 09.05.24 | 16:47 | 09.05.24 | 18:00 | 1:13 | 1 | 13 | [5 empty] | At Budhipadar end: O/C (R-N), Zone 1, Dist- 21.83km, Ir- 3.316kA At Bamra end: O/C (R-N), Zone 1, Dist- 26.71km, Ir- 2.28kA
|  | 03.06.24 | 20:04 | 03.06.24 | 20:09 | 0:05 | 0 | 5 | [5 empty] | At Budhipadar end: Over Current,Budhipadar end:- D/P operated(MiCOM p444): F.L=R-N F.D=51.58 km Ia=1.519 kA Ib=284.3 A Ic=525.7 A F. Resistance=3.1ohm Zone2 F. Duration=74.92 ms
|  | 05.06.24 | 04:12 | 05.06.24 | 10:08 | 5:56 | 0 | 30 | [5 empty] | D/P:-started phase-BC-N, tripped phase-ABC,FD-13.72KM, FD-304.1ms, Zone-4, IL1-111.7A, IL2-414.7A, IL3-431Amp
|  | 30.08.24 | 18:42 | 30.08.24 | 20:07 | 1:25 | 0 | 53 | [5 empty] | At Budhipadar end: A-N, ZONE 1, Dist-27.25km, IA-2.628kA, IB-68.50A, IC-821.8A At Bamra end: E/F, L1-N, Zone- 1, Dist-34.76km, Ia=1.536kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
154 | 220kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
155 | 220kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10 | 8760 | 100% | 0 | 87600
156 | 220kV Tarkera-RSP-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
157 | 220kV Tarkera-RSP-IV |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
158 | 220kV Therubali-Gunupur |  |  |  |  | 0.14861 | 0 | 10 | [7 empty] | 71.911 | 8760 | 100% | 11.9852 | 629940.36
|  | 06.06.24 | 18:31 | 06.06.24 | 22:05 | 3:34 | 0 | 10 | [5 empty] | At Therubali end: YN,Z1,0.06KM,Iy=8.6KA At Gunupur end: YN,Z2.73.9KM,Iy=869.6A
159 | 220kV Gunupur-Narendrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 149.669 | 8760 | 100% | 0 | 1311100.44
160 | 220kV Therubali-Aska New |  |  |  |  | 0.029167 | 0 | 10 | [7 empty] | 206.7 | 8760 | 100% | 34.45 | 1810692
|  | 06.06.24 | 18:33 | 06.06.24 | 19:15 | 0:42 | 0 | 10 | [5 empty] | At Aska New end: Earth Fault,Aska New end: rnALSTOM P444 D.P relay: A/.R lockout,Y phase to E/f,zone 2,distance= 197.7Km and IY= 667.5A. SIEMENS SIPROTEC 7SA52 D.P relay: A/R lockout,zone 2,L2E , distance=198.7Km and IL2= 0.79KA. At Therubali end: No tripping.
161 | 220kV Aska New-Narendrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 73.48 | 8760 | 100% | 0 | 643684.8
162 | 220kV Therubali-Bhanjanagar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 171.46 | 8760 | 100% | 0 | 1501989.6
163 | 220kV Therubali-Bhanjanagar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 171.46 | 8760 | 100% | 0 | 1501989.6
164 | 220kV Bhanjanagar- Aska New - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.6 | 8760 | 100% | 0 | 250536
165 | 220kV Bhanjanagar- Aska New - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.6 | 8760 | 100% | 0 | 250536
166 | 220kV TTPS-Meramundali-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
167 | 220kV TTPS-Meramundali-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 11.155 | 8760 | 100% | 0 | 97717.8
168 | 220kV TTPS- Telkoi |  |  |  |  | 0.73125 | 16 | 13 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 78.769 | 8760 | 99.81% | 1277.3706 | 690016.44
|  | 03.05.24 | 12:32 | 03.05.24 | 15:37 | 15:37 | 2 | 48 | [5 empty] | At TTPS end: Ir- 0.019kA, Iy- 0.076kA, Ib- 0.125kA
|  | 16.08.24 | 03:55 | 16.08.24 | 5:04 | 1:09 | 0 | 46 | [5 empty] | At TTPS end: Zone 1, Dist- 92.82km, Ir- 137.5A, Iy- 2.566kA, Ib- 2.504kA
|  | 07.09.24 | 12:53 | 07.09.24 | 13:40 | 0:47 | 0 | 39 | [5 empty] | At TTPS end: (i) ZONE-1 (ii) Dist-126.6 KM (iv) Ia=0 A , Ib=0 A , Ic =30.88 A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
169 | 220kV Telkoi- Joda |  |  |  |  | 0.1875 | 16 | 13 | [7 empty] | 103.227 | 8760 | 99.81% | 1673.9978 | 904268.52
|  | 03.05.24 | 12:32 | 03.05.24 | 15:37 | 3:05 | 2 | 48 | [5 empty] | At TTPS end: Ir- 0.019kA, Iy- 0.076kA, Ib- 0.125kA
|  | 16.08.24 | 03:55 | 16.08.24 | 4:41 | 0:46 | 0 | 46 | [5 empty] | At Joda end: Y-B-N, Zone 1, Dist- 76.9km, iy- 1.569kA, Ib- 1.606kA At Telkoi end: Y-B-N, Zone 1, Dist- 17.44km, Iy- 2.361kA, Ib- 2.29kA
|  | 07.09.24 | 12:53 | 07.09.24 | 13:32 | 0:39 | 0 | 39 | [5 empty] | At Telkoi end: R-Y-N, Zone 1, Dist- 43.54km, Ir- 2.066kA, Iy- 1.878kA At Joda end: R-Y-N, Zone 1, Dist- 50.82km, Ir- 1.823kA, Iy- 1.842kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
170 | 220kV TTPS-Joda |  |  |  |  | 0.061111 | 1 | 19 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 154 | 8760 | 99.98% | 202.7667 | 1349040
|  | 16.08.24 | 03:55 | 16.08.24 | 4:50 | 0:55 | 0 | 46 | [5 empty] | At Joda end: Y-B-N, Zone 1, Dist- 78km, Iy- 1.503kA, Ib- 1.597kA At Telkoi end: Y-B-N, Zone 1, Dist- 66.78km, Iy- 3.642kA, Ib- 3.472kA
|  | 07.09.24 | 12:53 | 07.09.24 | 13:26 | 0:33 | 0 | 33 | [5 empty] | At Joda end: R-Y-N, Zone 1, Dist- 52.04km, Ir- 1.619kA, Iy- 1.74kA At TTPS end: R-Y-N, Zone 1, Dist- 90.40km, Ir- 2.76kA, Iy- 2.542kA
171 | 220kV U. Kolab-Jayanagar-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
172 | 220kV U. Kolab-Jayanagar-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 6 | 8760 | 100% | 0 | 52560
173 | 220kV U. Kolab-Therubali Ckt-III |  |  |  |  | 0.035417 | 0 | 20 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 128 | 8760 | 100% | 42.6667 | 1121280
|  | 06.06.24 | 18:31 | 06.06.24 | 19:22 | 0:51 | 0 | 20 | [5 empty] | At Upper Kolab end: Y-N, Zone 2, Dist-156.3km, Iy- 0.775kA
132 KV
174 | 132kV Akhusing-Mohana |  |  |  |  | 1899-12-31 21:43 | 14 | 54 | [7 empty] | 69.2 | 8760 | 99.83% | 1031.08 | 606192
|  | 18.04.24 | 12:32 | 18.04.24 | 12:37 | 0:05 | 0 | 5 | [5 empty] | B-N Fault
|  | 06.05.24 | 16:45 | 07.05.24 | 12:34 | 18:07 | 0 | 51 | [5 empty] | At Mohana end: Distance Protection,At Akhusingh end: Dist=14.3Km, Ir=0.05Ka, Iy=0.45Ka, Ib=0.04Ka
|  | 14.05.24 | 15:06 | 15.05.24 | 13:43 | 22:37 | 0 | 15 | [5 empty] | At Mohana end: Earth Fault,IL1=0.05Ka, IL2=0.54Ka, IL3=0.03Ka [From Digapahandi end]
|  | 05.06.24 | 15:54 | 05.06.24 | 19:17 | 3:23 | 0 | 12 | [5 empty] | At Mohana end: Distance Protection,At Digapahandi end: Dist=42.84km, IR=47A, IY=1324A, IB=31A, IG=1249A
|  | 2024-10-12 | 17:11 | 2024-10-12 | 17:25 | 0:14 | 0 | 14 | [5 empty] | Supply failure from Machkund
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 20 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 8 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 27 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 22 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
175 | 132kV Akhusing-Parlakhemundi |  |  |  |  | 0.98819 | 35 | 40 | [7 empty] | 76.1 | 8760 | 99.59% | 2714.2333 | 666636
|  | 18.04.24 | 12:32 | 18.04.24 | 12:37 | 0:05 | 0 | 5 | [5 empty] | B-N Fault
|  | 20.05.24 | 18:25 | 20.05.24 | 18:39 | 0:14 | 0 | 14 | [5 empty] | TRIPPED ON O/C
|  | 28.08.24 | 14:44 | 28.08.24 | 14:52 | 0:08 | 0 | 8 | [5 empty] | At Podagada end: Dist Protection,Dist- 55.4 km, Y-Ph fault, IL1= 0.34kA, IL2= 0.95kA, IL3= 0.15kA
|  | 2024-10-12 | 17:11 | 2024-10-12 | 17:25 | 0:14 | 0 | 14 | [5 empty] | Supply failure from Machkund
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 20 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 8 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 27 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 22 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
|  | 2024-10-27 | 11:44 | 2024-10-28 | 3:34 | 15:50 | 15 | 50 | [5 empty] | At Paralakhemundi end: Zone 1, Ib- 4.56kA
|  | 3.11.24 | 11:11 | 3.11.24 | 16:37 | 5:26 | 5 | 26 | [5 empty] | At Akhusingh-Tripped on E/F due to 132kV B Ph CT fault at Paralakhemundi GSS. [TRIPPED AT AKHUSING END ON DP RELAY AT 11:11 BUT CHARGERD AT 11:37 BUT AGAIN TRIPPED ON SAME FAULT.]
|  | 14.11.24 | 10:47 | 14.11.24 | 11:16 | 0:29 | 0 | 26 | [5 empty] | Machkund supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
176 | 132kV Akhusing-Gunupur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.296 | 8760 | 100% | 0 | 204072.96
177 | 132kV Gunupur- Palasingi RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 16.214 | 8760 | 100% | 0 | 142034.64
178 | 132kV Gunupur- Parlakhemundi |  |  |  |  | 0 | 0 | 0 | [7 empty] | 62.6 | 756 | 100% | 0 | 47325.6
179 | 132kV Angul-Boinda |  |  |  |  | 0.15 | 14 | 3 | [7 empty] | 38.1 | 8760 | 99.84% | 535.305 | 333756
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 46 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 11.05.24 | 11:49 | 11.05.24 | 12:06 | 0:17 | 0 | 17 | [5 empty] | At Angul end: Remote End Tripping,CB did not trip at Boinda end.
|  | 20.06.24 | 19:38 | 20.06.24 | 20:10 | 0:32 | 0 | 17 | [5 empty] | At Angul end: Remote End Tripping, CB didnot trip at Boinda end
|  | 28.08.24 | 19:51 | 28.08.24 | 20:22 | 0:31 | 0 | 31 | [5 empty] | At Angul end: Tripped on DP Relay,Fault Abs. Dist-20.588km,Fault Loop -L3N, fault current=3.5kA At Boinda end: No tripping
|  | 4.11.24 | 12:20 | 4.11.24 | 12:32 | 0:12 | 0 | 12 | [5 empty] | At Angul end: Tripped on B/U Relay,fault current=2.06KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
180 | 132kV Boinda- RTSS Boinda |  |  |  |  | 0.22708 | 14 | 2 | [7 empty] | 2.947 | 8760 | 99.84% | 41.3562 | 25815.72
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 13 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 11.05.24 | 11:49 | 11.05.24 | 12:06 | 0:17 | 0 | 17 | [5 empty] | At Angul end: Remote End Tripping,CB did not trip at Boinda end.
|  | 26.05.24 | 18:10 | 26.05.24 | 18:28 | 0:18 | 0 | 18 | [5 empty] | At Rairakhol end: Earth Fault,O/C,Ia=343 amps, Ib=79.2 amps, Ic=173.5 amps, In= 209.44 amps, Ig=212.51 amps,Ia=343 amps, Ib=79.2 amps, Ic=173.5 amps, In= 209.44 amps, Ig=212.51 amps
|  | 02.06.24 | 20:24 | 02.06.24 | 21:57 | 1:33 | 0 | 14 | [5 empty] | DP RELAY INDICATION-3-PH trip,Trip R, Fault abs dist-(-1.00KM),Fault Loop-L1N, IL1- 466.93A ,IL2- 125.00A, IL3- 196.08A
|  | 20.06.24 | 19:38 | 20.06.24 | 20:10 | 0:32 | 0 | 17 | [5 empty] | At Angul end: Remote End Tripping, CB didnot trip at Boinda end
|  | 28.08.24 | 19:51 | 28.08.24 | 20:22 | 0:31 | 0 | 31 | [5 empty] | At Angul end: Tripped on DP Relay,Fault Abs. Dist-20.588km,Fault Loop -L3N, fault current=3.5kA At Boinda end: No tripping
|  | 4.11.24 | 12:20 | 4.11.24 | 12:32 | 0:12 | 0 | 12 | [5 empty] | At Angul end: Tripped on B/U Relay,fault current=2.06KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
181 | 132kV Boinda-Rairakhol |  |  |  |  | 0.38403 | 14 | 22 | [7 empty] | 59 | 8760 | 99.84% | 847.6333 | 516840
|  | 26.05.24 | 18:10 | 26.05.24 | 18:28 | 0:18 | 0 | 18 | [5 empty] | At Rairakhol end: Earth Fault,O/C,Ia=343 amps, Ib=79.2 amps, Ic=173.5 amps, In= 209.44 amps, Ig=212.51 amps,Ia=343 amps, Ib=79.2 amps, Ic=173.5 amps, In= 209.44 amps, Ig=212.51 amps
|  | 02.06.24 | 20:24 | 02.06.24 | 21:57 | 1:33 | 0 | 14 | [5 empty] | DP RELAY INDICATION-3-PH trip,Trip R, Fault abs dist-(-1.00KM),Fault Loop-L1N, IL1- 466.93A ,IL2- 125.00A, IL3- 196.08A
|  | 28.08.24 | 19:51 | 28.08.24 | 20:30 | 0:39 | 0 | 31 | [5 empty] | At Rairakhol end: Remote End Tripping,Incoming power supply to Boinda from Angul grid end failed.
|  | 17.09.24 | 0:33 | 17.09.24 | 0:48 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection,Distance -24.38KM, Current IL1-227.1A, IL2-138.2A, IL3-268.3A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 51.69ms At Boinda end: Distance -21.877KM, Current IL1-1739.51A, IL2-124.43A, IL3-266.12A, fault loop- IL1-E , Zone-1, General trip
|  | 25.09.24 | 03:31 | 25.09.24 | 3:43 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance -25.61KM, Current IL1-170.7A, IL2-161.7A, IL3-297.7A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 46.70ms At Boinda end: Distance -21.845KM, Current IL1-1778.20A, IL2-150.45A, IL3-295.88A, fault loop- IL1-E , Zone-1, General trip
|  | 09.09.24 | 20:45 | 09.09.24 | 20:57 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection At Boinda end: Distance -30.979KM, Current IL1-174.76A, IL2-1194.06A, IL3-49.11A, fault loop- IL2-E , Zone-1, General trip
|  | 21.09.24 | 04:17 | 21.09.24 | 4:32 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection, Distance -27.43KM, Current IL1-281.4A, IL2-88.38A, IL3-272.8A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 50.01ms At Boinda end: Distance -21.456KM, Current IL1-1725.99A, IL2-70.21A, IL3-260A, fault loop- IL1-E , Zone-1, General trip
|  | 2024-10-03 | 02:53 | 2024-10-03 | 3:07 | 0:14 | 0 | 14 | [5 empty] | At Rairakhol end: B-N, Zone 1, Dist- 28.05km, Ib- 0.123kA At Boinda end: B-N, Zone 1, Dist- 21.68km, Ib- 1.63kA
|  | 8.01.25 | 07:13 | 8.01.25 | 12:48 | 5:35 | 0 | 11 | [5 empty] | At Boinda end: Zone 1, Dist- 12.31km, Y-N, Iy- 1.26kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
182 | 132kV Maneswar-Rairakhol |  |  |  |  | 0.59722 | 14 | 37 | [7 empty] | 57.46 | 8760 | 99.83% | 839.8737 | 503349.6
|  | 05.04.24 | 18:29 | 05.04.24 | 19:08 | 0:39 | 0 | 10 | [5 empty] | At Maneswar end: Zone 1, Dist- 14.9km, Ir- 2.98kA
|  | 20.05.24 | 21:21 | 20.05.24 | 21:52 | 0:31 | 0 | 20 | [5 empty] | At Rairakhol end: Distance Protection,Zone- Z1, 2.11 KM, R-phase to Earth, Ir-6 KA
|  | 31.05.24 | 13:05 | 31.05.24 | 13:17 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection,Zone-1 , Distance =40.4KM ,Current IL1-0.42KA, IL2-1.82KA, IL3-0.22KA, fault loop- IL2-E At Maneswar end: Distance Protection,y-PH, Distance-40.4 km, Z1, pu time- 50 ms, trip time- 0 ms (Ir=0.42 Iy=1.82 Ib=0.22 ) kA, E/F -6 ms
|  | 01.06.24 | 13:53 | 01.06.24 | 19:15 | 5:22 | 0 | 7 | [5 empty] | At Rairakhol end: Distance Protection, distance-43.3 km, Ir=0.35 kA,Iy=1.67 kA, Ib=0.22 kA, distance pick up - 50 ms
|  | 01.06.24 | 19:56 | 01.06.24 | 20:06 | 0:10 | 0 | 10 | [5 empty] | At Rairakhol end: Over Current,Directional over current & earth fault operated, Trip A/B , LBB initiated, Ir=0.54 kA, Iy=0.54 kA, Ib=0.52 kA
|  | 01.06.24 | 20:47 | 01.06.24 | 23:22 | 2:35 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance-17.8 km, trip time-0 ms, Y & B ph , pu time - 53 ms, LE 2-3. Ir=0.22 kA, Iy=3.16 kA, Ib=3.39 kA
|  | 07.08.24 | 10:36 | 07.08.24 | 11:54 | 1:18 | 0 | 13 | [5 empty] | Supply failure from Sambalpur grid end
|  | 24.08.24 | 12:13 | 25.08.24 | 14:40 | 2:26 | 0 | 6 | [5 empty] | At Rairakhol end: Dist Protection,
|  | 05.09.24 | 00:47 | 05.09.24 | 1:03 | 0:16 | 0 | 16 | [5 empty] | Tripped at Rairakhol Grid end
|  | 17.09.24 | 0:33 | 17.09.24 | 0:48 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection,Distance -24.38KM, Current IL1-227.1A, IL2-138.2A, IL3-268.3A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 51.69ms At Boinda end: Distance -21.877KM, Current IL1-1739.51A, IL2-124.43A, IL3-266.12A, fault loop- IL1-E , Zone-1, General trip
|  | 25.09.24 | 03:31 | 25.09.24 | 3:43 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance -25.61KM, Current IL1-170.7A, IL2-161.7A, IL3-297.7A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 46.70ms At Boinda end: Distance -21.845KM, Current IL1-1778.20A, IL2-150.45A, IL3-295.88A, fault loop- IL1-E , Zone-1, General trip
|  | 2024-10-03 | 02:53 | 2024-10-03 | 3:07 | 0:14 | 0 | 14 | [5 empty] | At Rairakhol end: B-N, Zone 1, Dist- 28.05km, Ib- 0.123kA At Boinda end: B-N, Zone 1, Dist- 21.68km, Ib- 1.63kA
|  | 26.03.25 | 15:16 | 26.03.25 | 15:26 | 0:10 | 0 | 10 | [5 empty] | At Rairakhol end: Remote End Tripping
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
183 | 132kV Sambalpur-Maneswar |  |  |  |  | 0.82639 | 13 | 0 | [7 empty] | 11.2 | 8760 | 99.85% | 145.6 | 98112
|  | 20.05.24 | 21:21 | 20.05.24 | 21:56 | 0:35 | 0 | 24 | [5 empty] | At Maneswar end: Distance Protection,R ph, Z-1, Distance-8.4 km, pu time- 30 ms, trip time- 10 ms, (0.37, 0.25, 0.42) kA At Sambalpur end: Tripped on Z1, R-ph, Ia=6363A, Ib=251A, Ic=421A, Fault dist.=2.11KM, fault duration= 48.29ms
|  | 16.06.24 | 0:46 | 19.06.24 | 45462.7708 | 17:44 | 0 | 15 | [5 empty] | At Sambalpur end: Tripped on Z1, Bph E/F, Ia=239A, Ib=197A,Ic=3041A, Ig=2729A, Fault dist.=12.64KM, fault duration= 57.477ms At Burla PH end: tripped at 00:03Hr on Z1, Bph, Fault dist.=6.4KM
|  | 07.08.24 | 10:36 | 07.08.24 | 11:54 | 1:18 | 0 | 8 | [5 empty] | Supply failure from Sambalpur grid end
|  | 26.03.25 | 15:16 | 26.03.25 | 15:29 | 0:13 | 0 | 13 | [5 empty] | At Katapali end: O/C, Ir- 0.53kA, Iy- 0.58kA, Ib- 0.56kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
184 | 132kV Maneswar- RTSS Maneswar |  |  |  |  | 0.87361 | 14 | 13 | [7 empty] | 5.2 | 8760 | 99.84% | 73.9267 | 45552
|  | 20.05.24 | 21:21 | 20.05.24 | 21:56 | 0:35 | 0 | 24 | [5 empty] | At Maneswar end: Distance Protection,R ph, Z-1, Distance-8.4 km, pu time- 30 ms, trip time- 10 ms, (0.37, 0.25, 0.42) kA At Sambalpur end: Tripped on Z1, R-ph, Ia=6363A, Ib=251A, Ic=421A, Fault dist.=2.11KM, fault duration= 48.29ms
|  | 16.06.24 | 0:46 | 19.06.24 | 45462.7708 | 17:44 | 0 | 15 | [5 empty] | At Sambalpur end: Tripped on Z1, Bph E/F, Ia=239A, Ib=197A,Ic=3041A, Ig=2729A, Fault dist.=12.64KM, fault duration= 57.477ms At Burla PH end: tripped at 00:03Hr on Z1, Bph, Fault dist.=6.4KM
|  | 07.07.24 | 13:50 | 07.07.24 | 14:01 | 0:11 | 0 | 11 | [5 empty] | At Maneswar end: O/C (R Ph), Ir= 1.048A
|  | 07.08.24 | 10:36 | 07.08.24 | 11:54 | 1:18 | 0 | 13 | [5 empty] | Supply failure from Sambalpur grid end
|  | 05.09.24 | 00:47 | 05.09.24 | 1:03 | 0:16 | 0 | 16 | [5 empty] | Tripped at Rairakhol Grid end
|  | 17.09.24 | 0:33 | 17.09.24 | 0:48 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection,Distance -24.38KM, Current IL1-227.1A, IL2-138.2A, IL3-268.3A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 51.69ms At Boinda end: Distance -21.877KM, Current IL1-1739.51A, IL2-124.43A, IL3-266.12A, fault loop- IL1-E , Zone-1, General trip
|  | 25.09.24 | 03:31 | 25.09.24 | 3:43 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance -25.61KM, Current IL1-170.7A, IL2-161.7A, IL3-297.7A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 46.70ms At Boinda end: Distance -21.845KM, Current IL1-1778.20A, IL2-150.45A, IL3-295.88A, fault loop- IL1-E , Zone-1, General trip
|  | 2024-10-03 | 02:53 | 2024-10-03 | 3:07 | 0:14 | 0 | 14 | [5 empty] | At Rairakhol end: B-N, Zone 1, Dist- 28.05km, Ib- 0.123kA At Boinda end: B-N, Zone 1, Dist- 21.68km, Ib- 1.63kA
|  | 26.03.25 | 15:16 | 26.03.25 | 15:29 | 0:13 | 0 | 13 | [5 empty] | At Katapali end: O/C, Ir- 0.53kA, Iy- 0.58kA, Ib- 0.56kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
185 | 132kV Angul-Nandira (MCL)- I |  |  |  |  | 0.15 | 13 | 43 | [7 empty] | 10.826 | 8760 | 99.84% | 148.4966 | 94835.76
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 44 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 20.06.24 | 19:38 | 20.06.24 | 20:33 | 0:55 | 0 | 22 | [5 empty] | At Angul end: Remote End Tripping,CB didnot trip at MCL end
|  | 04.08.24 | 10:43 | 04.08.24 | 11:20 | 0:37 | 0 | 37 | [5 empty] | At Angul end: O/C (B Ph) & E/F, Ib-3.5kA. CB didnot trip at MCL end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
186 | 132kV Angul-Nandira (MCL)- II |  |  |  |  | 0.15 | 13 | 43 | [7 empty] | 10.826 | 8760 | 99.84% | 148.4966 | 94835.76
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 44 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 20.06.24 | 19:38 | 20.06.24 | 20:33 | 0:55 | 0 | 22 | [5 empty] | At Angul end: Remote End Tripping,CB didnot trip at MCL end
|  | 04.08.24 | 10:43 | 04.08.24 | 11:20 | 0:37 | 0 | 37 | [5 empty] | At Angul end: O/C (B Ph) & E/F, Ib-3.5kA. CB didnot trip at MCL end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
187 | 132kV Joda -Barbil |  |  |  |  | 0.05 | 12 | 55 | [7 empty] | 10.22 | 8760 | 99.85% | 132.0083 | 89527.2
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 20 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 24.03.25 | 20:21 | 24.03.25 | 20:29 | 0:08 | 0 | 8 | [5 empty] | At Joda end: O/C, Ir- 0.26kA, Iy- 0.43kA, Ib- 0.41kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
188 | 132kV Barbil- RML (Karakolha) |  |  |  |  | 0.14167 | 15 | 7 | [7 empty] | 31.811 | 8760 | 99.83% | 480.8763 | 278664.36
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 20 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 21.08.24 | 21:35 | 21.08.24 | 22:58 | 1:23 | 1 | 23 | [5 empty] | At Barbil end:Tripped Phase: ABC, Fault Current: Ia=42A,Ib-43A,Ic=41A At KSP end: Ia=261.1A, Ib-50.89A,Ic=299.4A, Dist.=9.069km
|  | 1.12.24 | 17:16 | 1.12.24 | 17:17 | 0:01 | 0 | 1 | [5 empty] | At Barbil end: Master trip relay operated
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
189 | 132kV Barbil - Bolani |  |  |  |  | 0.083333 | 13 | 36 | [7 empty] | 7.8 | 8760 | 99.84% | 106.08 | 68328
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 13 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
190 | 132kV Bolani - Arya Iron & Steel |  |  |  |  | 0.089583 | 13 | 45 | [7 empty] | 3.17 | 8760 | 99.84% | 43.5875 | 27769.2
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 13 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 25.11.24 | 20:52 | 25.11.24 | 21:01 | 0:09 | 0 | 9 | [5 empty] | P/S failure from Arya end
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
191 | 132kV Arya Iron & Steel- RML (Karakendra) |  |  |  |  | 0.089583 | 13 | 45 | [7 empty] | 12.639 | 8760 | 99.84% | 173.7862 | 110717.64
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 13 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 25.11.24 | 20:52 | 25.11.24 | 21:01 | 0:09 | 0 | 9 | [5 empty] | P/S failure from Arya end
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
192 | 132kV Arya Iron & Steel- BRPL |  |  |  |  | 0.089583 | 13 | 46 | [7 empty] | 9.008 | 8760 | 99.84% | 124.0101 | 78910.08
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 21.08.24 | 20:46 | 21.08.24 | 21:23 | 0:37 | 0 | 14 | [5 empty] | At Joda end: Fault Phase : CAT,Dist-4.07km, Fault Current: Ia=5126A,Ib-173A,Ic=7455A,Ig=2942At Barbil end: Breaker not tripped and no indication
|  | 25.11.24 | 20:52 | 25.11.24 | 21:01 | 0:09 | 0 | 9 | [5 empty] | P/S failure from Arya end
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
193 | 132kV RML (Karakendra)-Nalda RTSS |  |  |  |  | 0.057639 | 13 | 23 | [7 empty] | 6.554 | 8760 | 99.85% | 87.7144 | 57413.04
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
194 | 132kV RML (Karakendra)- RML (Karakolha) |  |  |  |  | 0.057639 | 13 | 23 | [7 empty] | 0.894 | 8760 | 99.85% | 11.9647 | 7831.44
|  | 11.05.24 | 17:27 | 11.05.24 | 17:38 | 0:11 | 0 | 11 | [5 empty] | At Joda end: Distance Protection,132kV Joda-Barbil Feeder tripped only at Joda end.Tripped Phase :- AB TTarget Zone-1Fault current-IL1=7370AIL2=5935AIL3=249A G=1330A Zone-1 Dist-3.79KM At Barbil end: Distance Protection,Fault Current at Barbil end : Ia=627A,Ib=565.8A,Ic=274A,Dist=6.791KM,Zone-I
|  | 08.05.24 | 17:27 | 08.05.24 | 17:43 | 0:16 | 0 | 16 | [5 empty] | At Joda end: O/C,At Joda end: DP relay: AGT, Fault current: A=4958A,B=222A,C=208A,G=4905A,Zone-I.Dist=2.08KM At Barbil end: CB not tripped
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
195 | 132kV Nalda-Beekay Steel |  |  |  |  | 0.063889 | 1 | 32 | [7 empty] | 5.4 | 8760 | 99.98% | 8.28 | 47304
|  | 28.08.24 | 2:00 | 28.08.24 | 2:36 | 0:36 | 0 | 36 | [5 empty] | At Rourkela end: O/C (R-Y-B), Zone 1, Dist- 45.99km, Ir- 2.886kA, Iy- 3.165kA, Ib- 2.916kA
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
196 | 132kV Beekay Steel - Bhalulata RTSS |  |  |  |  | 1899-12-31 19:08 | 3 | 4 | [7 empty] | 27 | 8760 | 99.96% | 82.8 | 236520
|  | 28.08.24 | 2:00 | 28.08.24 | 2:36 | 0:36 | 0 | 36 | [5 empty] | At Rourkela end: O/C (R-Y-B), Zone 1, Dist- 45.99km, Ir- 2.886kA, Iy- 3.165kA, Ib- 2.916kA
|  | 22.03.25 | 08:32 | 22.03.25 | 9:28 | 0:56 | 0 | 56 | [5 empty] | At Barbil end: B-N, Zone 1, Dist- 7.02km, Ib- 4.04kA No tripping at Bolani end
197 | 132 kV Aska New -Chatrapur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 48.8 | 8760 | 100% | 0 | 427488
198 | 132 kV Aska-Aska New-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.98 | 8760 | 100% | 0 | 61144.8
199 | 132kV Aska New- Hinjili |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.6 | 8760 | 100% | 0 | 215496
200 | 132kV Hinjili- Berhampur |  |  |  |  | 0.84931 | 0 | 30 | [7 empty] | 16.77 | 8760 | 99.99% | 8.385 | 146905.2
|  | 21.08.24 | 18:57 | 23.08.24 | 15:20 | 20:23 | 0 | 30 | [5 empty] | At Hinjili end: Dist Protection,Micom P442,Zone 1,Fault Dist-747.6m,Fault records ,IA-145.5A,IB-27.72A,IC-3.108kA At Berhampur end: DP RELAY B-phase,ZONE-2,Dist-,Ib-3.56kA
201 | 132kV Aska- Aska New- I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.66 | 8760 | 100% | 0 | 58341.6
202 | 132 kV Aska-Purusottampur |  |  |  |  | 0.017361 | 0 | 16 | [7 empty] | 28.21 | 8760 | 100% | 7.5227 | 247119.6
|  | 19.06.24 | 11:16 | 19.06.24 | 11:41 | 0:25 | 0 | 16 | [5 empty] | At Purusottampur end: Distance Protection,Tripped with Distance protection Relay, A/R Block, A/R Lockout, o/c in R-phase, fault current- IL1- 1.73 KA, IL2- 0.01 KA, IL3- 0.01 KA, Zone-2, Distance-17.4 KM. At Aska end: A/R OPERATED,Z-1,DIST-21.42K.M, R-N,IA-1.838KA,IB-130.8A,IC-155.9A
203 | 132 kV Aska New-Digapahandi-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.187 | 8760 | 100% | 0 | 334518.12
204 | 132 kV Aska New-Digapahandi-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 38.187 | 8760 | 100% | 0 | 334518.12
205 | 132 kV Balasore-Udala |  |  |  |  | 1899-12-31 03:02 | 13 | 25 | [7 empty] | 70.86 | 8760 | 99.85% | 950.705 | 620733.6
|  | 18.04.24 | 13:47 | 18.04.24 | 13:59 | 0:12 | 0 | 12 | [5 empty] | At Balasore end: R-N, Dist- 84.84km, Ir- 0.955kA, Iy-0.826kA, Ib- 0.589kA
|  | 15.06.24 | 21:27 | 15.06.24 | 23:03 | 1:36 | 0 | 13 | [5 empty] | H/T from Udala grid end as per Instruction of SLDC
|  | 20.06.24 | 12:32 | 20.06.24 | 13:58 | 1:26 | 0 | 16 | [5 empty] | At Balasore end: Distance Protection,Y-ph & B-ph optd,Dist optd,Zone-1,carrier send, Dist-55.75KM,Fault current Ir-172A,Iy-193A,Ib-1929A,In-1.5KA. At Udala end: Distance Protection
|  | 28.06.24 | 23:32 | 29.06.24 | 15:13 | 15:41 | 0 | 8 | [5 empty] | At Udala end: Remote End Tripping
|  | 03.07.24 | 8:00 | 03.07.24 | 8:09 | 0:09 | 0 | 9 | [5 empty] | At Udala end: DC Earth fault
|  | 21.09.24 | 07:32 | 21.09.24 | 15:30 | 7:58 | 0 | 27 | [5 empty] | At Balasore end: Distance Protection, First Fault: Dist R-ph ,Y-ph Optd,Zone-1,Auto reclose operated , Dist-5.89 KM, fault current-Ir=132A, Iy=9.1 KA, Ib=120A. Second Fault:Dist operated Y-ph operated,Zone-1,fault current Ir-21A,Iy-9.385A,Ib-17A,In-9389A.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
206 | 132 kV Betanati-Udala |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 49.89 | 8760 | 100% | 10.8095 | 437036.4
|  | 18.04.24 | 13:47 | 18.04.24 | 14:00 | 0:13 | 0 | 13 | [5 empty] | Source failure from Baripada PG & Balasore grid end
207 | 132 kV Baripada- Betanati |  |  |  |  | 1899-12-31 06:32 | 15 | 28 | [7 empty] | 24.43 | 8760 | 99.82% | 377.8507 | 214006.8
|  | 18.04.24 | 13:47 | 18.04.24 | 14:37 | 0:50 | 0 | 22 | [5 empty] | Source failure from Baripada PG & Balasore grid end
|  | 01.05.24 | 20:57 | 02.05.24 | 21:30 | 1899-12-31 00:33 | 0 | 34 | [5 empty] | At Betanati end: Y Ph, Dist- 14.95km
|  | 14.06.24 | 12:31 | 14.06.24 | 13:04 | 0:33 | 0 | 30 | [5 empty] | At Betanati end: DP relay operated ,started phase -CN ,Tripped phase-ABC ,Zone-I ,Fault location=9.567KM ,IA=112.4A, IB=244.2A, IC=115.8A . VAN=74.39KV, VBN=74.80KV, VCN=12.66KA . None of the Relay operated from Baripada grid end.
|  | 21.07.24 | 01:31 | 21.07.24 | 2:12 | 0:41 | 0 | 36 | [5 empty] | Failure of source
|  | 06.08.24 | 14:52 | 06.08.24 | 15:42 | 0:50 | 0 | 20 | [5 empty] | At Baripada end: E/F (Y-N), Zone 1, Iy- 3kA At Betanati end: Y-N, Zone 1, Dist- 4.54km, Ir- 0.139kA, Iy- 0.138kA, Ib- 0.127kA
|  | 08.08.24 | 17:01 | 08.08.24 | 17:40 | 0:39 | 0 | 13 | [5 empty] | At Betanati end: R-Y-B, Zone 1, Dist -12.60km, Ir- 0.118kA, Iy- 0.119kA, Ib- 0.182kA No tripping at Baripada end
|  | 23.09.24 | 14:53 | 23.09.24 | 16:23 | 1:30 | 0 | 25 | [5 empty] | At Baripada end: DP relay operated ,Zone -I , fault loop - L2-L3 ,Distance =16Km, IL1=0.07KA, IL2=3.45KA, IL3=3.38KA . At Betanati end: No tripping
|  | 28.09.24 | 12:31 | 28.09.24 | 12:46 | 0:15 | 0 | 14 | [5 empty] | Source Failure
|  | 2024-10-18 | 19:56 | 2024-10-18 | 20:37 | 0:41 | 0 | 14 | [5 empty] | At Betanati end: O/C (R-B), Zone 1, Dist- 33.72km, Ir- 0.063kA, Ib- 0.067kA At Baripada end: O/C (R-B), Zone 1, Dist- 13.4km, Ir- 3.73kA, Ib- 3.92kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
208 | 132 kV Balasore-Basta |  |  |  |  | 0 | 0 | 0 | [7 empty] | 32.51 | 8760 | 100% | 0 | 284787.6
209 | 132 kV Balasore- Balasore Alloy |  |  |  |  | 0 | 0 | 0 | [7 empty] | 6.45 | 8760 | 100% | 0 | 56502
210 | 132 kV Balasore-Birla Tyre |  |  |  |  | 0.14306 | 3 | 26 | [7 empty] | 2.598 | 8760 | 99.96% | 8.9198 | 22758.48
|  | 15.06.24 | 21:17 | 15.06.24 | 22:38 | 1:21 | 1 | 21 | [5 empty] | At Balasore end: E/F, O/C (R Ph), Zone 1, Dist- 0.5km, Ir- 75kA
|  | 31.01.25 | 05:50 | 31.01.25 | 7:55 | 2:05 | 2 | 5 | [5 empty] | At Balasore end: Earth Fault, O/C,E/F,Dist R-ph OPTD,Zone-1,dist-1.28KM, fault current:Ir=6.9KA,In=6.8KA
211 | 132 kV Balasore- Balasore RTSS |  |  |  |  | 0.099306 | 14 | 23 | [7 empty] | 3.565 | 8760 | 99.84% | 51.2766 | 31229.4
|  | 03.04.24 | 19:59 | 03.04.24 | 20:18 | 0:19 | 0 | 19 | [5 empty] | O/C (R Ph), Ir- 0.326kA, Iy- 0.325kA
|  | 07.04.24 | 20:01 | 07.04.24 | 20:06 | 0:05 | 0 | 5 | [5 empty] | O/C (R Ph), Ir- 0.3kA, Iy- 0.301kA
|  | 13.06.24 | 06:19 | 13.06.24 | 6:29 | 0:10 | 0 | 10 | [5 empty] | At Balasore end: Over Current,Fault report: O/C,R-ph OPTD fault current:Ir=314.74A,Iy=313.54A.
|  | 13.07.24 | 09:05 | 13.07.24 | 9:23 | 0:18 | 0 | 18 | [5 empty] | At Balasore end: O/C (R Ph), Ir- 0.352kA
|  | 07.08.24 | 19:57 | 07.08.24 | 20:11 | 0:14 | 0 | 14 | [5 empty] | At Balasore end: O/C (R-Y), If- 0.411kA
|  | 11.09.24 | 14:41 | 11.09.24 | 14:52 | 0:11 | 0 | 11 | [5 empty] | At Balasore end: Over Current,O/C,R-ph ,B-ph OPTD fault current:Ir=311A,Iy=309A
|  | 20.09.24 | 16:39 | 20.09.24 | 16:45 | 0:06 | 0 | 6 | [5 empty] | At Balasore end: Over Current,O/C,R-ph ,B-ph OPTD fault current:Ir=344A,Iy=343A
|  | 3.11.24 | 19:41 | 3.11.24 | 19:46 | 0:05 | 0 | 5 | [5 empty] | At Balasore end: Over Current,Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=289A,Iy=288A.rn
|  | 9.11.24 | 19:44 | 9.11.24 | 19:50 | 0:06 | 0 | 6 | [5 empty] | At Balasore end: Over Current, Fault report: O/C,R-ph ,B-ph OPTD fault current: Ir=353A,Iy=353A.rn
|  | 14.11.24 | 16:20 | 14.11.24 | 16:24 | 0:04 | 0 | 4 | [5 empty] | At Balasore end: Over Current,Fault report: O/C,R-ph ,B-ph OPTD fault current:Ir=374A,Iy=374A.rn
|  | 8.01.25 | 13:14 | 8.01.25 | 13:22 | 0:08 | 0 | 8 | [5 empty] | At Balasore end: O/C (R-B Ph), Ir- 0.369kA, Iy- 0.365kA
|  | 12.01.25 | 13:47 | 12.01.25 | 13:54 | 0:07 | 0 | 7 | [5 empty] | At Balasore end: O/C (R-B), Ir- 0.371kA, Ib- 0.372kA
|  | 9.02.25 | 01:46 | 9.02.25 | 1:54 | 0:08 | 0 | 8 | [5 empty] | At Balasore end: Over Current, O/C,R-ph ,B-ph OPTD fault current: Ir=324A, Iy=321A.
|  | 19.02.25 | 22:18 | 19.02.25 | 22:24 | 0:06 | 0 | 6 | [5 empty] | At Balasore end: Over Current, R-ph ,B-ph OPTD fault current:Ir=362A,Iy=360A.
|  | 23.02.25 | 19:38 | 23.02.25 | 19:44 | 0:06 | 0 | 6 | [5 empty] | At Balasore end: Over Current, R-ph ,B-ph OPTD fault current:Ir=283A,Iy=282A
|  | 21.03.25 | 16:24 | 21.03.25 | 16:30 | 0:06 | 0 | 6 | [5 empty] | At Balasore end: O/C, Ir- 0.313kA, Ib- 0.312kA
|  | 28.03.25 | 14:43 | 28.03.25 | 14:47 | 0:04 | 0 | 4 | [5 empty] | At Balasore end: O/C, Ir- 0.385kA, Iy- 0.383kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
212 | 132 kV Balasore-Chandipur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 45.76 | 8760 | 100% | 0 | 400857.6
213 | 132 kV Chandipur-Soro |  |  |  |  | 0.011806 | 0 | 17 | [7 empty] | 43.26 | 8760 | 100% | 12.257 | 378957.6
|  | 6.11.24 | 11:40 | 6.11.24 | 11:57 | 0:17 | 0 | 17 | [5 empty] | At Soro end: Distance Protection,Relay not operated. chandipur Grid Realy Details:- Distance Protection Relay: Zone-1, Distance-32.97Km, IA=0.19KA, IB=1.37KA, IC=0.15KA, IN=1.22KA.
214 | 132 kV Balasore-Somnathpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 4 | 8760 | 100% | 0 | 35040
215 | 132 kV Somnathpur-Stork |  |  |  |  | 0.30139 | 7 | 14 | [7 empty] | 0.1 | 8760 | 99.92% | 0.72333 | 876
|  | 7.11.24 | 12:20 | 7.11.24 | 19:34 | 7:14 | 7 | 14 | [5 empty] | O/C,R-phase P/U,Y-phase P/U, Fault Current: Ia-7.32KA,Ib-0.07KA,Ic-0.19KA
216 | 132 kV Somnathpur-EMAMI |  |  |  |  | 0.054861 | 1 | 19 | [7 empty] | 6 | 8760 | 99.98% | 7.9 | 52560
|  | 21.08.24 | 13:35 | 21.08.24 | 14:54 | 1:19 | 1 | 19 | [5 empty] | At Somnathpur end: Tripped
217 | 132kV Balugaon-Chandpur |  |  |  |  | 0.12292 | 13 | 35 | [7 empty] | 43.12 | 8760 | 99.84% | 585.7133 | 377731.2
|  | 15.04.24 | 10:15 | 15.04.24 | 11:44 | 1:29 | 0 | 28 | [5 empty] | At Chandpur-A/R block at Chandpur end. Y-B Ph, Zone 1, Dist- 22.5km, Ir- 0.15kA, Iy- 1.98kA, Ib- 1.84kA At Balugaon-No breaker operated.
|  | 18.04.24 | 10:56 | 18.04.24 | 11:33 | 0:37 | 0 | 16 | [5 empty] | B-N, Zone 1, Dist- 21.3km, Ib- 1.12kA
|  | 30.04.24 | 23:25 | 30.04.24 | 23:31 | 0:06 | 0 | 6 | [5 empty] | O/C (Y & B Ph), Iy- 0.44kA, Ib-0.45kA
|  | 23.02.25 | 16:52 | 24.02.25 | 17:37 | 0:45 | 0 | 45 | [5 empty] | At Chandpur end: R-Y, Zone 2, Dist- 44.3km, Ir- 1.63kA, Iy- 1.48kA, A/R Block At Balugaon end: CB not operated
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
218 | 132 kV Balugaon-Solari RTSS |  |  |  |  | 0.82153 | 13 | 31 | [7 empty] | 14.1 | 8760 | 99.85% | 190.585 | 123516
|  | 18.04.24 | 10:56 | 18.04.24 | 11:33 | 0:37 | 0 | 10 | [5 empty] | B-N, Zone 1, Dist- 21.3km, Ib- 1.12kA
|  | 22.04.24 | 22:32 | 22.04.24 | 22:52 | 0:20 | 0 | 20 | [5 empty] | Distance Protection,Earth Fault, Yph O/C &E/F,Dist-0.6km,IR-0A,IY-2929A,IB-22A,IG-2946A,Yph O/C&E/F,IR-0A,IY-3kA,IB-0.03kA
|  | 30.04.24 | 23:25 | 30.04.24 | 23:31 | 0:06 | 0 | 6 | [5 empty] | O/C (Y & B Ph), Iy- 0.44kA, Ib-0.45kA
|  | 13.02.25 | 03:57 | 13.02.25 | 4:06 | 0:09 | 0 | 9 | [5 empty] | At Balugaon end: Distance Protection,Earth FaultIR=0.00A, IY=3066A, IB=35A, IG=3076A, Zone=1, Distance=0.6KM,Y-ph, IR=0.00KA, IY=3.1KA, IB=0.03KA
|  | 23.02.25 | 16:52 | 24.02.25 | 11:23 | 18:31 | 0 | 46 | [5 empty] | At Balugaon end: B-N, Zone 1, Dist- 0.93km, Ib- 1.494kA At Chatrapur end: B-N, Dist- 60.35km, Zone 2, Ib- 1.493KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
219 | 132 kV Banki-Nuapatna |  |  |  |  | 0.0041667 | 0 | 6 | [7 empty] | 20.61 | 8760 | 100% | 2.061 | 180543.6
|  | 7.02.25 | 12:20 | 7.02.25 | 12:26 | 0:06 | 0 | 6 | [5 empty] | Incomer Failure from GSS, Nuapatna
220 | 132 kV Bargarh-ACC Ckt I |  |  |  |  | 0.041667 | 12 | 54 | [7 empty] | 2.87 | 8760 | 99.85% | 37.023 | 25141.2
|  | 2024-10-06 | 18:20 | 2024-10-06 | 18:34 | 0:14 | 0 | 14 | [5 empty] | At Bargarh end: Earth FaultZone 1,Y-N, E/F,15.61 Km,IR-458.4A,IY-308.8A,IB=325.6A, Fault duration-50.04 ms
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 24 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
221 | 132 kV Bargarh-ACC Ckt II |  |  |  |  | 0.041667 | 12 | 54 | [7 empty] | 2.87 | 8760 | 99.85% | 37.023 | 25141.2
|  | 2024-10-06 | 18:20 | 2024-10-06 | 18:34 | 0:14 | 0 | 14 | [5 empty] | At Bargarh end: Earth FaultZone 1,Y-N, E/F,15.61 Km,IR-458.4A,IY-308.8A,IB=325.6A, Fault duration-50.04 ms
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 24 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
222 | 132 kV Katapalli-Thuapalli |  |  |  |  | 0.036806 | 0 | 53 | [7 empty] | 33.5 | 8760 | 99.99% | 29.5917 | 293460
|  | 23.05.24 | 19:14 | 23.05.24 | 20:07 | 0:53 | 0 | 53 | [5 empty] | At Katapali end: Distance Protection,Distance protection optd in zone1 with fault distance of 1.02km, time duration=0.108ms IR=15KA, IY=100A, IB=69.2A At Thuapali end: Distance Protection,L1 to Earth Fault,Zone-1 trip FD-29.3KM,IL1-1.18KA,IL2-0.01KA,IL3-0.00KA
223 | 132 kV Thuapalli-Bargarh |  |  |  |  | 0.016667 | 0 | 24 | [7 empty] | 43.9 | 8760 | 100% | 17.56 | 384564
|  | 02.08.24 | 15:06 | 02.08.24 | 15:30 | 0:24 | 0 | 24 | [5 empty] | At Bargarh end: Zone 2, Dist- 24.70km, Ir- 219A, Iy- 349A, Ib- 442A At Thuapali end: E/F (B-N), Zone 1, Dist- 9.2km, Ib- 2.68kA
224 | 132 kV Bargarh New-Ghens Ckt -I |  |  |  |  | 0.046528 | 13 | 39 | [7 empty] | 29.13 | 8760 | 99.84% | 397.6245 | 255178.8
|  | 23.05.24 | 19:14 | 23.05.24 | 19:35 | 0:21 | 0 | 53 | [5 empty] | At Bhatli end: Remote End Tripping,220kV Line tripped at source grid GSS Bargarh New.
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 30 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
225 | 132 kV Bargarh New-Ghens Ckt -II |  |  |  |  | 0.046528 | 13 | 39 | [7 empty] | 29.13 | 8760 | 99.84% | 397.6245 | 255178.8
|  | 23.05.24 | 19:14 | 23.05.24 | 19:35 | 0:21 | 0 | 53 | [5 empty] | At Bhatli end: Remote End Tripping,220kV Line tripped at source grid GSS Bargarh New.
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 30 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
226 | 132 kV Bargarh New- Bhatli Ckt -I |  |  |  |  | 0.046528 | 13 | 39 | [7 empty] | 40.225 | 8760 | 99.84% | 549.0713 | 352371
|  | 23.05.24 | 19:14 | 23.05.24 | 19:35 | 0:21 | 0 | 53 | [5 empty] | At Bhatli end: Remote End Tripping,220kV Line tripped at source grid GSS Bargarh New.
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 30 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
227 | 132 kV Bargarh New- Bhatli Ckt -II |  |  |  |  | 0.046528 | 13 | 39 | [7 empty] | 40.225 | 8760 | 99.84% | 549.0713 | 352371
|  | 23.05.24 | 19:14 | 23.05.24 | 19:35 | 0:21 | 0 | 53 | [5 empty] | At Bhatli end: Remote End Tripping,220kV Line tripped at source grid GSS Bargarh New.
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 30 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
228 | 132kV Baripada-Kuchei PG |  |  |  |  | 0.58542 | 16 | 15 | [7 empty] | 3.1 | 8760 | 99.81% | 50.375 | 27156
|  | 18.04.24 | 13:47 | 18.04.24 | 14:37 | 0:50 | 0 | 50 | [5 empty] | At PGCIL end: O/C, Ir- 0.7kA, Iy- 0.73kA, Ib- 0.7kA
|  | 01.05.24 | 20:57 | 02.05.24 | 2:30 | 5:33 | 0 | 24 | [5 empty] | At Baripada end: O/C (Y Ph), Iy- 5.05kA
|  | 14.06.24 | 12:31 | 14.06.24 | 13:48 | 1:17 | 0 | 33 | [5 empty] | At Baripada PG end: DP Relay operated ,distance-7.478KM, Fault current =5.46KA, Zone-I,B-Phase to ground ,Fault voltage (Vcn)=34.52KV . Backup relay operated : trip time=51ms . None of the Relay operated from Baripada grid end.
|  | 21.07.24 | 01:31 | 21.07.24 | 2:12 | 0:41 | 0 | 12 | [5 empty] | At Baripada PG end: O/C (R-B), Ir- 0.79kA, Ib- 0.94kA
|  | 08.08.24 | 17:01 | 08.08.24 | 18:36 | 1:35 | 0 | 39 | [5 empty] | At Baripada end: R-Y-B, Zone 1 ,Dist -8.958km, Ir- 0.414kA, Iy-0.405kA, Ib- 0.461kA At Baripada PG end: Directional O/C & E/F, Ir- 5.86kA, Iy-5.58kA, Ib-0.45kA, Dist- 11.2km
|  | 23.09.24 | 14:53 | 23.09.24 | 15:41 | 0:48 | 0 | 48 | [5 empty] | At Baripada end: Over Current, At Baripada PG end: back up relay operated , Directional O/C in Y & B - Phase ,IL1=0.16KA, IL2=1KA, IL3=0.82KA .
|  | 28.09.24 | 12:31 | 28.09.24 | 15:17 | 2:46 | 0 | 16 | [5 empty] | At Baripada end: DP relay operated, started phase :B N , Fault duration -31.67ms ,Relay trip time -0.00ms ,IL1=286.9A, IL2=459.2A, IL3=236.1A .VAN=78.48KV, VBN=78.01KV ,VCN=37.35KV . At Baripada PG end: Backup O/C protection operated , Directional O/C trip ,IL1=0.32KA, IL2=0.29KA, IL3=4.7KA .
|  | 2024-10-18 | 19:56 | 2024-10-18 | 20:29 | 0:33 | 0 | 33 | [5 empty] | At Baripada PG end: R-B, Zone 3, Ir- 3.543kA, Ib- 3.847kA CB didnot trip from Baripada grid end .
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
229 | 132kV Berhampur-Digapahandi |  |  |  |  | 0.026389 | 0 | 29 | [7 empty] | 31.48 | 8760 | 99.99% | 15.2153 | 275764.8
|  | 07.07.24 | 14:37 | 07.07.24 | 14:58 | 0:21 | 0 | 21 | [5 empty] | At Digapahandi end: Y-N, Zone 1, Iy- 1.k391A, Dist- 23.81km
|  | 21.08.24 | 18:57 | 21.08.24 | 19:14 | 0:17 | 0 | 8 | [5 empty] | At Digapahandi end: Back up relay,Bphase earth fault, fault currents ia-0.17kA,ib-0.37kA,ic-1.44kA
230 | 132kV Bhadrak-FACOR |  |  |  |  | 0.18889 | 16 | 21 | [7 empty] | 4.564 | 8760 | 99.81% | 74.6214 | 39980.64
|  | 09.05.24 | 17:06 | 09.05.24 | 18:05 | 0:59 | 0 | 59 | [5 empty] | At Bhadrak end: O/C,IL1-79.87A,IL2-92.54A. IL3-47.01A
|  | 12.05.24 | 14:58 | 12.05.24 | 16:10 | 1:12 | 1 | 1 | [5 empty] | At Bhadrak end: Remote End Tripping,IL1-1876.15A, IL2-417.31A,IL3-850.12A, IN-915.85A At Balasore end: Distance Protection,Main-I: Dist R-ph, Optd,Zone-2,Zone-3,Auto reclose lock out OPTD,fault distance-115.35KM, fault current-Ir=1876.151A, Iy=417.328 A, Ib=850.123A,In-915.858A.
|  | 16.05.24 | 06:37 | 16.05.24 | 07:00 | 0:23 | 0 | 23 | [5 empty] | At Bhadrak end: O/C,IL1-222.1A, IL2-172.1A, IL3-176.2A
|  | 21.05.24 | 12:16 | 21.05.24 | 12:24 | 0:08 | 0 | 8 | [5 empty] | At Bhadrak end: O/C,IL1-201.5A, IL2-185.8A, IL3-214.6A
|  | 21.05.24 | 14:58 | 21.05.24 | 15:04 | 0:06 | 0 | 6 | [5 empty] | At Bhadrak end: O/C,IL1-199.8A, IL2-158.8A,IL3-166.2A
|  | 05.07.24 | 14:58 | 05.07.24 | 15:19 | 0:21 | 0 | 21 | [5 empty] | At Bhadrak end: E/F, B-N, Zone 1, Dist- 5.383 km, Ib-5.703kA
|  | 17.09.24 | 10:20 | 17.09.24 | 11:30 | 1:10 | 1 | 10 | [5 empty] | At Jajpur Town end: Distance Protection,Irn=197.1A, Iyn=78.84A, Ibn=86.27A, Vrn=67.94 KV, Vyn=5.97KV, Vbn=70.79KV
|  | 2024-10-17 | 19:15 | 2024-10-17 | 19:28 | 0:13 | 0 | 13 | [5 empty] | At Bhadrak end: Over Current tripped on Backup Relay, R phase P/U, E/F P/U ,IL1=200.7A, IL2=161.0A, IL3=195.7A,
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
231 | 132kV Bhadrak-Dhamara Port |  |  |  |  | 0.58542 | 25 | 22 | [7 empty] | 63.9 | 8760 | 99.71% | 1620.93 | 559764
|  | 28.04.24 | 17:58 | 28.04.24 | 20:16 | 2:18 | 2 | 18 | [5 empty] | O/C (R Ph), Zone 1, Dist- 51.26km, Ir- 1.828kA
|  | 12.05.24 | 14:58 | 12.05.24 | 15:49 | 0:51 | 0 | 50 | [5 empty] | At Bhadrak end: Remote End Tripping,IL1-2.05KA,IL2-0.41KA, IL3-0.83KA
|  | 13.08.24 | 18:52 | 13.08.24 | 19:19 | 0:27 | 0 | 27 | [5 empty] | At Bhadrak end: Zone 1, O/C (B Ph), Ib- 3.037kA, Dist- 18.64km
|  | 17.09.24 | 10:20 | 17.09.24 | 11:30 | 1:10 | 0 | 30 | [5 empty] | At Jajpur Town end: Distance Protection,Irn=197.1A, Iyn=78.84A, Ibn=86.27A, Vrn=67.94 KV, Vyn=5.97KV, Vbn=70.79KV
|  | 2024-10-25 | 02:05 | 2024-10-25 | 11:22 | 9:17 | 9 | 17 | [5 empty] | At Bhadrak end: Distance Protection, started phase-AN,Ia=1.792KA,Ib=238.20A,Ic=263.7A, distance=50.04KM, At DPCL end: Zone-I, R phase , distance=4.62KM, Ir=262.5A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
232 | 132kV Bhadrak-Dhamara Port Traction |  |  |  |  | 0.18889 | 15 | 52 | [7 empty] | 35.3 | 8760 | 99.82% | 560.0933 | 309228
|  | 23.06.24 | 12:33 | 23.06.24 | 13:48 | 1:15 | 1 | 15 | [5 empty] | At Bhadrak end: Distance Protection,Over Current,ACTIVE GROUP I, STARTED PHASE -CN, TRIPPED PHASE-C, ZONE-1, DIST-15.90 KM, Ia-33.76 A, Ib-29.97 A, Ic-4.462 KA, Van-71.18 KV, Vbn- 72.70 KV, Vcn- 47.33 KV,B PHASE O/C
|  | 15.07.24 | 08:25 | 15.07.24 | 9:30 | 1:05 | 1 | 5 | [5 empty] | At Bhadrak end: O/C (B-N), Zone 1, Dist- 15.91km, Ib- 4.37kA
|  | 17.09.24 | 10:20 | 17.09.24 | 11:30 | 1:10 | 0 | 30 | [5 empty] | At Jajpur Town end: Distance Protection,Irn=197.1A, Iyn=78.84A, Ibn=86.27A, Vrn=67.94 KV, Vyn=5.97KV, Vbn=70.79KV
|  | 15.03.25 | 11:57 | 15.03.25 | 12:59 | 1:02 | 1 | 2 | [5 empty] | At Bhadrak end: R-N, Zone 1, Dist- 28.65km, Ir- 2.516kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
233 | 132kV Bhadrak-Bhadrak RTSS |  |  |  |  | 0.12778 | 15 | 3 | [7 empty] | 8.086 | 8760 | 99.83% | 121.6943 | 70833.36
|  | 12.05.24 | 14:58 | 12.05.24 | 15:49 | 0:51 | 0 | 50 | [5 empty] | At Bhadrak end: Remote End Tripping,IL1-2.05KA,IL2-0.41KA, IL3-0.83KA
|  | 25.05.24 | 15:01 | 25.05.24 | 15:04 | 0:03 | 0 | 3 | [5 empty] | At Bhadrak end: O/C,IL2-0.27KA,IL3-0.26KA
|  | 13.07.24 | 09:13 | 13.07.24 | 9:18 | 0:05 | 0 | 5 | [5 empty] | At Bhadrak end: O/C (Y-B Ph), Iy- 0.27kA, Ib- 0.27kA
|  | 17.08.24 | 09:19 | 17.08.24 | 9:28 | 0:09 | 0 | 9 | [5 empty] | At Bhadrak end: O/C, If- 0.27kA
|  | 17.09.24 | 10:20 | 17.09.24 | 11:30 | 1:10 | 1 | 10 | [5 empty] | At Jajpur Town end: Distance Protection,Irn=197.1A, Iyn=78.84A, Ibn=86.27A, Vrn=67.94 KV, Vyn=5.97KV, Vbn=70.79KV
|  | 12.11.24 | 09:12 | 12.11.24 | 9:18 | 0:06 | 0 | 6 | [5 empty] | O/C
|  | 12.11.24 | 10:33 | 12.11.24 | 10:37 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 14.11.24 | 14:37 | 14.11.24 | 14:41 | 0:04 | 0 | 4 | [5 empty] | At Bhadrak end: Over Current,Over Current, IL2=0.30 KA (Y Phase), IL3=0.30 KA (B Phase)
|  | 16.11.24 | 10:14 | 16.11.24 | 10:16 | 0:02 | 0 | 2 | [5 empty] | At Bhadrak end: Over Current,Over Current, IL2=0.26 KA (Y Phase), IL3=0.26 KA (B Phase)rn
|  | 3.02.25 | 08:37 | 3.02.25 | 8:42 | 0:05 | 0 | 5 | [5 empty] | At Bhadrak end: Over Current, Y phase,B Phase IL2=0.28KA, IL3=0.28KA
|  | 3.02.25 | 11:53 | 3.02.25 | 11:56 | 0:03 | 0 | 3 | [5 empty] | At Bhadrak end: Over CurrentOver current Y phase,B Phase IL2=0.28KA, IL3=0.28KA
|  | 5.03.25 | 10:35 | 5.03.25 | 10:40 | 0:05 | 0 | 5 | [5 empty] | At Bhadrak end: O/C (Y-B), (Iy, Ib)- 0.27kA
|  | 9.03.25 | 20:01 | 9.03.25 | 20:05 | 0:04 | 0 | 4 | [5 empty] | At Bhadrak end: O/C, If- 0.29kA
|  | 10.03.25 | 17:10 | 10.03.25 | 17:15 | 0:05 | 0 | 5 | [5 empty] | At Bhadrak end: O/C, If- 0.29kA
|  | 18.03.25 | 17:14 | 18.03.25 | 17:18 | 0:04 | 0 | 4 | [5 empty] | At Bhadrak end: O/C, If- 0.26kA
|  | 20.03.25 | 15:47 | 20.03.25 | 15:51 | 0:04 | 0 | 4 | [5 empty] | At Bhadrak end: O/C, Iy- 0.28kA, Ib- 0.27kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
234 | 132kV Bhadrak-Jajpur Town |  |  |  |  | 0.32083 | 15 | 13 | [7 empty] | 40.12 | 8760 | 99.83% | 610.4927 | 351451.2
|  | 12.05.24 | 14:58 | 12.05.24 | 16:54 | 1:56 | 0 | 50 | [5 empty] | At Jajpur Town end: Remote End Tripping
|  | 20.05.24 | 17:27 | 20.05.24 | 18:50 | 1:23 | 0 | 12 | [5 empty] | At Bhadrak end: Remote End Tripping,Started phase B-N, Tripped phase R-Y-B, Zone-1, Fault distance=1.35 KM, Ir=81.7A, Iy=196.4A, Ib=9.875 KA, Vr=72.29KV, Vy=73.54 KV, Vb=12.2KV, Fault resistance=0.456 ohm At Jajpur Town end: Remote End Tripping, Started phase B-N, Tripped phase R-Y-B, Zone-1, Fault distance=1.35 KM, Ir=81.7A, Iy=196.4A, Ib=9.875 KA, Vr=72.29KV, Vy=73.54 KV, Vb=12.2KV, Fault resistance=0.456 ohm
|  | 06.06.24 | 16:24 | 06.06.24 | 16:45 | 0:21 | 0 | 21 | [5 empty] | At Jajpur Town end: Remote End Tripping,Started Phase C-N, Tripping Phase A-B-C, Zone-1, Fault Distance =1.33 KM, Ia=148A, Ib=290.8A, Ic=9.6KA, Van=71.2KV, Vbn=72KV, Vcn=11.17KV At Bhadrak end: Distance Protection,Over Current,Earth Fault,STARTED PHASE -CN, TRIPPED PHASE-ABC, ZONE-1, DIST-1.329 KM, Ia-148.8 A, Ib-290.8 A, Ic-9.630 KA,
|  | 15.06.24 | 20:54 | 15.06.24 | 21:51 | 0:57 | 0 | 57 | [5 empty] | At Jajpur Town end: Remote End Tripping,Started phase Y-N, Tripped phase Y-N, Zone-1, Fault distance=2.224KM, Irn=6.14A, Iyn=5.64KA, Ibn=5.56A, Vyn=78.43 KV, Vyn=19.69KV, Vbn=80.36KV, Fault resistance=2.47 ohm
|  | 18.08.24 | 14:20 | 18.08.24 | 15:16 | 0:56 | 0 | 18 | [5 empty] | At Jajpur Town end: B-N, Zone 1, Dist- 1km, Ib- 0.273kA
|  | 17.09.24 | 10:20 | 17.09.24 | 11:30 | 1:10 | 0 | 6 | [5 empty] | At Jajpur Town end: Distance Protection,Irn=197.1A, Iyn=78.84A, Ibn=86.27A, Vrn=67.94 KV, Vyn=5.97KV, Vbn=70.79KV
|  | 24.09.24 | 16:04 | 24.09.24 | 17:03 | 0:59 | 0 | 29 | [5 empty] | At Jajpur Town end: Remote End Tripping,Started phase B-N, Tripped phase B-N, Zone-1, Dist=28.65KM, Irn=9A, Iyn=8.9A, Ibn=2.7KA, VRn=77.03 KV, Vyn=77.42KV, Vbn=59.37KV
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
235 | 132kV Bhanjanagar-Aska-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.32 | 8760 | 100% | 0 | 291883.2
236 | 132kV Bhanjanagar-Aska-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 33.72 | 8760 | 100% | 0 | 295387.2
237 | 132kV Bhanjanagar- G. Udaygiri |  |  |  |  | 0.3875 | 9 | 13 | [7 empty] | 53.4 | 8760 | 99.89% | 492.17 | 467784
|  | 14.05.24 | 15:27 | 14.05.24 | 21:28 | 6:01 | 6 | 1 | [5 empty] | Tripped at Bhanjanagar end only. Distance Protection, CN, Z-1, D=41.36km, IC=1.04 KA
|  | 12.03.25 | 12:16 | 12.03.25 | 15:33 | 3:17 | 3 | 12 | [5 empty] | At Bhanjanagar end: Y-B, Zone 1, Dist- 36.43km, Iy- 3.141kA, Ib- 2.974kA
238 | 132KV G. Udaygiri -Phulbani |  |  |  |  | 0.52292 | 24 | 28 | [7 empty] | 54.5 | 8760 | 99.72% | 1333.4333 | 477420
|  | 14.05.24 | 15:27 | 14.05.24 | 21:28 | 6:01 | 6 | 1 | [5 empty] | Tripped at Bhanjanagar end only. Distance Protection, CN, Z-1, D=41.36km, IC=1.04 KA
|  | 02.06.24 | 13:42 | 02.06.24 | 14:39 | 0:57 | 0 | 57 | [5 empty] | At G.Udaygiri end: Distance Protection, zone-1 , D-23.6KM, Ir-1.40KA, Iy-0.13KA & Ib-0.25KA.
|  | 20.06.24 | 17:02 | 20.06.24 | 17:38 | 0:36 | 0 | 36 | [5 empty] | At G.Udaygiri end: Distance Protection, zone-1 , D-26.3KM, Ir-0.17KA, Iy-0.28KA & Ib-1.48KA.
|  | 23.09.24 | 18:46 | 23.09.24 | 19:31 | 0:45 | 0 | 45 | [5 empty] | At G.Udaygiri end: Distance Protection, zone-1 , D-15.7KM, Ir-1.90KA, & Ib-1.72KA.
|  | 24.09.24 | 16:19 | 24.09.24 | 17:16 | 0:57 | 0 | 57 | [5 empty] | At G.Udaygiri end: Distance Protection, zone-1 , D-43.5KM, Iy-1.56KA, & Ib-1.53KA.
|  | 12.03.25 | 12:16 | 12.03.25 | 15:33 | 3:17 | 3 | 12 | [5 empty] | At Bhanjanagar end: Y-B, Zone 1, Dist- 36.43km, Iy- 3.141kA, Ib- 2.974kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
239 | 132kV Pratapsasan -Badagada (Kesura) |  |  |  |  | 0.040278 | 12 | 50 | [7 empty] | 11.108 | 8760 | 99.85% | 142.5527 | 97306.08
|  | 23.04.24 | 14:22 | 23.04.24 | 14:38 | 0:16 | 0 | 8 | [5 empty] | Bus bar Protection and 96 relay operated.
|  | 14.05.24 | 14:10 | 14.05.24 | 14:27 | 0:17 | 0 | 17 | [5 empty] | At Kesura end: O/C,IA-0.315KA, IB-5.062KA, IC-4.559KA, IG-3.467KA At Pratapsasan end: O/C,AT PRATAPSASAN GSS IB-287.3A, IC-2.3KA, IG-2KA AT KESURA GSS IA-0.315KA, IB-5.062KA, IC-4.559KA, IG-3.467KA
|  | 19.05.24 | 10:53 | 19.05.24 | 11:08 | 0:15 | 0 | 15 | [5 empty] | At Kesura end: Remote End Tripping,Pratapsasan Grid End-O/C(R-Ph), Ia-2.4KA, Ib-84A, Ic-279A At Pratapsasan end: Distance Protection,AT Pratapsasan Grid Ia-2.4KA, Ib-84A, Ic-279A
|  | 23.05.24 | 00:12 | 23.05.24 | 0:22 | 0:10 | 0 | 10 | [5 empty] | At Pratapsasan end: Distance Protection,Tripped from Pratapsasan end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
240 | 132kV Pratapsasan -Nimapara |  |  |  |  | 0.029861 | 12 | 36 | [7 empty] | 35.083 | 8760 | 99.86% | 442.0458 | 307327.08
|  | 26.04.24 | 07:25 | 26.04.24 | 07:34 | 0:09 | 0 | 8 | [5 empty] | R-N, Zone 4, Dist- 0.188km, Ir- 2.517kA
|  | 23.04.24 | 14:22 | 23.04.24 | 14:44 | 0:22 | 0 | 16 | [5 empty] | Distance ProtectionZ1 , BN, D-24.05km , Ia-493.4A , Ib-2.165kA , Ic-310.5A,
|  | 04.07.24 | 17:10 | 04.07.24 | 17:22 | 0:12 | 0 | 12 | [5 empty] | At Nimapara end: Over Current, Bus fault
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
241 | 132kV Pratapsasan -Phulnakhara Ckt-I |  |  |  |  | 0.20764 | 0 | 49 | [7 empty] | 14.64 | 8760 | 99.99% | 11.956 | 128246.4
|  | 23.04.24 | 14:22 | 23.04.24 | 14:47 | 0:25 | 0 | 20 | [5 empty] | O/C767.9,762.5,815.1A
|  | 01.05.24 | 18:25 | 01.05.24 | 18:56 | 4:34 | 0 | 29 | [5 empty] | At Pratapsasan end: Y-B Ph, Zone 2, Dist- 14.73km, Iy- 2.95kA, Ib- 2.87kA At Phulnakhara end: Y-B Ph, Zone 2, Dist- 3.615km, Iy- 5.461kA, Ib- 5.529kA
242 | 132kV Pratapsasan -Phulnakhara Ckt-II |  |  |  |  | 0.017361 | 0 | 20 | [7 empty] | 14.64 | 8760 | 100% | 4.88 | 128246.4
|  | 23.04.24 | 14:22 | 23.04.24 | 14:47 | 0:25 | 0 | 20 | [5 empty] | O/C767.9,762.5,815.1A
243 | 132kV Bhubaneswar-Phulnakhara |  |  |  |  | 0.0375 | 0 | 49 | [7 empty] | 22.74 | 8760 | 99.99% | 18.571 | 199202.4
|  | 23.04.24 | 14:22 | 23.04.24 | 14:47 | 0:25 | 0 | 20 | [5 empty] | O/C767.9,762.5,815.1A
|  | 01.05.24 | 18:25 | 01.05.24 | 18:54 | 0:29 | 0 | 29 | [5 empty] | At Bhubaneswar end: Y-B Ph, Iy- 3.444kA, Ib- 3.42kA
244 | 132kV Bhubaneswar-Nayapalli |  |  |  |  | 0.025 | 0 | 36 | [7 empty] | 6.16 | 5292 | 99.99% | 3.696 | 32598.72
|  | 24.02.25 | 7:03 | 24.02.25 | 7:39 | 0:36 | 0 | 36 | [5 empty] | Tripped on R ph O/C & E/F
245 | 132kV Bhubaneswar-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.18 | 8760 | 100% | 0 | 45376.8
246 | 132kV Chandaka-Mancheswar-B UG Cable |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.8 | 8760 | 100% | 0 | 94608
247 | 132kV Bidanasi-Brajabiahripur |  |  |  |  | 0.017361 | 0 | 25 | [7 empty] | 10.1 | 8760 | 100% | 4.2083 | 88476
|  | 25.06.24 | 16:57 | 25.06.24 | 17:22 | 0:25 | 0 | 25 | [5 empty] | At Bidanasi end: DP relay, R-ph, Zone-1, Distance- 6.05km, Ir=3.45kA, Iy=226.5A, Ib=76.3A
248 | 132kV Brajabiharipur-BPPL-Chandaka |  |  |  |  | 0.084722 | 13 | 38 | [7 empty] | 33.1 | 8760 | 99.84% | 451.2633 | 289956
|  | 19.04.24 | 12:21 | 19.04.24 | 13:10 | 0:49 | 0 | 25 | [5 empty] | Distance Protection, At BPPL end, Fault Distance-5.4km, Ir-0.19kA, Iy-0.09kA, Ib-5.19kA. rnAt Brajabiharipur end, O/C & E/F Back up relay pick up in B-phase
|  | 25.06.24 | 16:57 | 25.06.24 | 17:22 | 0:25 | 0 | 25 | [5 empty] | At Brajabiharipur end: Distance Protection, R-ph-E/F, Distance-2.1km, Zone-1, Ir=6.25kA, Iy=0.43kA, Ib=0.22kA. At BPPL end, the said feeder was ideally charged from their end (BPPL CB was in closed condition)
|  | 2024-10-19 | 15:08 | 2024-10-19 | 15:56 | 0:48 | 0 | 48 | [5 empty] | At Brajabiharipur end: Distance Protection, Fault Phase:- R-phase (Top conductor), Zone-01, Fault Distance= 1.6km, Fault Currents: Ir=6.39kA, Iy=0.36kA, Ib=0.33kArn At BPPL end: Fault Phase:- R-phase (Ir=3.6) , Fault Distance= 12.5km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
249 | 132 kV Bargarh- Bargarh New |  |  |  |  | 0.071528 | 1 | 37 | [7 empty] | 26.6 | 8760 | 99.98% | 43.0033 | 233016
|  | 23.09.24 | 22:22 | 23.09.24 | 23:05 | 0:43 | 0 | 43 | [5 empty] | At Bargarh New end: Earth Fault,Backup relay operated. Ia-0.84kA, Ib-0.95kA, Ic-0.88kA
|  | 2024-10-06 | 18:20 | 2024-10-06 | 18:34 | 0:14 | 0 | 14 | [5 empty] | At Bargarh end: Earth FaultZone 1,Y-N, E/F,15.61 Km,IR-458.4A,IY-308.8A,IB=325.6A, Fault duration-50.04 ms
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 24 | [5 empty] | Over loading of Transformer
|  | 28.03.25 | 10:36 | 28.03.25 | 10:43 | 0:07 | 0 | 7 | [5 empty] | Tripped at Bolangir New end only
250 | 132 kV Bargarh New -Barpalli |  |  |  |  | 0.059028 | 12 | 42 | [7 empty] | 10.6 | 8760 | 99.86% | 134.62 | 92856
|  | 03.04.24 | 19:31 | 03.04.24 | 19:41 | 0:10 | 0 | 10 | [5 empty] | O/C, Ir- 0.45kA, Iy- 0.24kA, Ib- 0.44kA
|  | 20.09.24 | 8:09 | 20.09.24 | 8:45 | 0:36 | 0 | 6 | [5 empty] | Source Failure
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 17 | [5 empty] | Over loading of Transformer
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
251 | 132 kV Barpalli- New Bolangir |  |  |  |  | 0 | 0 | 0 | [7 empty] | 59.2 | 8760 | 100% | 0 | 518592
252 | 132 kV Barpalli-Dunguripalli RTSS |  |  |  |  | 0.039583 | 12 | 44 | [7 empty] | 12.8 | 8760 | 99.85% | 162.9867 | 112128
|  | 03.04.24 | 19:31 | 03.04.24 | 19:41 | 0:10 | 0 | 10 | [5 empty] | O/C, Ir- 0.45kA, Iy- 0.24kA, Ib- 0.44kA
|  | 20.09.24 | 8:09 | 20.09.24 | 8:15 | 0:06 | 0 | 6 | [5 empty] | Source Failure
|  | 2024-10-10 | 19:04 | 2024-10-10 | 19:13 | 0:09 | 0 | 9 | [5 empty] | At Bargarh New end: Over Current, Ia-0.61kA, Ib-0.56kA, Ic-0.62kA
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 17 | [5 empty] | Over loading of Transformer
|  | 25.02.25 | 18:52 | 25.02.25 | 18:54 | 0:02 | 0 | 2 | [5 empty] | Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
253 | 132 kV New Bolangir - Sonepur -I |  |  |  |  | 0.16597 | 15 | 59 | [7 empty] | 52.85 | 8760 | 99.82% | 844.7192 | 462966
|  | 01.04.24 | 16:45 | 01.04.24 | 17:00 | 0:15 | 0 | 15 | [5 empty] | Source failure due to tree falling 132kV Sonepur-Bolangir line
|  | 19.04.24 | 16:27 | 19.04.24 | 18:08 | 1:41 | 1 | 41 | [5 empty] | Remote end Tripping
|  | 07.05.24 | 05:27 | 07.05.24 | 06:07 | 0:40 | 0 | 40 | [5 empty] | At Bolangir New end: O/C, Ir- 0.605kA, Iy- 0.454kA, Ib- 0.345kA
|  | 11.06.24 | 17:00 | 11.06.24 | 17:16 | 0:16 | 0 | 16 | [5 empty] | At Bolangir New end: Distance Protection,Ia=150.9A, Ib=402.6A, Ic=3.168KA, Fault distance=28.83Km, Relay trip time=79.9ms
|  | 04.09.24 | 10:13 | 04.09.24 | 10:22 | 0:09 | 0 | 9 | [5 empty] | At Bolangir New: Dist- 46.3km, Ir- 2.367kA, Iy- 0.236kA, Ib- 0.518kA
|  | 28.02.25 | 23:17 | 28.02.25 | 23:33 | 0:16 | 0 | 16 | [5 empty] | At Bolangir New end: Dist- 55.28km, Zone 2, Ir- 1.679kA
|  | 31.03.25 | 09:52 | 31.03.25 | 10:34 | 0:42 | 0 | 42 | [5 empty] | At Bolangir New end: B-N, Ib- 1.031kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
254 | 132 kV New Bolangir - Sonepur -II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 52.45 | 4836 | 100% | 0 | 253648.2
255 | 132 kV Sonepur - Boudh |  |  |  |  | 0.27847 | 18 | 41 | [7 empty] | 50.25 | 8760 | 99.79% | 938.8375 | 440190
|  | 01.04.24 | 16:45 | 01.04.24 | 17:00 | 0:15 | 0 | 15 | [5 empty] | Source failure due to tree falling 132kV Sonepur-Bolangir line
|  | 19.04.24 | 16:27 | 19.04.24 | 18:08 | 1:41 | 1 | 41 | [5 empty] | Remote end Tripping
|  | 20.04.24 | 16:21 | 20.04.24 | 17:59 | 1:38 | 1 | 38 | [5 empty] | Y-B, Zone 1, Dist- 21.79km, Iy- 3.597kA, Ib- 3.214kA
|  | 07.05.24 | 05:27 | 07.05.24 | 06:07 | 0:40 | 0 | 40 | [5 empty] | At Bolangir New end: O/C, Ir- 0.605kA, Iy- 0.454kA, Ib- 0.345kA
|  | 11.06.24 | 05:01 | 11.06.24 | 5:18 | 0:17 | 0 | 17 | [5 empty] | At Boudh end: Remote End Tripping,no relay operate
|  | 26.06.24 | 17:52 | 26.06.24 | 18:06 | 0:14 | 0 | 14 | [5 empty] | At Boudh end: Earth Fault,E/F in R-ph .Ir-1.488 KA 25.7 KM
|  | 04.09.24 | 10:13 | 04.09.24 | 10:58 | 0:45 | 0 | 45 | [5 empty] | At Boudh end: Dist- 57.63km, Zone 2
|  | 07.09.24 | 4:33 | 07.09.24 | 4:40 | 0:07 | 0 | 7 | [5 empty] | Tripped on E/F. 3.297 KM. Ia- 127.6 A, Ib-2.264 KA, Ic-80.34 A
|  | 28.02.25 | 23:17 | 28.02.25 | 23:33 | 0:16 | 0 | 16 | [5 empty] | At Bolangir New end: Dist- 55.28km, Zone 2, Ir- 1.679kA
|  | 14.03.25 | 10:55 | 14.03.25 | 11:01 | 0:06 | 0 | 6 | [5 empty] | Failed from source
|  | 31.03.25 | 09:52 | 31.03.25 | 10:34 | 0:42 | 0 | 42 | [5 empty] | At Bolangir New end: B-N, Ib- 1.031kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
256 | 132 kV Sonepur - Birmaharajpur |  |  |  |  | 0.84931 | 32 | 22 | [7 empty] | 24.774 | 8760 | 99.63% | 801.8518 | 217020.24
|  | 01.04.24 | 16:45 | 01.04.24 | 17:00 | 0:15 | 0 | 14 | [5 empty] | Source failure due to tree falling 132kV Sonepur-Bolangir line
|  | 19.04.24 | 16:27 | 19.04.24 | 18:08 | 1:41 | 1 | 41 | [5 empty] | Remote end Tripping
|  | 20.04.24 | 16:21 | 20.04.24 | 17:59 | 1:38 | 1 | 38 | [5 empty] | Y-B, Zone 1, Dist- 21.79km, Iy- 3.597kA, Ib- 3.214kA
|  | 07.05.24 | 05:27 | 07.05.24 | 06:07 | 0:40 | 0 | 40 | [5 empty] | At Bolangir New end: O/C, Ir- 0.605kA, Iy- 0.454kA, Ib- 0.345kA
|  | 17.05.24 | 08:03 | 17.05.24 | 08:18 | 0:15 | 0 | 15 | [5 empty] | At Biramaharajpur end: Remote End Tripping,SOURCE END TRIP
|  | 14.06.24 | 06:00 | 14.06.24 | 9:01 | 3:01 | 3 | 1 | [5 empty] | At Biramaharajpur end: Remote End Tripping,Shutdown availed for 132kV Bolangir-Sonepur Line from Sonepur end
|  | 18.06.24 | 06:04 | 18.06.24 | 7:58 | 1:54 | 1 | 54 | [5 empty] | At Biramaharajpur end: Remote End Tripping,Shutdown availed for 132kV Bolangir-Sonepur Line from Sonepur end
|  | 30.06.24 | 06:00 | 30.06.24 | 14:18 | 8:18 | 8 | 18 | [5 empty] | At Biramaharajpur end: Remote End Tripping, Shutdown availed for 132kV Bolangir-Sonepur Line from Sonepur end
|  | 03.07.24 | 07:00 | 03.07.24 | 8:21 | 1:21 | 1 | 21 | [5 empty] | Source failure
|  | 04.09.24 | 10:13 | 04.09.24 | 10:28 | 0:15 | 0 | 15 | [5 empty] | At Biramaharajpur end: Remote end tripping
|  | 5.11.24 | 09:53 | 5.11.24 | 10:00 | 0:07 | 0 | 7 | [5 empty] | At Biramaharajpur end: Distance Protection,Earth fault on B-phase(1.5kA), fault Resistance- 15.58 ohm, distance- 5km At Sonepur end: Tripped on E/F. Ia- 97.3 A, Ib- 189.9 A, Ic- 1.69 KA. 21.52 KM
|  | 28.02.25 | 23:17 | 28.02.25 | 23:33 | 0:16 | 0 | 16 | [5 empty] | At Bolangir New end: Dist- 55.28km, Zone 2, Ir- 1.679kA
|  | 31.03.25 | 09:52 | 31.03.25 | 10:34 | 0:42 | 0 | 42 | [5 empty] | At Bolangir New end: B-N, Ib- 1.031kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
257 | 132 kV New Bolangir - Bolangir Ckt - II |  |  |  |  | 0.97917 | 13 | 57 | [7 empty] | 3.008 | 8760 | 99.84% | 41.9616 | 26350.08
|  | 04.04.24 | 20:02 | 04.04.24 | 20:25 | 20:25 | 0 | 10 | [5 empty] | O/C
|  | 19.04.24 | 16:27 | 19.04.24 | 18:08 | 1:41 | 0 | 23 | [5 empty] | Distance Protection, Ia- 532A, Ib-2.813kA, Ic-2.514kA, Distance- 34.54km
|  | 11.06.24 | 16:54 | 11.06.24 | 17:07 | 0:13 | 0 | 13 | [5 empty] | Supply failure
|  | 11.06.24 | 17:37 | 11.06.24 | 17:47 | 0:10 | 0 | 10 | [5 empty] | Supply failure
|  | 15.07.24 | 15:57 | 15.07.24 | 16:50 | 0:53 | 0 | 53 | [5 empty] | At Bolangir end: E/F, O/C
|  | 07.09.24 | 18:55 | 07.09.24 | 19:03 | 0:08 | 0 | 8 | [5 empty] | At Bolangir end: Remote End Tripping,tripped with 132kV balangir new CKT I line simultaneously.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
258 | 132kV New Bolangir-Patnagarh Ckt - I |  |  |  |  | 0.0375 | 12 | 47 | [7 empty] | 39.41 | 8760 | 99.85% | 503.7912 | 345231.6
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 22.02.25 | 17:50 | 22.02.25 | 18:02 | 0:12 | 0 | 12 | [5 empty] | Tripped during E&MR testing
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
259 | 132kV New Bolangir-Patnagarh Ckt - II |  |  |  |  | 0.0375 | 12 | 34 | [7 empty] | 39.41 | 8760 | 99.86% | 495.2523 | 345231.6
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 27.06.24 | 11:21 | 27.06.24 | 11:46 | 0:25 | 0 | 12 | [5 empty] | At Bolangir New end: Distance Protection,Ia=82.93A, Ib=118.6A, Ic=6.524KA, Fault distance=3.528Km, Fault duration=80.01ms, fault resistance=1.04ohms At Patnagarh end: Distance Protection,C-N phase, Zone-II, loc:33.67KM, Ia=85.74A, Ib=119.34A, Ic=193.98A
|  | 8.02.25 | 16:28 | 8.02.25 | 16:33 | 0:05 | 0 | 5 | [5 empty] | At Bolangir New end: Over CurrentIa=389A, Ib=400A, Ic=396A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
260 | 132kV Duburi- BRPL |  |  |  |  | 0.37083 | 2 | 14 | [7 empty] | 7.632 | 8760 | 99.97% | 17.0448 | 66856.32
|  | 2.12.24 | 17:30 | 2.12.24 | 19:25 | 1:55 | 1 | 55 | [5 empty] | At Duburi end: O/C (R-N), Ir- 4.783kA
|  | 1.02.25 | 06:00 | 1.02.25 | 12:59 | 6:59 | 0 | 19 | [5 empty] | At Duburi end: R-N, Dist- 0.871km, Zone 1, Ir- 11.61kA No tripping at MESCO end.
261 | 132kV BRPL-Mesco |  |  |  |  | 0.37083 | 2 | 14 | [7 empty] | 4.436 | 8760 | 99.97% | 9.9071 | 38859.36
|  | 2.12.24 | 17:30 | 2.12.24 | 19:25 | 1:55 | 1 | 55 | [5 empty] | At Duburi end: O/C (R-N), Ir- 4.783kA
|  | 1.02.25 | 06:00 | 1.02.25 | 12:59 | 6:59 | 0 | 19 | [5 empty] | At Duburi end: R-N, Dist- 0.871km, Zone 1, Ir- 11.61kA No tripping at MESCO end.
262 | 132kV Lapanga-Jharsuguda |  |  |  |  | 0.0625 | 1 | 30 | [7 empty] | 10.4 | 8760 | 99.98% | 15.6 | 91104
|  | 05.06.24 | 04:11 | 05.06.24 | 5:12 | 1:01 | 1 | 1 | [5 empty] | At Lapanga end: R-N, Zone 1, Dist- 10.6km, Ir- 8.7kA
|  | 13.06.24 | 19:33 | 14.06.24 | 45457.8347 | 0:29 | 0 | 29 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.07KA IL2-0.23KA IL3-10.03KA DIST-1.9KM At Jharsuguda end: No tripping
263 | 132kV Budhipadar-Jharsuguda Ckt-I |  |  |  |  | 0.10347 | 1 | 2 | [7 empty] | 7 | 8760 | 99.99% | 7.2333 | 61320
|  | 05.06.24 | 04:11 | 05.06.24 | 6:40 | 2:29 | 1 | 2 | [5 empty] | At Jharsuguda end: Y-B, Zone 1, Iy- 0.592kA, Ib- 0.683kA
264 | 132kV Budhipadar-Jharsuguda Ckt-II |  |  |  |  | 0.53542 | 1 | 43 | [7 empty] | 4.5 | 8760 | 99.98% | 7.725 | 39420
|  | 05.06.24 | 04:11 | 05.06.24 | 6:03 | 1:52 | 1 | 2 | [5 empty] | At Jharsuguda end: B-N, Zone 1, Ir- 0.242kA, Iy- 0.819kA, Ib- 0.658kA
|  | 13.06.24 | 19:06 | 14.06.24 | 14.06.24 | 10:59 | 0 | 41 | [5 empty] | At Budhipadar end: Over Current, D/P(Areva P4): F.L-C-N, ZONE 1, il1- 531.3a,il2-235.3a,il3-13.5ka,F.R-1.805ohm, F.D- 1.299km,F.DUR- 51.72ms, RTT- 80.06msrn At Jharsuguda end: Distance Protection,CN, zone-I, Ir= 532.1 A, Iy=236.5 A, Ib= 3.715 kA, Fault Resistance= 5.930 ohm1.299km,F.DUR- 51.72ms, RTT- 80.06ms
265 | 132kV Budhipadar- Bamra |  |  |  |  | 0.91736 | 17 | 58 | [7 empty] | 53 | 8760 | 99.79% | 952.2333 | 464280
|  | 02.06.24 | 19:23 | 02.06.24 | 21:03 | 1:40 | 1 | 40 | [5 empty] | At Bamra end: Distance Protection,D.P-Fault Loop- L2-N, Zone- 1, Distance-9.037KM, F.D- 71.58ms,RTT=79.90ms, Ia=287.5A, Ib=3.292KA,Ic=253.5A At Budhipadar end: D/P operated, F.L=Y-N, F.D=38.57 km, Ia=291A,Ib=1.804kA, Ic=241 A, F. Resistance=21.09ohm,Zone1, F. Duration=58.26 ms
|  | 05.06.24 | 4:55 | 05.06.24 | 18:41 | 13:46 | 0 | 30 | [5 empty] | H/T for restoration of power supply
|  | 28.06.24 | 17:48 | 28.06.24 | 20:03 | 2:15 | 0 | 9 | [5 empty] | At Bamra end: Distance Protection,D.P- Fault Loop- L1-N, Zone- 1, Distance-21.14KM,R-Phase operated, F.D- 73.36ms, RTT=80.03ms, Ia=2.166KA, Ib=144.7A,Ic=230.2A,F.R-18.98ohm Make & type of Relay-ALSTOM Micom & P442 At Budhipadar end: D/P(MICOM P444): F.L-A-N,zone 1, F.D-27.38 KM,F.Dur- 60.02ms,IL1-2.58ka,IL2-133.7a,IL3-236.5a,F.R-13.41ohm
|  | 18.08.24 | 16:36 | 18.08.24 | 18:34 | 1:58 | 1 | 58 | [5 empty] | At Bamra end: Earth Fault,D.P- Fault Loop- L1-N, Zone- 1, Dist-14.33km,R- Phase operated, Dist-71.67ms,RTT=79.96ms, Ia=3.232kA, Ib-215.2A,Ic=299.8A, In-3921.07 At Budhipadar end: Dist Protection, Fault loop: Rph-N,Zone1, Dist-33.84 km, Duration=40.33 ms Ir=2.40 kA,Iy-205.7 A, Ib-306.3 A
|  | 23.08.24 | 17:59 | 23.08.24 | 19:40 | 1:41 | 1 | 0 | [5 empty] | At Budhipadar end: Dist Protection,D/P operated: F.L- A-N, ZONE 1, Dist-39.69km, Distur- 66.56ms, IA-2.388kA, IB-321.5A, IC-389.6A F.resistance-4.917ohm, At Bamra end: Earth Fault,D.P- Fault Loop- L1-N, Zone- 1, Dist-8.85km,R- Phase operated, Dist-74.88ms,RTT=79.87ms, Ia=4.427kA, Ib-330.9A,Ic=383.0A Ig=1.953A
|  | 23.08.24 | 23:08 | 23.08.24 | 23:49 | 0:41 | 0 | 41 | [5 empty] | At Budhipadar end: Dist Protection,D/P operated: F.L- A-N, ZONE 1, Dist-36.30km, Distur- 51.66ms, IA-2.438kA, IB-219.6A, IC-553.4A F.resistance-9.196ohm At Bamra end: Earth Fault,D.P- Fault Loop- L1-N, Zone- 1, Dist-12.19km,R- Phase operated, Dist-71.66ms,RTT=79.99ms, Ia=2.707kA, Ib-233.5A,Ic=554.3A Ig=3.551A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
266 | 132kV Bamra-Rajgangpur |  |  |  |  | 1899-12-31 03:59 | 17 | 3 | [7 empty] | 44.2 | 8760 | 99.81% | 753.61 | 387192
|  | 19.05.24 | 20:46 | 19.05.24 | 21:35 | 0:49 | 0 | 49 | [5 empty] | At Bamra end: Earth Fault,Fault=E/F, Fault Loop- L1-N, F.D- 570ms, RTT=551.0ms, Ia=2.303KA, Ib=199.4A, Ic=237.6A,In=2.166KA Make & type of Relay-ALSTOM Micom & P141 At Rajgangpur end: Earth Fault,DP Relay Operated, R-Phase, Zone- 1, IR=3.319 KA, IY=200.6 A, IB=234.8 A, IG= 3.284 KA, Distance=16.43 KM,
|  | 01.06.24 | 19:43 | 01.06.24 | 20:43 | 1:00 | 0 | 23 | [5 empty] | At Rajgangpur end: Over Current,TRIPPED AT BAMRA SIDE ZONE I,DISTANCE=8.193 KM,IA=4.64 KA,IB=288.6 A,IC=4.75 KA, FD=46.72 ms,FR=8.681 Ω,RT Time=80.09 ms
|  | 02.06.24 | 19:41 | 03.06.24 | 10:38 | 14:57 | 0 | 23 | [5 empty] | At Bamra end: Earth Fault,Fault type= E/F & O/C, R-phase operated, , F.D=620 ms, RTT=65 ms ,Ia= 1.837KA, Ib= 170.3A, Ic= 203A, In=1.616KA Make & type of Relay-ALSTOM Micom & P141 At Rajgangpur end: Earth Fault,R-PH,Z1-PU/Z1 TRIP, ZONE-1,IR=1.322 KA, IY=160.3 A, IB=192 A, DISTANCE=22.69 KM, MASTER TRIP RELAY OPERATED
|  | 13.06.24 | 16:59 | 13.06.24 | 17:50 | 0:51 | 0 | 16 | [5 empty] | At Rajgangpur end: Earth Fault,EARTH FAULT, R-PH, ZONE-3,IR=831.7A, IY=142.1 A, IB=183.9 A, DISTANCE=70.83 KM, FD=69.90 ms, MASTER TRIP RELAY OPERATED At Bamra end: Earth Fault, MASTER Fault type=E/F & O/C , R phase operated, F.D- 739ms,RTT=669ms, Ia= 1.448KA, Ib= 101.8A, Ic= 180.1A, In=1.34A
|  | 15.06.24 | 22:25 | 16.06.24 | 1:25 | 3:00 | 1 | 15 | [5 empty] | At Rajgangpur end: Earth Fault,R-PH,Z1 PU/Z1 TRIP, ZONE-1, IR=1.178 KA, IY=164.7 A, IB=301.6 A, DISTANCE=0 KM, FD=61.81 ms,RTT=80.19 ms MASTER TRIP RELAY OPERATED At Bamra end: Over Current,Fault type=O/C , R-Y-B-phase operated, F.D- 611ms,RTT=541ms, Ia= 2.193KA, Ib= 145.5A, Ic= 292.9A,
|  | 11.07.24 | 15:19 | 11.07.24 | 15:36 | 0:17 | 0 | 17 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.389kA, Iy- 0.401kA, Ib- 0.315kA
|  | 11.07.24 | 17:02 | 11.07.24 | 17:14 | 0:12 | 0 | 12 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.399kA, Iy- 0.392kA, Ib- 0.33kA
|  | 13.08.24 | 19:52 | 13.08.24 | 20:20 | 0:28 | 0 | 28 | [5 empty] | At Bamra end: E/F (R-N), Zone 1, Dist- 33.02km, Ir- 5.92kA
|  | 23.08.24 | 17:39 | 24.08.24 | 0:04 | 6:25 | 1 | 0 | [5 empty] | At Bamra end: Earth Fault,D.P- Fault Loop- L1-N, Zone- 1, Dist-8.38km,R-Phase operated, Dist-71.70ms,RTT=80.04ms, Ia=5.724kA, Ib-11.58A,Ic=10.95A,In=4.717kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
267 | 132kV Budhipadar-Sundargarh-I |  |  |  |  | 0.0090278 | 0 | 13 | [7 empty] | 31.21 | 8760 | 100% | 6.7622 | 273399.6
|  | 05.06.24 | 4:55 | 05.06.24 | 5:08 | 0:13 | 0 | 13 | [5 empty] | H/T for restoration of power supply
268 | 132kV Budhipadar-Sundargarh-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.21 | 8760 | 100% | 0 | 273399.6
269 | 132kV Budhipadar-MCL(Jorbaga)-I |  |  |  |  | 1899-12-31 20:52 | 55 | 48 | [7 empty] | 22.6 | 8760 | 99.36% | 1261.08 | 197976
|  | 18.05.24 | 13:28 | 18.05.24 | 16:39 | 3:11 | 3 | 11 | [5 empty] | At Budhipadar end: O/C,At Budhipadar end: D/P (MiCOM P444): F.L=Cph-N, zone 1, f.Dur=70.02 ms, RTT 0ms, F.D= 5.236 km, Il1=5.39 A, Il2=3.77A, Il3=9.6 kA, F.R=2.05 ohm
|  | 01.06.24 | 19:24 | 01.06.24 | 22:26 | 3:02 | 3 | 2 | [5 empty] | D/P operated: F.L=Y-B-N, F.D=9.78 km, Ia=4.76A Ib=9.01KA, Ic=7.65KA, F. Resistance=1.68ohm, Zone1, F. Duration=73.32ms
|  | 13.06.24 | 19:19 | 14.06.24 | 7:40 | 12:21 | 12 | 20 | [5 empty] | At Budhipadar end: Over Current, D/P(MICOM P444): F.L- A-N, ZONE 1,F.DU- 65.07ms,F.D- 11.63km, IL1- 2.76ka,IL2-4.7A,IL3-4.112A
|  | 16.06.24 | 03:26 | 16.06.24 | 5:52 | 2:26 | 2 | 26 | [5 empty] | R-N, Zone 1, Dist- 16.61km, Ir- 1.64kA
|  | 19.06.24 | 09:22 | 19.06.24 | 11:37 | 2:15 | 1 | 37 | [5 empty] | D/P: F.L- Bph-E, ZONE 1, F.D- 1.295km,F.Dur- 68.3ms, IL1-5.154A,IL2-3.48A,IL3-10.52KA, F.R-4.315ohm
|  | 05.06.24 | 3:47 | 05.06.24 | 10:05 | 6:18 | 6 | 18 | [5 empty] | At Budhipadar end: Over Current,(B.padar end ) D/P u2013 Tripped Phase-ABC, Fault loop- Bph to E, Zone 1, Dist- 1.57km, IL1- 135.9A, IL2-181.5A, IL3- 10.77kA, Fault duration- 70.01ms.
|  | 16.06.24 | 03:26 | 16.06.24 | 4:07 | 0:41 | 0 | 41 | [5 empty] | R-N, Zone 1, Dist- 12.2km, Ir- 2.28kA
|  | 06.08.24 | 15:44 | 06.08.24 | 17:10 | 1:26 | 1 | 1 | [5 empty] | At Budhipadar end: R-B-N, Zone 1, Dist- 14.17km, Ir- 5.642kA, Ib- 5.917kA
|  | 30.08.24 | 19:02 | 30.08.24 | 19:55 | 0:53 | 0 | 53 | [5 empty] | At Budhipadar end: Dist Protection,D/P operated: F.L- A-N, ZONE 2, Dist-17.78km, Distur- 340.0ms, IA-3.828kA, IB-117.4A, IC-110.8A F.resistance-3.37ohm,
|  | 17.09.24 | 09:40 | 17.09.24 | 12:42 | 3:02 | 3 | 2 | [5 empty] | At Budhipadar end: Over Current,D/P (MiOM P444): F-L=C-N, F.D= 3.886 km, F. Dur= 71.61 ms,Ia=180.1 A, Ib=294.2A,Ic=9.787kA
|  | 23.01.25 | 13:49 | 23.01.25 | 23:06 | 9:17 | 9 | 17 | [5 empty] | At Budhipadar end: DP operated, Zone-1,FL-Rph-E,FD-2.4KM,F.Duration-71.68ms, IL1-11.10KA, IL2-161.9A, IL3-277.3A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
270 | 132kV Budhipadar-Lakhanpur |  |  |  |  | 1899-12-31 11:48 | 18 | 53 | [7 empty] | 29.524 | 8760 | 99.78% | 557.5115 | 258630.24
|  | 05.06.24 | 4:55 | 05.06.24 | 8:52 | 3:57 | 0 | 47 | [5 empty] | H/T for restoration of power supply
|  | 19.06.24 | 09:22 | 19.06.24 | 11:08 | 1:46 | 1 | 37 | [5 empty] | At Lakhanpur end: Distance Protection,Phase-CN, ( Ia-0.00kA, Ib-0.01kA, Ic-2.18kA), Zone-1, Distance=18.8KM. At Budhipadar end: D/P: F.L- Bph-E, ZONE 1, F.D- 4.416km, Trip time- 79.96ms, F.Dur- 69.96ms, IL3-9.826KA, F.R-5.46ohm
|  | 20.06.24 | 17:12 | 21.06.24 | 16:09 | 22:57 | 1 | 11 | [5 empty] | At Lakhanpur end: Distance Protection,Phase-AN, ( Ia-1.86kA, Ib-0.33kA, Ic-0.31kA), Zone-1, Distance=12.8KM At Budhipadar end: D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-10.89km,IL1-7.47KA,IL2-341.8A,IL3-330.6A,F.R-297.7mohm,F.dur-65.09ms
|  | 08.07.24 | 13:18 | 08.07.24 | 18:06 | 4:48 | 1 | 2 | [5 empty] | At Lakhanpur end: Zone 1, Dist-20.2km, If- 2.21kA At Budhipadar end: Zone 1, B-N, Dist- 5.057km, Ib- 12.87kA
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 2024-10-09 | 13:36 | 2024-10-09 | 14:09 | 0:33 | 0 | 33 | [5 empty] | At Lakhanpur end: Remote end Tripping, At Budhipadar end: Ia=0.415kA, Ib=0.396kA, Ic=0.174kA
|  | 2.11.24 | 12:18 | 2.11.24 | 12:31 | 0:13 | 0 | 13 | [5 empty] | Remote End Tripping, At Budhipadar end: Ia=0.299kA, Ib=0.279kA, Ic=0.107kA, In=0.002kA.
|  | 18.01.25 | 4:40 | 18.01.25 | 5:04 | 0:24 | 0 | 24 | [5 empty] | At Budhipadar end: Dir O/C,Dir E/f,IL1-511.3A,IL2-466.4A,IL3-3.97A
|  | 18.03.25 | 12:54 | 18.03.25 | 13:20 | 0:26 | 0 | 22 | [5 empty] | Ir- 0.3kA, Iy- 0.276kA, Ib- 0.155kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
271 | 132kV Lakhanpur- Brajrajnagar (Remja) |  |  |  |  | 0.15069 | 15 | 37 | [7 empty] | 20.109 | 8760 | 99.82% | 314.0356 | 176154.84
|  | 20.06.24 | 17:12 | 21.06.24 | 18:23 | 1:11 | 1 | 11 | [5 empty] | At Brajarajnagar end: Earth Fault,DP operated, Zone 1, FL= R-E, Fault Dist. 2.3 km, IL1= 8.49 KA
|  | 08.07.24 | 14:26 | 08.07.24 | 15:28 | 1:02 | 1 | 2 | [5 empty] | At Lakhanpur end: Source Failure due to overloading of 132kV Budhipadar-Brajarajnagar Line.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 18.03.25 | 12:54 | 18.03.25 | 13:34 | 0:40 | 0 | 40 | [5 empty] | Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
272 | 132kV Brajrajnagar (Remja)- MCL(Jorbaga) |  |  |  |  | 1899-12-31 14:13 | 33 | 39 | [7 empty] | 24.855 | 8760 | 99.62% | 836.3707 | 217729.8
|  | 01.06.24 | 19:31 | 02.06.24 | 12:29 | 16:58 | 16 | 58 | [5 empty] | At Brajarajnagar end: Distance Protection,zone-2 , IL1=0KA, IL2=0.47KA, IL3=0.01, Fault distance =17.9km, Fault duration =40ms
|  | 20.06.24 | 17:12 | 21.06.24 | 18:09 | 0:57 | 0 | 54 | [5 empty] | D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-8.135km,IL1-7.78KA,IL2-338.8A,IL3-920.3A,F.R-1.14ohm,F.dur-93.44ms
|  | 08.07.24 | 14:26 | 08.07.24 | 15:10 | 15:10 | 0 | 40 | [5 empty] | At Budhipadar end: O/C (R Ph), Ir- 0.46kA No tripping at Brajarajnagar end.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 06.08.24 | 15:44 | 06.08.24 | 18:03 | 2:19 | 1 | 1 | [5 empty] | At Brajarajnagar end: R-B, Zone 1, Ir- 5.45kA, Ib- 5.62kA, Dist- 16.4km
|  | 30.08.24 | 19:02 | 30.08.24 | 20:38 | 1:36 | 0 | 53 | [5 empty] | At Brajarajnagar end: Dist Protection,Zone 1, IL1= 1.15 kA, IL1-E, fault Dist- 20.6 km, fault duration- 352 ms
|  | 18.01.25 | 4:40 | 18.01.25 | 5:09 | 0:29 | 0 | 29 | [5 empty] | At Budhipadar end: Dir L1 Pu,IL1-0.46KA,IL2-0.43KA,IL3-0.06KA)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
273 | 132kV Budhipadar-MSP |  |  |  |  | 0.056944 | 1 | 22 | [7 empty] | 0.592 | 8760 | 99.98% | 0.80907 | 5185.92
|  | 05.06.24 | 4:55 | 05.06.24 | 5:30 | 0:35 | 0 | 35 | [5 empty] | H/T for restoration of power supply
|  | 16.06.24 | 3:36 | 16.06.24 | 4:23 | 0:47 | 0 | 47 | [5 empty] | B-N, Ib- 2.98kA
274 | 132kV Budhipadar-Brajrajnagar (Remja) |  |  |  |  | 0.81736 | 15 | 44 | [7 empty] | 11.75 | 8760 | 99.82% | 184.8667 | 102930
|  | 05.06.24 | 4:55 | 05.06.24 | 5:12 | 0:17 | 0 | 17 | [5 empty] | H/T for restoration of power supply
|  | 20.06.24 | 17:12 | 21.06.24 | 18:09 | 0:57 | 0 | 54 | [5 empty] | D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-8.135km,IL1-7.78KA,IL2-338.8A,IL3-920.3A,F.R-1.14ohm,F.dur-93.44ms
|  | 08.07.24 | 14:26 | 08.07.24 | 15:10 | 15:10 | 0 | 40 | [5 empty] | At Budhipadar end: O/C (R Ph), Ir- 0.46kA No tripping at Brajarajnagar end.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 18.01.25 | 4:40 | 18.01.25 | 5:09 | 0:29 | 0 | 29 | [5 empty] | At Budhipadar end: Dir L1 Pu,IL1-0.46KA,IL2-0.43KA,IL3-0.06KA)
|  | 18.03.25 | 12:54 | 18.03.25 | 14:54 | 2:00 | 0 | 40 | [5 empty] | Y-N, Dist- 1.652km, Iy- 10.53kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
275 | 132kV Brajrajnagar- RTSS Kecchobahal |  |  |  |  | 0.82569 | 17 | 14 | [7 empty] | 11.75 | 8760 | 99.8% | 202.4917 | 102930
|  | 05.06.24 | 4:55 | 05.06.24 | 5:12 | 0:17 | 0 | 17 | [5 empty] | H/T for restoration of power supply
|  | 20.06.24 | 17:12 | 21.06.24 | 18:09 | 0:57 | 0 | 54 | [5 empty] | D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-8.135km,IL1-7.78KA,IL2-338.8A,IL3-920.3A,F.R-1.14ohm,F.dur-93.44ms
|  | 08.07.24 | 14:26 | 08.07.24 | 15:10 | 15:10 | 0 | 40 | [5 empty] | At Budhipadar end: O/C (R Ph), Ir- 0.46kA No tripping at Brajarajnagar end.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 18.01.25 | 4:40 | 18.01.25 | 5:09 | 0:29 | 0 | 29 | [5 empty] | At Budhipadar end: Dir L1 Pu,IL1-0.46KA,IL2-0.43KA,IL3-0.06KA)
|  | 18.03.25 | 12:54 | 18.03.25 | 15:06 | 2:12 | 2 | 10 | [5 empty] | Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
276 | 132kV Brajrajnagar- RTSS Belpahar Ckt-I |  |  |  |  | 0.82361 | 17 | 4 | [7 empty] | 11.293 | 8760 | 99.81% | 192.7339 | 98926.68
|  | 05.06.24 | 4:55 | 05.06.24 | 5:12 | 0:17 | 0 | 17 | [5 empty] | H/T for restoration of power supply
|  | 20.06.24 | 17:12 | 21.06.24 | 18:09 | 0:57 | 0 | 54 | [5 empty] | D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-8.135km,IL1-7.78KA,IL2-338.8A,IL3-920.3A,F.R-1.14ohm,F.dur-93.44ms
|  | 08.07.24 | 14:26 | 08.07.24 | 15:10 | 15:10 | 0 | 40 | [5 empty] | At Budhipadar end: O/C (R Ph), Ir- 0.46kA No tripping at Brajarajnagar end.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 18.01.25 | 4:40 | 18.01.25 | 5:09 | 0:29 | 0 | 29 | [5 empty] | At Budhipadar end: Dir L1 Pu,IL1-0.46KA,IL2-0.43KA,IL3-0.06KA)
|  | 18.03.25 | 12:54 | 18.03.25 | 15:03 | 2:09 | 2 | 0 | [5 empty] | Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
277 | 132kV Brajrajnagar- RTSS Belpahar Ckt-II |  |  |  |  | 0.82361 | 17 | 4 | [7 empty] | 11.293 | 8760 | 99.81% | 192.7339 | 98926.68
|  | 05.06.24 | 4:55 | 05.06.24 | 5:12 | 0:17 | 0 | 17 | [5 empty] | H/T for restoration of power supply
|  | 20.06.24 | 17:12 | 21.06.24 | 18:09 | 0:57 | 0 | 54 | [5 empty] | D/P(MICOM P444): F.L- A-N, ZONE 1, F.D-8.135km,IL1-7.78KA,IL2-338.8A,IL3-920.3A,F.R-1.14ohm,F.dur-93.44ms
|  | 08.07.24 | 14:26 | 08.07.24 | 15:10 | 15:10 | 0 | 40 | [5 empty] | At Budhipadar end: O/C (R Ph), Ir- 0.46kA No tripping at Brajarajnagar end.
|  | 20.07.24 | 09:45 | 20.07.24 | 10:29 | 0:44 | 0 | 44 | [5 empty] | At Budhipdar end: Ir- 299.8A, Iy-271.9A, Ib-111.9A
|  | 18.01.25 | 4:40 | 18.01.25 | 5:09 | 0:29 | 0 | 29 | [5 empty] | At Budhipadar end: Dir L1 Pu,IL1-0.46KA,IL2-0.43KA,IL3-0.06KA)
|  | 18.03.25 | 12:54 | 18.03.25 | 15:03 | 2:09 | 2 | 0 | [5 empty] | Source failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
278 | 132kV Budhipadar - Kalunga |  |  |  |  | 1900-01-01 02:48 | 16 | 59 | [7 empty] | 99 | 8760 | 99.81% | 1681.35 | 867240
|  | 29.05.24 | 11:42 | 29.05.24 | 11:50 | 0:08 | 0 | 8 | [5 empty] | At Kalunga end: Distance Protection," 1) Fault Loop: Y-N 2)Zone-1 3) Fault Location: 35.62 km 4) Current- Ir- 320.0 A, Iy- 2.721 KA, Ib- 332.1 A 5) Fault Duration- 61.70 ms 6)Fault Resistance- 1.71 ohm
|  | 31.05.24 | 11:38 | 31.05.24 | 12:09 | 0:31 | 0 | 31 | [5 empty] | At Budhipadar end: O/C,Budhipadar End:D/P (MiCOM P444):F.L=Y ph-E,Zone 1,F.Dur=65.01 ms,F.D=34.52 km,Il1=336. A, Il2=2.78 kA,Il3=351.3 AF.R=-1.4 ohm At Kalunga end: Distance Protection,DP RELAY-1) Fault Loop: Y-N2)Zone-13) Fault Location: 34.52 km4) Current- Ir- 336.3 A, Iy- 2.78 kA, Ib- 351.5 A5) Fault Duration- 65.01 ms6)Fault Resistance- 1.47 ohm
|  | 01.06.24 | 19:14 | 01.06.24 | 21:57 | 2:43 | 0 | 37 | [5 empty] | At Kalunga end: DP Relay- Tripped Phase- R-N, Zone- 1, Fault location- 71.49 km, Fault duration- 41.65 ms,relay trip time - 79.47 ms, Ir-182.4 A, Iy-11.02A, Ib-10.69A, Fault Resistance- 31.76 ohm At Budhipadar end: zone-1,fault location-29.35 km,fault duration-71.65 ms, Ir-2.52 kA,Iy-308.0 A,Ib-355.0 A,fault resistance-15.40 ohm
|  | 20.06.24 | 16:16 | 20.06.24 | 18:36 | 2:20 | 0 | 7 | [5 empty] | At Kalunga end: DP Relay- Tripped Phase- B-N, Zone- 1, Fault location- 14 km, Fault duration- 59.96 ms,relay trip time - 79.95 ms, Ir-364.5 A, Iy-473.1A, Ib-433.7A, Fault Resistance- 42.72 ohm At Budhipadar end: zone-1,fault location-74.31 km,fault duration-59.96 ms, Ir-353.3A,Iy-464.5 A,Ib-1.47 kA,fault resistance-11.91 ohm
|  | 15.06.24 | 22:26 | 16.06.24 | 1:17 | 2:51 | 0 | 3 | [5 empty] | At Budhipadar end: D/P(MICOM P444)F.L- AB-N, ZONE 1,F.D-69.02km, F.dur-61.82ms, RTT-0s, IL1- 1.282kA, IL2-1.946kA, IL3-115.1A,Fault resistance- -9.061ohm At Kalunga end: No tripping
|  | 11.06.24 | 12:17 | 11.06.24 | 14:24 | 2:07 | 0 | 6 | [5 empty] | At Budhipadar end: Over Current,(At Budhipdar End):-DP (F.L- Yph-E, zone 1, F.D-30.75km, ia- 356a, Ib- 3.013ka, Ic- 363.9a, F.R- 2.0ohm, F.dur- 61.64ms)rn
|  | 13.06.24 | 17:00 | 13.06.24 | 18:24 | 1:24 | 0 | 6 | [5 empty] | At Budhipadar end: Over Current, D/P(MICOM P444)F.L- ABC, ZONE 1,F.D-62.73km, F.dur-64.24ms, RTT-0s, IL1- 1.673ka,IL2-242.9a, IL3-2.48karn
|  | 28.06.24 | 17:48 | 28.06.24 | 20:31 | 2:43 | 0 | 9 | [5 empty] | At Kalunga end: DP Relay- Tripped Phase- B-N, Zone- 1, Fault location- 51.65 km, Fault duration- 170 ms,relay trip time - 80.01 ms, Ir-300.2 A, Iy-322.4A, Ib-399.2A, Fault Resistance- 14.40 ohm At Budhipadar end: zone-1,fault location-24.10 km,fault duration-75.01 ms, Ir-3.6 kA,Iy-316A,Ib-394.9A,fault resistance-1.991 ohm
|  | 02.06.24 | 19:27 | 02.06.24 | 22:36 | 3:09 | 0 | 21 | [5 empty] | At Kalunga end: DP Relay- Tripped Phase- R-N, Zone- 1, Fault location- 31.20 km, Fault duration- 53.31 ms,relay trip time - 79.97 ms, Ir-442.9 A, Iy-252.8A, Ib-448.5A,Vrn-23.07 kv,Vyn-74.73 kv , Vbn-73.99 kv, Fault Resistance- 30.03 ohm At Budhipadar end: zone-1,fault location-61.73 km,fault duration-54.97 ms, Ir-1.743 kA,Iy-234.1 A,Ib-443.6 A,fault resistance-1.424 ohm
|  | 05.06.24 | 4:55 | 05.06.24 | 11:11 | 6:16 | 0 | 47 | [5 empty] | H/T for restoration of power supply
|  | 10.07.24 | 12:53 | 10.07.24 | 13:34 | 0:41 | 0 | 3 | [5 empty] | B-N, Zone 1, Dist- 34.56km, Ib- 2.818kA
|  | 14.07.24 | 3:47 | 14.07.24 | 4:01 | 0:14 | 0 | 14 | [5 empty] | R-Y-B, Dist- 74.26km, Ir-1.059kA, Iy-1.051kA, Ib-1.171kA
|  | 23.08.24 | 17:54 | 23.08.24 | 19:34 | 1:40 | 1 | 0 | [5 empty] | At Budhipadar end: Dist Protection,D/P operated: F.L- A-N, ZONE 1, Dist-37km, Distur- 56.74ms, IA-2.017kA, IB-74.85A, IC-44.15A F.resistance-14.98ohm, At Kalunga end: Earth Fault,Tripped ph- R-N, Zone- 1, Dist- 44.78 km, Fault Duration- 120.2 msec, Relay Trip time-, Ir= 1.188 kA, Iy-57.04 A, Ib-38.49 A, Fault Resistance - 20.49 ohm
|  | 23.08.24 | 22:26 | 24.08.24 | 0:31 | 2:05 | 0 | 41 | [5 empty] | At Budhipadar end: A-C-N, ZONE 1, Dist-40.91km, IA-3.111kA, IB-191.5A, IC-3.645kA At Kalunga end: E/F, R-N, Zone 1, Dist- 44.78 km, Ir=1.188 kA, Iy-57.04 A, Ib-38.49 A
|  | 10.09.24 | 16:50 | 10.09.24 | 17:14 | 0:24 | 0 | 3 | [5 empty] | At Kalunga end: Distance Protection,DP RELAY- ZONE-1, LOC-73.00 KM, DURATION-54.94ms , RTT-0 ms, Ir-1.5 KA At Budhipadar end: D/P-1(micom p442): F.L- Rph-E, ZONE 1, F.D- 73.69km, fault duration-54.94ms,IA-1.527KA, IB-287.4A, IC-477.6A ,F.R= -29.41mohm
|  | 10.09.24 | 17:14 | 11.09.24 | 14:46 | 21:32 | 0 | 3 | [5 empty] | At Kalunga end: Distance Protection,DP relay- zone-1, loc-69.48 km, RTT-0 ms, Duration-84.91 ms, Ir-1.4 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
279 | 132kV Kalunga - EIPL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2.25 | 1668 | 100% | 0 | 3753
280 | 132kV Burla PH-Chipilima Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.5 | 8760 | 100% | 0 | 170820
281 | 132kV Burla PH-Hindalco-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
282 | 132kV Burla PH-Hindalco-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 9 | 8760 | 100% | 0 | 78840
283 | 132kV Burla PH-Katapalli Ckt-I |  |  |  |  | 0.64861 | 0 | 42 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 7 | 8760 | 99.99% | 4.9 | 61320
|  | 23.05.24 | 19:14 | 24.05.24 | 10:48 | 15:34 | 0 | 42 | [5 empty] | At Katapali end: Earth Fault,Back up relay optd with IR=0A, IY=0A, IB=5.94KA fault duration=0.108ms
284 | 132kV Burla PH-Katapali Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 22.26 | 8760 | 100% | 0 | 194997.6
285 | 132kV Burla-Hirakud |  |  |  |  | 0.061111 | 1 | 52 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 6.2 | 8760 | 99.98% | 11.5733 | 54312
|  | 01.04.24 | 8:53 | 01.04.24 | 10:21 | 0.061111 | 1 | 52 | [5 empty] | At Burla PH end: E/F R Ph insulator burst at Loc No 118 from Lapanga end.
286 | 132kV Hirakud-Lapanga |  |  |  |  | 1900-01-01 09:24 | 20 | 59 | [7 empty] | 38.2 | 8760 | 99.76% | 801.5633 | 334632
|  | 01.04.24 | 8:53 | 02.04.24 | 17:26 | 1899-12-31 08:33 | 0 | 56 | [5 empty] | At Lapanga end: R-N, Zone 1, Dist- 3.4km, Ir- 13.76kA At Hirakud end: E/F, Ir- 1.512kA R Ph insulator burst at Loc No 118 from Lapanga end.
|  | 13.05.24 | 8:58 | 13.05.24 | 11:00 | 2:02 | 0 | 58 | [5 empty] | At Lapanga end: Distance Protection,IR-0.01KA IY-3.11KA IB-0.01KA DIST-52.6KM ZONE-2 FAULT DURATION-414mSec FAULT RESISTANCE-7.14Ohm B/U- YPH-E,O/C,E/F PICK UP At Hirakud end: MAIN RELAY: NA, BACKUP RELAY: IR=0.4KA, IY=5.7KA,IB=0.2KA
|  | 13.06.24 | 19:29 | 13.06.24 | 20:50 | 1:21 | 1 | 21 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.38KA IL2-0.25KA IL3-12.38KA DIST-1.8KM
|  | 01.06.24 | 20:53 | 01.06.24 | 22:37 | 1:44 | 1 | 44 | [5 empty] | At Lapanga end: Distance Protection,MAIN RELAY-1:- FAULT LOOP-L1-E ZONE-1 IL1-13.86KA IL2-0.06KA IL3-0.01KA DIST-1.7KM
|  | 03.09.24 | 14:29 | 04.09.24 | 10:13 | 19:44 | 4 | 0 | [5 empty] | At Lapanga end: O/C (R-Y), Zone 1, Dist- 15.6km, Ir- 5.48kA, Iy- 5.71kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
287 | 132kV Burla-Lapanga |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 43.6 | 8760 | 100% | 0 | 381936
288 | 132kV Lapanga-Budhipadar |  |  |  |  | 1899-12-31 06:03 | 15 | 18 | [7 empty] | 16 | 8760 | 99.83% | 244.8 | 140160
|  | 01.06.24 | 20:55 | 02.06.24 | 13:26 | 16:31 | 1 | 44 | [5 empty] | At Lapanga end: Over Current,O/C,L1-L2 IL1-0.0KA IL2-0.03KA IL3-8.62KA PUT-441mSec
|  | 05.06.24 | 03:46 | 05.06.24 | 16:30 | 12:44 | 0 | 46 | [5 empty] | At Lapanga end: O/C (R-N)
|  | 13.06.24 | 19:32 | 14.06.24 | 45457.8472 | 0:48 | 0 | 48 | [5 empty] | At Budhipadar end: Over Current,(AT Budhipadar end): D/P(SIEMENS 7SA52): F.L- L3-E, IL1-0.65KA,IL2-0.42KA,IL3-2.98KArn At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L3-E ZONE-1 IL1-0.65KA IL2-0.42KA IL3-9.12KA DIST-NA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
289 | 132kV Burla PH-Sambalpur |  |  |  |  | 0.82083 | 15 | 5 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 19.5 | 8760 | 99.83% | 294.125 | 170820
|  | 13.05.24 | 8:58 | 13.05.24 | 9:42 | 0:44 | 1 | 28 | [5 empty] | No tripping at Sambalpur end. Tripped at Burla PH end
|  | 20.05.24 | 21:21 | 20.05.24 | 22:14 | 0:53 | 0 | 48 | [5 empty] | At Sambalpur end: Tripped on Z1, Bph E/F, Ia=239A, Ib=197A,Ic=3041A, Ig=2729A, Fault dist.=12.64KM, fault duration= 57.477ms At Burla PH end: Tripped on Z1, Bph, Fault dist.=6.4KM
|  | 16.06.24 | 0:46 | 19.06.24 | 45462.7708 | 17:44 | 0 | 15 | [5 empty] | At Sambalpur end: Tripped on Z1, Bph E/F, Ia=239A, Ib=197A,Ic=3041A, Ig=2729A, Fault dist.=12.64KM, fault duration= 57.477ms At Burla PH end: tripped at 00:03Hr on Z1, Bph, Fault dist.=6.4KM
|  | 07.08.24 | 10:36 | 07.08.24 | 10:44 | 0:08 | 0 | 8 | [5 empty] | At Sambalpur end: No tripping At Burla PH end: O/C (B Ph), Ib- 1.19kA, Dist- 6.6km
|  | 2024-10-08 | 14:20 | 2024-10-08 | 14:33 | 0:13 | 0 | 26 | [5 empty] | At SambaIpur end:No tripping At Burla PH end: Yph,O/C, DP operated,Z1, Fault dist.=54.7KM, impedance=9.95 ohm,Iy= 3.75A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
290 | 132kV Chainpal-Angul |  |  |  |  | 0.10625 | 1 | 13 | [7 empty] | 14.93 | 8760 | 99.99% | 18.1648 | 130786.8
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 44 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 20.06.24 | 19:38 | 20.06.24 | 20:07 | 0:29 | 0 | 29 | [5 empty] | At Chainpal end: Distance Protection,ZONE-1, L1-N, DISTANCE=6.67KM, IA=3.8KA
291 | 132kV Chainpal-Global-TFL |  |  |  |  | 0.31597 | 19 | 34 | [7 empty] | 11.6 | 8760 | 99.78% | 226.9733 | 101616
|  | 05.05.24 | 12:01 | 05.05.24 | 12:54 | 0:53 | 0 | 53 | [5 empty] | Source Failure at GSS Chainpal as AUTO TRF I tripped at TTPS end
|  | 28.05.24 | 08:24 | 28.05.24 | 9:22 | 0:58 | 0 | 58 | [5 empty] | At Chainpal end: O/C,Earth Fault,Directional Overcurrent R phase, IR = 5.4kA,Directional Earth Fault, IN = 4.5kA At Global end: Remote End Tripping,Relay Indication at GSS Chainpal: Directional Overcurrent R phase, IR = 5.4kA, & E/F
|  | 05.06.24 | 6:40 | 05.06.24 | 7:03 | 0:23 | 0 | 23 | [5 empty] | At Chainpal end: Distance Protection,ZONE-1, L3N, DISTANCE=1.92KM, IC=9.2KA
|  | 19.09.24 | 10:48 | 19.09.24 | 11:26 | 0:38 | 0 | 37 | [5 empty] | 132kV Source failure.
|  | 25.03.25 | 17:58 | 25.03.25 | 22:41 | 4:43 | 4 | 43 | [5 empty] | O/C (B Ph), Ib- 8.29kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
292 | 132kV Chainpal-TFL |  |  |  |  | 0.1125 | 1 | 11 | [7 empty] | 7 | 8760 | 99.99% | 8.2833 | 61320
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 34 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 19.09.24 | 10:48 | 19.09.24 | 11:26 | 0:38 | 0 | 37 | [5 empty] | 132kV Source failure.
293 | 132kV Chainpal- Chainpal RTSS |  |  |  |  | 0.11458 | 1 | 5 | [7 empty] | 0.448 | 8760 | 99.99% | 0.48533 | 3924.48
|  | 05.05.24 | 11:44 | 05.05.24 | 13:58 | 2:14 | 0 | 34 | [5 empty] | At Meramundali end: O/C, Iy- 10.57kA At Chainpal end: Zone 2, Dist- 7.63km, Iy- 3.6kA
|  | 19.09.24 | 10:48 | 19.09.24 | 11:19 | 0:31 | 0 | 31 | [5 empty] | 132kV Source failure.
294 | 132kV Chandaka-Bhubaneswar-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.5 | 8760 | 100% | 0 | 48180
295 | 132kV Chandaka-Bhubaneswar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.5 | 8760 | 100% | 0 | 48180
296 | 132kV Chandaka-Mendhasal |  |  |  |  | 0 | 0 | 0 | [7 empty] | 18.1 | 8760 | 100% | 0 | 158556
297 | 132kV Chandaka-Nimapara |  |  |  |  | 0.12014 | 13 | 25 | [7 empty] | 65 | 8760 | 99.85% | 872.0833 | 569400
|  | 26.04.24 | 07:25 | 26.04.24 | 08:00 | 0:35 | 0 | 26 | [5 empty] | R-N, Zone 4, Dist- 0.674km, Ir- 1.77kA
|  | 07.04.24 | 18:02 | 07.04.24 | 19:32 | 1:30 | 0 | 17 | [5 empty] | At Chandaka end: R-B-N, Zone 1, Dist- 10.21km, Ir- 5.316kA, Ib- 5.547kA At Nimapara end: R-B-N, Zone 1, Dist- 50.37km, Ir- 1.13kA, Ib- 1.16kA
|  | 17.06.24 | 16:29 | 17.06.24 | 16:59 | 0:30 | 0 | 30 | [5 empty] | At Chandaka end: Distance Protection,A-B-N, Z-1, D=9.49KM, 5.86KA, 5.576KA, 202.8A
|  | 04.07.24 | 17:10 | 04.07.24 | 17:28 | 0:18 | 0 | 12 | [5 empty] | At Chandaka end: Y-N, Zone 2, Dist- 52.67km, Iy- 1.872kA At Nimapara end: Y-N, Zone 4, Dist- 0.491km, Iy- 1.7kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
298 | 132kV Chandaka-Ranasinghpur |  |  |  |  | 0.17847 | 13 | 1 | [7 empty] | 27.85 | 8760 | 99.85% | 362.5142 | 243966
|  | 07.04.24 | 18:02 | 07.04.24 | 19:36 | 1:34 | 0 | 17 | [5 empty] | At Chandaka end: R-B-N, Zone 1, Dist- 9.673km, Ir- 5.226kA, Ib- 5.663kA
|  | 17.06.24 | 16:29 | 17.06.24 | 17:04 | 0:35 | 0 | 15 | [5 empty] | At Chandaka end: Distance Protection,A-B-C-N, Z-1, D=8.215KM, 5.605KA, 6.268KA, 9.481KA At Ranasinghpur end: Remote End Tripping,Ia=5.605Ka, Ib=6.268Ka, Ic=9.481Ka, Distance=8.215Km(Zone 1)
|  | 18.06.24 | 14:00 | 18.06.24 | 15:22 | 1:22 | 0 | 13 | [5 empty] | At Chandaka end: Distance Protection,A-B-N, Z-1, D=8.26KM, 9.15KA, 5.64KA, 883A At Ranasinghpur end: Distance Protection,Zone1 distance= 17.55Km, Ia=239.1A, Ib=172.1A, Ic=872.7A.
|  | 28.02.25 | 02:00 | 28.02.25 | 2:46 | 0:46 | 0 | 16 | [5 empty] | At Chandaka end: Distance ProtectionC-N, Z-1, 9.486KM, 611A, 589.3A, 6.241KA, AR UNSUCCESSFUL
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
299 | 132kV Chandaka- Mancheswar-B Ckt -I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.2 | 8760 | 100% | 0 | 98112
300 | 132kV Chandaka B-Unit-8 |  |  |  |  | 0.040278 | 0 | 58 | [7 empty] | 11.4 | 8760 | 99.99% | 11.02 | 99864
|  | 24.02.25 | 12:56 | 24.02.25 | 13:54 | 0:58 | 0 | 58 | [5 empty] | 132kV I/C POWER SUPPLY FAILED FROM CHANDAKA -B END.
301 | 132kV Chandpur - Atri |  |  |  |  | 0.029167 | 0 | 42 | [7 empty] | 43.03 | 8760 | 99.99% | 30.121 | 376942.8
|  | 05.04.24 | 11:14 | 05.04.24 | 11:40 | 0:26 | 0 | 26 | [5 empty] | At Atri end: O/C (B Ph), Ib- 0.854kA At Chandpur end: O/C (B Ph), Ib- 0.854kA
|  | 18.04.24 | 11:20 | 18.04.24 | 11:36 | 0:16 | 0 | 16 | [5 empty] | At Atri end: O/C (B Ph), Dist- 35.53km, Ib- 0.282kA No tripping at Chandpur end
302 | 132kV Atri - Khurdha Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.29 | 8760 | 100% | 0 | 90140.4
303 | 132kV Atri - Khurdha Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.24 | 8760 | 100% | 0 | 89702.4
304 | 132kV Atri-Shamuka |  |  |  |  | 0.39167 | 12 | 45 | [7 empty] | 68.94 | 8760 | 99.85% | 878.985 | 603914.4
|  | 13.06.24 | 23:58 | 13.06.24 | 45457.3368 | 8:07 | 0 | 20 | [5 empty] | At Atri end: Distance Protection,R-Y-B phase-N, Zone- 1, IR =4.598 kA, IY=4.496 kA, IB=4.614 kA, Distance- 23.19 km At Shamuka end: Remote End Tripping,Ir-4.598kA,Iy-4.496KA,Ib-4.614KA,DISTANCE-23.19, FAULT TYPE: 3Phase to ground, Zone-I
|  | 16.06.24 | 11:53 | 16.06.24 | 12:07 | 0:14 | 0 | 14 | [5 empty] | At Shamuka end: Remote End Tripping,Fault Type: RYphase to ground , Ir-2,408KA, Iy-2.179KA,Ib-283.7A , Distance-55.26km, Zone-I At Atri end: Distance Protection,R-Y phase-N , Ir = 2.408 kA, Iy= 2.179 kA, Ib= 283.7 A , Distance-55.26 km, Zone-1
|  | 27.12.24 | 16:47 | 27.12.24 | 17:50 | 1:03 | 0 | 11 | [5 empty] | At Atri end: B-N, Ib- 1.666kA, Zone-2, Dist- 59.9 km At Shamuka end: Y-B, Zone-2
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
305 | 132kV Atri - Argul Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
306 | 132kV Atri - Argul Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 19.4 | 8760 | 100% | 0 | 169944
307 | 132kV Atri - Banki |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.5 | 8760 | 100% | 0 | 179580
308 | 132kV Khurdha-Kaipadar RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.26 | 8760 | 100% | 0 | 98637.6
309 | 132kV Chandikhol-Kendrapada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31.2 | 8760 | 100% | 0 | 273312
310 | 132kV Chatrapur-Balugaon |  |  |  |  | 0.84444 | 13 | 4 | [7 empty] | 53.79 | 8760 | 99.85% | 702.856 | 471200.4
|  | 07.04.24 | 17:03 | 07.04.24 | 18:42 | 1:39 | 0 | 13 | [5 empty] | At Balugaon end: E/F (R-N), Zone 1, Dist- 20.60km, Ir- 1.002kA At Chatrapur end: R-N, Zone 1, Dist- 40.47km, Ir- 1.093kA, A/R Lockout
|  | 30.04.24 | 23:25 | 30.04.24 | 23:31 | 0:06 | 0 | 6 | [5 empty] | O/C (Y & B Ph), Iy- 0.44kA, Ib-0.45kA
|  | 23.02.25 | 16:52 | 24.02.25 | 11:23 | 18:31 | 0 | 45 | [5 empty] | At Balugaon end: B-N, Zone 1, Dist- 0.93km, Ib- 1.494kA At Chatrapur end: B-N, Dist- 60.35km, Zone 2, Ib- 1.493KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
311 | 132kV Chatrapur-Ganjam |  |  |  |  | 1899-12-31 03:18 | 39 | 18 | [7 empty] | 12.6 | 8760 | 99.55% | 495.18 | 110376
|  | 7.11.24 | 00:33 | 7.11.24 | 10:54 | 10:21 | 10 | 21 | [5 empty] | At Chatrapur end: Distance Protection,DP Relay (SEL 311C):AG-T,Z-1,Fault Distance:4.78km,IR=5964A,IY=52A,IB=183A,IG=5745A
|  | 30.12.24 | 08:15 | 30.12.24 | 8:45 | 0:30 | 0 | 30 | [5 empty] | DP Relay operated with 86A & 86B
|  | 11.03.25 | 11:28 | 12.03.25 | 3:55 | 16:27 | 16 | 27 | [5 empty] | At Chatrapur end: Y-B, Zone 2, Dist- 11.32km, Iy- 4.637kA, Ib- 4.585kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
312 | 132kV Chatrapur-IRE-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
313 | 132kV Chatrapur-IRE-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.8 | 8760 | 100% | 0 | 50808
314 | 132kV Chatrapur-Rambha RTSS |  |  |  |  | 0.47986 | 23 | 31 | [7 empty] | 28.5 | 8760 | 99.73% | 670.225 | 249660
|  | 25.04.24 | 11:53 | 25.04.24 | 11:56 | 0:03 | 0 | 3 | [5 empty] | O/C (R-Y), Ir- 0.27kA, Iy- 0.23kA
|  | 25.04.24 | 12:13 | 25.04.24 | 12:17 | 0:04 | 0 | 4 | [5 empty] | O/C (R-Y), Ir- 0.27kA, Iy- 0.28kA
|  | 21.05.24 | 14:15 | 21.05.24 | 14:30 | 0:15 | 0 | 15 | [5 empty] | At Chatrapur end: O/C,Back-up relay (Siemens Siprotec 7SJ66) O/C (R-Y )Ph with M/R (IR=0.27KA,IY=0.27KA)
|  | 26.05.24 | 05:18 | 26.05.24 | 05:25 | 0:07 | 0 | 7 | [5 empty] | At Chatrapur end: O/C,Back-up relay (Siemens Siprotec 7SJ66) O/C (R-Y) Ph with M/R (IR=0.91KA,IY=0.91KA).
|  | 23.08.24 | 11:23 | 23.08.24 | 11:26 | 0:03 | 0 | 3 | [5 empty] | At Chatrapur end: O/C,Back-up relay, O/C (R-Y )Ph with M/R (IR=0.26kA,Iy-0.25kA)
|  | 23.08.24 | 14:56 | 23.08.24 | 15:00 | 0:04 | 0 | 4 | [5 empty] | At Chatrapur end: O/C,Back-up relay, O/C (R-Y )Ph with M/R (IR=0.27kA,Iy-0.26kA)
|  | 6.12.24 | 23:36 | 7.12.24 | 10:16 | 10:40 | 10 | 40 | [5 empty] | At Chatrapur end: Y-N, Iy- 5.97kA, Dist- 5.25km
|  | 10.12.24 | 07:23 | 10.12.24 | 7:31 | 0:08 | 0 | 8 | [5 empty] | O/C (R-Y), Ir- 0.314kA, Iy- 0.308kA
|  | 20.01.25 | 06:28 | 20.01.25 | 6:31 | 0:03 | 0 | 3 | [5 empty] | At Chatrapur end: O/C (R-Y), If- 0.267kA
|  | 12.02.25 | 16:25 | 12.02.25 | 16:29 | 0:04 | 0 | 4 | [5 empty] | At Chatrapur end: Over CurrentO/C (R,Y Phase) BU Operated IR=257.1A,IY=249.8A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
315 | 132kV Chhend-Shree Ganesh Metalics |  |  |  |  | 0.775 | 30 | 36 | [7 empty] | 12.26 | 2748 | 98.89% | 375.156 | 33690.48
|  | 04.05.24 | 10:27 | 04.05.24 | 12:39 | 2:12 | 2 | 12 | [5 empty] | At Chend end: B-N, Zone 1, Dist- 10.59km, ib- 2.761kA
|  | 03.05.24 | 12:54 | 03.05.24 | 13:36 | 0:42 | 0 | 42 | [5 empty] | At Tarkera end: B-N, Zone 2, Ib- 5.225kA
|  | 15.06.24 | 21:36 | 16.06.24 | 12:51 | 15:15 | 15 | 15 | [5 empty] | At Chhend end: Distance Protection,Distance Protection,Zone 2 loc-12.54km time-80.23 ms IL1=252.4A ,IL2=4.321KA ,IL3=267.3A ,Zone 1 loc-11.35km time-80.12 ms IL1=222.5A ,IL2=4.947KA ,IL3=4.993KA
|  | 21.06.24 | 17:29 | 21.06.24 | 17:56 | 0:27 | 0 | 27 | [5 empty] | At Chhend end: Distance Protection,Zone-1 loc=4.72km IL1=110.7A IL2=178.8A IL3=6.38KA Trip time-79.9ms
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
316 | 132kV Chhend-Kuarnmunda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.778 | 6012 | 100% | 0 | 58785.336
317 | 132kV Kuarnmunda-Shree Ganesh Metalics |  |  |  |  | 0.22847 | 5 | 29 | [7 empty] | 3.482 | 6012 | 99.91% | 19.093 | 20933.784
|  | 22.02.25 | 15:59 | 22.02.25 | 21:28 | 5:29 | 5 | 29 | [5 empty] | At Kuarmunda end: R-Y-B (O/C), Zone 1, Dist- 669.2 mtr, Ir- 8.675kA , Iy- 6.712kA, Ib- 0.086kA
318 | 132kV Shree Ganesh Metalics-Adhunik Metalics |  |  |  |  | 0.12083 | 2 | 54 | [7 empty] | 11.78 | 8760 | 99.97% | 34.162 | 103192.8
|  | 04.05.24 | 10:27 | 04.05.24 | 12:39 | 2:12 | 2 | 12 | [5 empty] | At Chend end: B-N, Zone 1, Dist- 10.59km, ib- 2.761kA
|  | 03.05.24 | 12:54 | 03.05.24 | 13:36 | 0:42 | 0 | 42 | [5 empty] | At Tarkera end: B-N, Zone 2, Ib- 5.225kA
319 | 132kV Chhend-Nuagaon RTSS |  |  |  |  | 0.14583 | 15 | 30 | [7 empty] | 34.6 | 8760 | 99.82% | 536.3 | 303096
|  | 03.05.24 | 12:54 | 03.05.24 | 13:36 | 0:42 | 0 | 42 | [5 empty] | At Tarkera end: B-N, Zone 2, Ib- 5.225kA
|  | 20.06.24 | 17:24 | 20.06.24 | 45463.7264 | 0:02 | 0 | 2 | [5 empty] | At Chhend end: Distance Protection,BC Zone-1 loc-20.14 km IL1=30 A IL2=3.32KA IL3=0A Ig=3.31KA
|  | 20.06.24 | 17:27 | 20.06.24 | 45463.7569 | 0:43 | 0 | 43 | [5 empty] | At Chhend end: Distance Protection,zone 1 Loc-9.81 km IL1=4856A IL2=7 A IL3=0 A IG=4862 A
|  | 14.07.24 | 16:58 | 14.07.24 | 19:01 | 2:03 | 2 | 3 | [5 empty] | At Chend end: R-Y, Zone 1, Dist-18.75 km, Ir- 4.524kA, Iy- 4.239kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
320 | 132kV Chipilima-Katapalli Ckt-I |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
321 | 132kV Chipilima-Katapalli Ckt-II |  |  |  |  | 0 | 0 | 0 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor and additional 12 hours is added. |  | 12.66 | 8760 | 100% | 0 | 110901.6
322 | 132kV Choudwar-Bidanasi |  |  |  |  | 0.19931 | 13 | 44 | [7 empty] | 15.41 | 8760 | 99.84% | 211.6307 | 134991.6
|  | 03.04.24 | 13:04 | 03.04.24 | 13:13 | 0:09 | 0 | 9 | [5 empty] | At Choudwar end: Zone 1, Ir- 0.501kA, Iy- 0.792kA, Ib- 4.86kA, Dist- 4.537km At Bidanasi end: E/F (Y-N), Zone 1, Dist- 7.44km, Iy- 5.9kA
|  | 19.04.24 | 18:23 | 19.04.24 | 18:50 | 0:27 | 0 | 27 | [5 empty] | At Bidanasi end: Zone 2, Dist- 7.44km, Ir- 1.055kA, Iy- 1.25kA, Ib- 4.97kA At Choudwar end: O/C (R-Y-B), Zone 4, Dist- -0.199km, Ir- 4.985kA, Iy- 1.058KA, Ib- 1.254kA
|  | 19.04.24 | 12:21 | 19.04.24 | 15:07 | 2:46 | 0 | 12 | [5 empty] | Remote end Tripping
|  | 11.05.24 | 23:10 | 11.05.24 | 23:45 | 0:35 | 0 | 15 | [5 empty] | At Bidanasi end: O/C ( B Ph), Zone 1, Ir-1.31KA, Iy-1.21KA, Ib-5.1KA At Choudwar end: Zone 1, Ir- 1.444kA, Iy- 1.317kA, Ib- 1.21kA
|  | 28.07.24 | 17:45 | 28.07.24 | 17:53 | 0:08 | 0 | 8 | [5 empty] | At Bidanasi end: O/C, Ir- 3.91kA, Iy- 3.89kA, Ib- 3.87kA
|  | 2024-10-18 | 13:00 | 2024-10-18 | 13:19 | 0:19 | 0 | 10 | [5 empty] | At Choudwar end: Line Differentional Protection, Zone 1, distance- 5.11km, Ir- 0.42kA, Iy- 0.51kA, Ib- 5.443kArn At Bidanasi end: Zone 1, dist-8.01km, Ir-0.511kA, Iy-0.005kA, Ib-0.419kA
|  | 12.02.25 | 07:49 | 12.02.25 | 8:12 | 0:23 | 0 | 23 | [5 empty] | At Choudwar end: Over Current At Bidanasi end: O/C R,Y,B phase, E/F. Ir-1.5kA, Iy-1.3kA, Ib-4.5kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
323 | 132kV Choudwar-Kendrapara Road RTSS |  |  |  |  | 0.20764 | 14 | 19 | [7 empty] | 4.6 | 8760 | 99.84% | 65.8567 | 40296
|  | 19.04.24 | 18:23 | 19.04.24 | 18:50 | 0:27 | 0 | 27 | [5 empty] | At Bidanasi end: Zone 2, Dist- 7.44km, Ir- 1.055kA, Iy- 1.25kA, Ib- 4.97kA At Choudwar end: O/C (R-Y-B), Zone 4, Dist- -0.199km, Ir- 4.985kA, Iy- 1.058KA, Ib- 1.254kA
|  | 19.04.24 | 12:21 | 19.04.24 | 15:07 | 2:46 | 0 | 39 | [5 empty] | Remote end Tripping
|  | 11.05.24 | 23:10 | 11.05.24 | 23:45 | 0:35 | 0 | 15 | [5 empty] | At Bidanasi end: O/C ( B Ph), Zone 1, Ir-1.31KA, Iy-1.21KA, Ib-5.1KA At Choudwar end: Zone 1, Ir- 1.444kA, Iy- 1.317kA, Ib- 1.21kA
|  | 13.07.24 | 12:57 | 13.07.24 | 13:14 | 0:17 | 0 | 17 | [5 empty] | At TS Alloys end: O/C (R-Y Ph)
|  | 28.07.24 | 17:45 | 28.07.24 | 17:53 | 0:08 | 0 | 8 | [5 empty] | At Bidanasi end: O/C, Ir- 3.91kA, Iy- 3.89kA, Ib- 3.87kA
|  | 2024-10-18 | 13:00 | 2024-10-18 | 13:19 | 0:19 | 0 | 10 | [5 empty] | At Choudwar end: Line Differentional Protection, Zone 1, distance- 5.11km, Ir- 0.42kA, Iy- 0.51kA, Ib- 5.443kArn At Bidanasi end: Zone 1, dist-8.01km, Ir-0.511kA, Iy-0.005kA, Ib-0.419kA
|  | 12.02.25 | 07:49 | 12.02.25 | 8:16 | 0:27 | 0 | 23 | [5 empty] | At Choudwar end: Over Current At TS Alloys: O/C , E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
324 | 132kV Cuttack-Jagatsinghpur |  |  |  |  | 0.21667 | 12 | 34 | [7 empty] | 34.71 | 8760 | 99.86% | 436.189 | 304059.6
|  | 19.04.24 | 12:21 | 19.04.24 | 15:07 | 2:46 | 0 | 4 | [5 empty] | Remote end Tripping
|  | 23.04.24 | 14:22 | 23.04.24 | 14:48 | 0:26 | 0 | 10 | [5 empty] | Remote end Tripping
|  | 23.09.24 | 21:18 | 23.09.24 | 21:51 | 0:33 | 0 | 8 | [5 empty] | At Cuttack end: Distance Protection,Tripped on Distance Protection in zone 3 with LG fault ( Y-ph to Ground).rnIndications on DP Relay: Trip in Zone 3, Dist: shown 48.3km (But the line length is only 35.112km)rnFault Currents: IR=296.8kA, IY=1.924kA, IB=120.5A At Jagatsinghpur end: No tripping
|  | 2024-10-07 | 14:59 | 2024-10-07 | 16:26 | 1:27 | 0 | 12 | [5 empty] | Tripped on O/C in Y-ph & E/F. Indications on DP Relay: Trip in Zone 2, Fault Location: 32.35km, Current: IR=288.4A, IY=3.459kA, IB=3.345kA, Van=74.12kV, Vbn=54.44kV, Vcn=52.83kV
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
325 | 132kV Cuttack-Phulnakhara |  |  |  |  | 0 | 0 | 0 | [7 empty] | 20.26 | 8760 | 100% | 0 | 177477.6
326 | 132kV Dhenkanal-Khuntuni-Grid Steel -ICCL |  |  |  |  | 0.32569 | 14 | 7 | [7 empty] | 39.18 | 8760 | 99.84% | 553.091 | 343216.8
|  | 06.05.24 | 17:27 | 06.05.24 | 17:47 | 0:20 | 0 | 20 | [5 empty] | At Khajuriakata end: E/F (B Ph), Zone 1, Dist- 13.2km, Ib- 1.825kA
|  | 08.05.24 | 17:56 | 08.05.24 | 18:04 | 0:08 | 0 | 8 | [5 empty] | At Khuntuni end: Distance Protection,At Khntn end- Zone-1, R-Ph fault, fault distance-14.33 KM, Fault current-Ir=298.32 A, Iy=163.71 A, Ib=289.07 A.
|  | 26.05.24 | 08:51 | 26.05.24 | 08:56 | 0:05 | 0 | 3 | [5 empty] | At Khuntuni end: Remote End Tripping,fault at Meramundali end
|  | 17.06.24 | 16:20 | 17.06.24 | 16:36 | 0:16 | 0 | 16 | [5 empty] | At Khuntuni end: Remote End Tripping,Incoming supply failed from Meramundali GSS end.
|  | 13.07.24 | 12:56 | 13.07.24 | 13:14 | 0:18 | 0 | 10 | [5 empty] | Supply failure
|  | 11.12.24 | 9:18 | 11.12.24 | 9:21 | 0:03 | 0 | 3 | [5 empty] | Source failure at Dhenkanal end
|  | 6.01.25 | 12:44 | 6.01.25 | 12:55 | 0:11 | 0 | 11 | [5 empty] | At Khuntuni end: R-N, Zone 1, Dist- 14.34km, Ir- 0.424kA At ICCL end: R-N, Zone 2, Dist- 19.96km, Ir- 5kA
|  | 6.01.25 | 13:13 | 6.01.25 | 18:56 | 5:43 | 0 | 14 | [5 empty] | At Khuntuni end: R-N, Zone 1, Dist- 14.34km, Ir- 0.27kA At ICCL end: R-N, Zone 2, Dist- 20.1km, Ir- 4.976kA
|  | 11.01.25 | 18:08 | 11.01.25 | 18:34 | 0:26 | 0 | 23 | [5 empty] | At Khuntuni end: Remote End Tripping
|  | 7.02.25 | 12:20 | 7.02.25 | 12:27 | 0:07 | 0 | 7 | [5 empty] | At Khuntuni end: Incoming supply failed from Dhenkanal end
|  | 28.03.25 | 12:30 | 28.03.25 | 12:42 | 0:12 | 0 | 12 | [5 empty] | At Khuntuni end: E/F, Iy- 1.105kA No tripping at Dhenkanal end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
327 | 132kV Khuntuni- Shree Cement |  |  |  |  | 0.32153 | 14 | 0 | [7 empty] | 6.45 | 8760 | 99.84% | 90.3 | 56502
|  | 06.05.24 | 17:27 | 06.05.24 | 17:47 | 0:20 | 0 | 20 | [5 empty] | At Khajuriakata end: E/F (B Ph), Zone 1, Dist- 13.2km, Ib- 1.825kA
|  | 08.05.24 | 17:56 | 08.05.24 | 18:04 | 0:08 | 0 | 8 | [5 empty] | At Khuntuni end: Distance Protection,At Khntn end- Zone-1, R-Ph fault, fault distance-14.33 KM, Fault current-Ir=298.32 A, Iy=163.71 A, Ib=289.07 A.
|  | 13.07.24 | 12:56 | 13.07.24 | 13:14 | 0:18 | 0 | 10 | [5 empty] | Supply failure
|  | 18.07.24 | 19:50 | 18.07.24 | 19:57 | 0:07 | 0 | 7 | [5 empty] | At Khajuriakata end: O/C (R-N), Ir- 3.187kA, Zone 1, Dist- 2.7km
|  | 18.07.24 | 21:29 | 18.07.24 | 21:31 | 0:02 | 0 | 2 | [5 empty] | At Khajuriakata end: O/C (R-N), Ir- 3.19kA, Zone 1, Dist- 2.7km
|  | 6.01.25 | 12:44 | 6.01.25 | 12:55 | 0:11 | 0 | 11 | [5 empty] | At Khuntuni end: R-N, Zone 1, Dist- 14.34km, Ir- 0.424kA At ICCL end: R-N, Zone 2, Dist- 19.96km, Ir- 5kA
|  | 6.01.25 | 13:13 | 6.01.25 | 18:56 | 5:43 | 0 | 14 | [5 empty] | At Khuntuni end: R-N, Zone 1, Dist- 14.34km, Ir- 0.27kA At ICCL end: R-N, Zone 2, Dist- 20.1km, Ir- 4.976kA
|  | 11.01.25 | 18:08 | 11.01.25 | 18:43 | 0:35 | 0 | 29 | [5 empty] | At Meramundali end: R-N, Zone 1, Ir- 3.85kA, Dist- 24.6km At Dhenkanal end: R-N, Ir- 1.35kA, Zone 1, Dist- 16.65km
|  | 7.02.25 | 12:20 | 7.02.25 | 12:27 | 0:07 | 0 | 7 | [5 empty] | At Khuntuni end: Incoming supply failed from Dhenkanal end
|  | 28.03.25 | 12:30 | 28.03.25 | 12:42 | 0:12 | 0 | 12 | [5 empty] | At Khuntuni end: E/F, Iy- 1.105kA No tripping at Dhenkanal end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
328 | 132kV Dhenkanal-Joranda RTSS |  |  |  |  | 0.11042 | 14 | 28 | [7 empty] | 19.35 | 8760 | 99.83% | 279.93 | 169506
|  | 07.04.24 | 19:44 | 07.04.24 | 19:52 | 0:08 | 0 | 8 | [5 empty] | Zone 1, Dist- 15.65km, Ir-2.438kA
|  | 08.05.24 | 18:39 | 08.05.24 | 18:48 | 0:09 | 0 | 9 | [5 empty] | At Dhenkanal end: Distance Protection,Z-2, Distance=15.66Km, Ia=20.7A, Ib=0A, Ic=2.188KA
|  | 02.06.24 | 22:29 | 02.06.24 | 23:07 | 0:38 | 0 | 38 | [5 empty] | At Dhenkanal end: Distance Protection,Z-2, Distance=20.69Km, Ia=24.03A, Ib=0A, Ic=2.427KA
|  | 17.06.24 | 16:20 | 17.06.24 | 16:35 | 0:15 | 0 | 15 | [5 empty] | At Khajuriakata end: Over Current,Z-2,R-g, Dist-65.5 KM, Ir-1.262 KA
|  | 13.07.24 | 12:56 | 13.07.24 | 13:14 | 0:18 | 0 | 10 | [5 empty] | Supply failure
|  | 31.07.24 | 11:22 | 31.07.24 | 11:29 | 0:07 | 0 | 7 | [5 empty] | At Dhenkanal end: E/F (B-N), Zone 1, Ib- 2.071kA, Dist- 15.23km
|  | 18.08.24 | 04:25 | 18.08.24 | 4:39 | 0:14 | 0 | 14 | [5 empty] | At Dhenkanal end: E/F (R-N), Ir- 2.689kA, Zone 2, Dist- 17km
|  | 11.12.24 | 9:18 | 11.12.24 | 9:21 | 0:03 | 0 | 3 | [5 empty] | Source failure at Dhenkanal end
|  | 11.01.25 | 18:08 | 11.01.25 | 18:34 | 0:26 | 0 | 23 | [5 empty] | At Khuntuni end: Remote End Tripping
|  | 7.02.25 | 12:20 | 7.02.25 | 12:27 | 0:07 | 0 | 7 | [5 empty] | At Khuntuni end: Incoming supply failed from Dhenkanal end
|  | 22.03.25 | 19:18 | 22.03.25 | 19:32 | 0:14 | 0 | 14 | [5 empty] | At Dhenkanal end: Y-N, Iy- 2.193kA, Zone 1, Dist- 4.57km At Meramundali end: Y-N, Iy- 3.01kA, Zone 1, Dist- 37.6km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
329 | 132kV Digapahandi-Chikiti ckt - I |  |  |  |  | 0.045139 | 1 | 5 | [7 empty] | 29.1 | 8760 | 99.99% | 31.525 | 254916
|  | 01.06.24 | 15:11 | 01.06.24 | 16:16 | 1:05 | 1 | 5 | [5 empty] | At Digapahandi end: Earth Fault, DP optd. BCN, ZONE -II, Ia- 102.7A, Ib -155.6A, Ic - 1.429KA, dist- 35.81kmrn
330 | 132kV Digapahandi-Chikiti ckt - II |  |  |  |  | 0.045139 | 1 | 5 | [7 empty] | 29.1 | 8760 | 99.99% | 31.525 | 254916
|  | 01.06.24 | 15:11 | 01.06.24 | 16:16 | 1:05 | 1 | 5 | [5 empty] | At Digapahandi end: Earth Fault,DP optd. BCN, ZONE -II, Ia- 106.2A, Ib -159A, Ic - 1.429KA, dist- 35.83km
331 | 132kV Duburi-BC Mohanty |  |  |  |  | 0.079861 | 13 | 55 | [7 empty] | 11.97 | 8760 | 99.84% | 166.5825 | 104857.2
|  | 07.06.24 | 16:12 | 07.06.24 | 17:22 | 1:10 | 1 | 10 | [5 empty] | At BC Mohanty SW end: Distance Protection, Zone: Z1, Dist: -0.1KM, Ia=0.32KA,Ib=0.35KA, Ic=0.38KA At Duburi GSS end: Zone: Z2, Dist.=7.09KM, Ia=7.04KA,Ib=7.32KA,Ic=0.38KA,Van=34.05KV,Vbn=33.06KV,Vcn=72.22KV
|  | 22.06.24 | 02:39 | 22.06.24 | 2:49 | 0:10 | 0 | 10 | [5 empty] | At BC Mohanty SW end: Over Current,Ia=58.27KA,Ib=53.35KA,Ic=36.36KA,Van=77.99KV, Vbn=78.08KV,Vcn=78.96KV
|  | 12.08.24 | 15:56 | 12.08.24 | 16:31 | 0:35 | 0 | 35 | [5 empty] | At Daitari end: O/C, Ir- 0.113kA, Iy- 0.126kA, Ib- 0.128kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
332 | 132kV BCMohanty-Daitari |  |  |  |  | 0.28125 | 18 | 45 | [7 empty] | 21.224 | 8760 | 99.79% | 397.95 | 185922.24
|  | 16.04.24 | 15:04 | 16.04.24 | 20:01 | 4:57 | 4 | 57 | [5 empty] | At BC Mohanty: Zone 1, Dist- 5.1km, Ir- 6.17kA, Iy- 6.14kA
|  | 07.06.24 | 16:12 | 07.06.24 | 17:25 | 1:13 | 1 | 13 | [5 empty] | At Daitari end: Distance Protection,Zone=Z1, Dist.=14.29KM, Ia=0.33KA,Ib=0.35KA,Ic=0.35KA, Van=14.39KV,Vbn=11.64KV,Vcn=73.61KV
|  | 12.08.24 | 15:56 | 12.08.24 | 16:31 | 0:35 | 0 | 35 | [5 empty] | At Daitari end: O/C, Ir- 0.113kA, Iy- 0.126kA, Ib- 0.128kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
333 | 132kV BCMohanty-Tomka RTSS |  |  |  |  | 0.097222 | 14 | 20 | [7 empty] | 11.46 | 8760 | 99.84% | 164.26 | 100389.6
|  | 16.04.24 | 15:04 | 16.04.24 | 15:35 | 0:31 | 0 | 31 | [5 empty] | Zone 1, Dist- 4.05km, Ir- 5.48kA
|  | 07.06.24 | 16:12 | 07.06.24 | 17:22 | 1:10 | 1 | 10 | [5 empty] | At BC Mohanty SW end: Distance Protection, Zone: Z1, Dist: -0.1KM, Ia=0.32KA,Ib=0.35KA, Ic=0.38KA At Duburi GSS end: Zone: Z2, Dist.=7.09KM, Ia=7.04KA,Ib=7.32KA,Ic=0.38KA,Van=34.05KV,Vbn=33.06KV,Vcn=72.22KV
|  | 12.08.24 | 15:56 | 12.08.24 | 16:31 | 0:35 | 0 | 35 | [5 empty] | At Daitari end: O/C, Ir- 0.113kA, Iy- 0.126kA, Ib- 0.128kA
|  | 2024-10-07 | 17:48 | 2024-10-07 | 17:52 | 0:04 | 0 | 4 | [5 empty] | At BC Mohanty SW end: Over CurrentIa=237.7A,Ic=240.2A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
334 | 132kV Daitari-Bamnipal(Tisco) |  |  |  |  | 0.52083 | 24 | 30 | [7 empty] | 10.227 | 8760 | 99.72% | 250.5615 | 89588.52
|  | 16.04.24 | 15:04 | 16.04.24 | 20:01 | 4:57 | 4 | 57 | [5 empty] | At BC Mohanty: Zone 1, Dist- 5.1km, Ir- 6.17kA, Iy- 6.14kA
|  | 07.06.24 | 16:12 | 07.06.24 | 17:25 | 1:13 | 1 | 13 | [5 empty] | At Daitari end: Distance Protection,Zone=Z1, Dist.=14.29KM, Ia=0.33KA,Ib=0.35KA,Ic=0.35KA, Van=14.39KV,Vbn=11.64KV,Vcn=73.61KV
|  | 12.08.24 | 15:56 | 12.08.24 | 16:31 | 0:35 | 0 | 35 | [5 empty] | At Daitari end: O/C, Ir- 0.113kA, Iy- 0.126kA, Ib- 0.128kA
|  | 12.08.24 | 21:31 | 12.08.24 | 22:07 | 0:36 | 0 | 36 | [5 empty] | At Daitari end: Zone 1, Dist- 1.57km, Ir- 0.04kA, Iy- 0.055kA, Ib- 0.046kA
|  | 2024-10-23 | 09:13 | 2024-10-23 | 9:53 | 0:40 | 0 | 40 | [5 empty] | At Daitari end: LBB Protection, B/U relay details are Ia=12A,Ib=85A, Ic=25A,Van=74.6KV,Vbn=75.1KV,Vcn=61.4KV
|  | 2024-10-27 | 18:36 | 2024-10-27 | 20:52 | 2:16 | 2 | 16 | [5 empty] | At Daitari end: Distance Protection,Over Current, Zone=Z1,Dist.=1.85KM,Ia=0.49KA,Ib=0.48KA,Ic=0.36KA,Van=75.1KV,Vbn=6.04KV At BC Mohanty SW end: Distance ProtectionZone=Z1,Dist.=11.8KM,Ia=0.52KA,Ib=4.93KA,Ic=4.65KA
|  | 22.11.24 | 13:39 | 22.11.24 | 14:07 | 0:28 | 0 | 28 | [5 empty] | At Daitari end: Earth Fault,B/U relay, Ia=94.7A,Ib=79.7A, Ic=118.8A,Van=47.5KV,Vbn=73.3KV,Vcn=73.8KV
|  | 2.12.24 | 17:29 | 2.12.24 | 18:07 | 0:38 | 0 | 38 | [5 empty] | At Daitari end: E/F
|  | 21.12.24 | 03:50 | 21.12.24 | 4:57 | 1:07 | 1 | 7 | [5 empty] | At Daitari end: E/F, Ia=130.3A,Ib=91.1A,Ic=41.5A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
335 | 132kV Duburi-Jajpur Road Ckt-I |  |  |  |  | 0.056944 | 1 | 22 | [7 empty] | 13.2 | 8760 | 99.98% | 18.04 | 115632
|  | 19.05.24 | 07:02 | 19.05.24 | 7:19 | 0:17 | 0 | 17 | [5 empty] | At Duburi end: O/C,Ia=1.71KA,Ib=0.14KA, Ic= 0.31KA
|  | 15.06.24 | 20:39 | 15.06.24 | 21:44 | 1:05 | 1 | 5 | [5 empty] | At Duburi end: Distance Protection, DP RELAY OPERATED, FAULT CURRENT: IA=6.3KA, IB=244A, IC=300A;F. VOLTAGE: VAN=35.81KV,VBN=76.57KV,VCN=76.95KV; F. ZONE-I; FAULT RESISTANCE=597.7mΩ; FAULT LOCATION=6.67KM At Jajpur Road end: DP RELAY OPERATED, FAULT CURRENT: IA=3.02KA, IB=246.9A, IC=295.5A; F. VOLTAGE: VAN=25.49KV, VBN=84.29KV,VCN=68.36KV; F. ZONE-II; FAULT RESISTANCE=4.646Ω; FAULT LOCATION=6.439KM
336 | 132kV Duburi-Jajpur Road Ckt-II |  |  |  |  | 0.084028 | 2 | 1 | [7 empty] | 13.2 | 8760 | 99.98% | 26.62 | 115632
|  | 19.05.24 | 07:02 | 19.05.24 | 7:19 | 0:17 | 0 | 17 | [5 empty] | At Duburi end: O/C,Ia=1.71KA,Ib=0.14KA, Ic= 0.31KA
|  | 07.06.24 | 15:33 | 07.06.24 | 17:17 | 1:44 | 1 | 44 | [5 empty] | At Duburi end: Distance Protection, DP RELAY OPERATED, FAULT CURRENT: IA=114.7A,IB=265.1A,IC=8.86KA;F. VOLTAGE: VAN=73.0KV,VBN=73.57KV,VCN=24.77KV; F. ZONE-I; FAULT RESISTANCE=481.7Ω; FAULT LOCATION=3.18KM At Jajpur Road end: DP RELAY OPERATED, FAULT CURRENT: IA=116.8A, IB=264.0A, IC=1.634KA; F. VOLTAGE: VAN=73.34KV, VBN=72.56KV,VCN=17.13KV; F. ZONE-I; FAULT RESISTANCE=3.74Ω; FAULT LOCATION=8.87KM
337 | 132kV Duburi-Jakhapura RTSS |  |  |  |  | 0.12778 | 3 | 4 | [7 empty] | 12.45 | 8760 | 99.96% | 38.18 | 109062
|  | 07.04.24 | 19:10 | 07.04.24 | 20:14 | 1:04 | 1 | 4 | [5 empty] | Y-N, Zone 1, Dist- 9.115km, Iy- 7.26kA
|  | 07.06.24 | 15:09 | 07.06.24 | 17:09 | 2:00 | 2 | 0 | [5 empty] | At Duburi end: Distance Protection,
338 | 132kV JSWCL- Mesco |  |  |  |  | 0.18125 | 4 | 21 | [7 empty] | 5.464 | 8760 | 99.95% | 23.7684 | 47864.64
|  | 2.12.24 | 17:30 | 2.12.24 | 21:51 | 4:21 | 4 | 21 | [5 empty] | At Duburi end: O/C, Dist- 6km, Ir- 6.72kA
339 | 132kV Duburi-JSWCL |  |  |  |  | 0.18125 | 4 | 21 | [7 empty] | 9.26 | 8760 | 99.95% | 40.281 | 81117.6
|  | 2.12.24 | 17:30 | 2.12.24 | 21:51 | 4:21 | 4 | 21 | [5 empty] | At Duburi end: O/C, Dist- 6km, Ir- 6.72kA
340 | 132kV ICCL-Choudwar |  |  |  |  | 0.83194 | 13 | 37 | [7 empty] | 0.5 | 8760 | 99.84% | 6.8083 | 4380
|  | 03.04.24 | 13:04 | 03.04.24 | 13:13 | 0:09 | 0 | 9 | [5 empty] | At Choudwar end: Zone 1, Ir- 0.501kA, Iy- 0.792kA, Ib- 4.86kA, Dist- 4.537km At Bidanasi end: E/F (Y-N), Zone 1, Dist- 7.44km, Iy- 5.9kA
|  | 19.04.24 | 18:23 | 19.04.24 | 18:50 | 0:27 | 0 | 27 | [5 empty] | At Bidanasi end: Zone 2, Dist- 7.44km, Ir- 1.055kA, Iy- 1.25kA, Ib- 4.97kA At Choudwar end: O/C (R-Y-B), Zone 4, Dist- -0.199km, Ir- 4.985kA, Iy- 1.058KA, Ib- 1.254kA
|  | 28.07.24 | 17:45 | 28.07.24 | 17:53 | 0:08 | 0 | 8 | [5 empty] | At Bidanasi end: O/C, Ir- 3.91kA, Iy- 3.89kA, Ib- 3.87kA
|  | 28.07.24 | 17:45 | 28.07.24 | 18:15 | 18:15 | 0 | 30 | [5 empty] | Supply failure
|  | 12.02.25 | 07:49 | 12.02.25 | 8:48 | 0:59 | 0 | 23 | [5 empty] | At Choudwar end: Over Current, O/C R,Y,B phase, E/F. At ICCL end: No tripping
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
341 | 132kV Jabamayee FAlloys-Duburi |  |  |  |  | 0.032639 | 0 | 42 | [7 empty] | 12 | 8760 | 99.99% | 8.4 | 105120
|  | 05.05.24 | 12:00 | 05.05.24 | 12:22 | 0:22 | 0 | 17 | [5 empty] | At Duburi end: O/C, Ir- 0.58kA, Iy- 0.63kA, Ib- 0.61kA
|  | 02.06.24 | 20:18 | 02.06.24 | 20:43 | 0:25 | 0 | 25 | [5 empty] | At Duburi end: Distance Protection,Distant Protection RelayrnStart Phase - C N,Tripped Phase - A B C, ZONE-1, FAULT LOCATION = 6.289KM, Ia=52.14A,Ib=70.55A, Ic=3.99KA,Van=74.57KV,Vbn=75.96KV, Vcn=31.63KV , Fault Resistance= 1.005 ohm, Relay Trip time =79.96ms
342 | 132kV Jabamayee FAlloys-Sukinda RTSS |  |  |  |  | 0.032639 | 0 | 42 | [7 empty] | 3.87 | 8760 | 99.99% | 2.709 | 33901.2
|  | 05.05.24 | 12:00 | 05.05.24 | 12:22 | 0:22 | 0 | 17 | [5 empty] | At Duburi end: O/C, Ir- 0.58kA, Iy- 0.63kA, Ib- 0.61kA
|  | 02.06.24 | 20:18 | 02.06.24 | 20:43 | 0:25 | 0 | 25 | [5 empty] | At Duburi end: Distance Protection,Distant Protection RelayrnStart Phase - C N,Tripped Phase - A B C, ZONE-1, FAULT LOCATION = 6.289KM, Ia=52.14A,Ib=70.55A, Ic=3.99KA,Van=74.57KV,Vbn=75.96KV, Vcn=31.63KV , Fault Resistance= 1.005 ohm, Relay Trip time =79.96ms
343 | 132kVJajpur Road-Anandpur Ckt-I |  |  |  |  | 0.028472 | 0 | 41 | [7 empty] | 29.6 | 8760 | 99.99% | 20.2267 | 259296
|  | 19.05.24 | 07:02 | 19.05.24 | 07:43 | 0:41 | 0 | 41 | [5 empty] | At Anandapur end:Zone-1, 'R' Pha Ia-1.7KA I
344 | 132kVJajpur Road-Anandpur Ckt-II |  |  |  |  | 0.028472 | 0 | 41 | [7 empty] | 29.6 | 8760 | 99.99% | 20.2267 | 259296
|  | 19.05.24 | 07:02 | 19.05.24 | 07:43 | 0:41 | 0 | 41 | [5 empty] | At Anandapur end:Zone-1, 'R' Pha Ia-1.7KA I
345 | 132kV Bhadrak-Agarpada |  |  |  |  | 0 | 0 | 0 | [7 empty] | 28.07 | 8760 | 100% | 0 | 245893.2
346 | 132kV Agarpada-Anandpur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 41 | 8760 | 100% | 0 | 359160
347 | 132kVJajpur Road-Chandikhol |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.31 | 8760 | 100% | 0 | 300555.6
348 | 132kVJajpur Road-Jajpur Town |  |  |  |  | 0.17917 | 14 | 12 | [7 empty] | 25.05 | 8760 | 99.84% | 355.71 | 219438
|  | 07.06.24 | 15:03 | 07.06.24 | 17:30 | 2:27 | 0 | 21 | [5 empty] | At Jajpur Road end: Remote End Tripping,Started phase Y-N, Tripped phase Y-N, Zone-1, Fault distance=3.34KM, Irn=5.25A, Iyn=6.2KA, Ibn=5.3A, Vyn=76.77 KV, Vyn=19.52KV, Vbn=77.2KV, Fault resistance=472.8 mohm At Jajpur Town end: No tripping
|  | 15.06.24 | 20:47 | 15.06.24 | 21:51 | 1:04 | 1 | 4 | [5 empty] | At Jajpur Road end: DP RELAY OPERATED, FAULT CURRENT: IA=6.14A, IB=5.64KA, IC=5.56A; F. VOLTAGE: VAN=78.43KV, VBN=19.69KV,VCN=80.36KV; F. ZONE-I; FAULT RESISTANCE=2.47Ω; FAULT LOCATION=2.22KM At Jajpur Town end: No tripping
|  | 22.09.24 | 20:38 | 22.09.24 | 20:56 | 0:18 | 0 | 18 | [5 empty] | At Jajpur Road end: Over Current,Ia=471.1 A ,Ib=503.3 A , Ic=518.8 A At Jajpur Town end: Remote End Tripping,Tripped on O/C. Ia=471.1A,Ib=503.3A,Ic=518.8A
|  | 24.09.24 | 16:04 | 24.09.24 | 16:33 | 0:29 | 0 | 29 | [5 empty] | At Jajpur Town end: Remote End Tripping,Started phase B-N, Tripped phase B-N, Zone-1, Dist=17.36KM, Irn=270A, Iyn=357.7A, Ibn=3.5KA, Vrn=77.56 KV, Vyn=78.97KV, Vbn=50.68KV, Fault resistance=1.32 ohm
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
349 | 132kVJajpur Road-RAMCO |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.13 | 8760 | 100% | 0 | 255178.8
350 | 132kV RAMCO- Kendrapara |  |  |  |  | 0.031944 | 0 | 31 | [7 empty] | 41.43 | 8760 | 99.99% | 21.4055 | 362926.8
|  | 29.05.24 | 20:03 | 29.05.24 | 20:17 | 0:14 | 0 | 14 | [5 empty] | At Kendrapara end: Distance Protection,Tripped on DP, Zone-1, B-Phase, Distance=11.3Km, IR=24.6A, IY=54.9A, IB=3.29kA, IN=3.21kA
|  | 18.03.25 | 7:45 | 18.03.25 | 8:17 | 0:32 | 0 | 17 | [5 empty] | At Kendrapara end: Zone 4, Ir- 0.245kA, Ib- 0.179kA No tripping at RAMCO end
351 | 132kV Kuchei PG- Jaleswar |  |  |  |  | 0.22014 | 0 | 36 | [7 empty] | 78.88 | 8760 | 99.99% | 47.328 | 690988.8
|  | 11.09.24 | 11:49 | 11.09.24 | 17:06 | 5:17 | 0 | 36 | [5 empty] | At Jaleswar end: Distance Protection,Z4, Y-B-Gnd, Distance :2.2 KM , Ir-1695.3A, Iy-1662.8A, Ib-1792.1A, Vrn-2.175 KV, Vyn-1.614 KV, Vbn-1.301 KV. At Baripada PG end: No tripping
352 | 132kV Kuchei PG- Bhogarai |  |  |  |  | 0 | 0 | 0 | [7 empty] | 100.91 | 8760 | 100% | 0 | 883971.6
353 | 132kV Jaleswar-Bhogarai |  |  |  |  | 0.18472 | 0 | 36 | [7 empty] | 57.13 | 8760 | 99.99% | 34.278 | 500458.8
|  | 11.09.24 | 11:49 | 11.09.24 | 16:15 | 4:26 | 0 | 36 | [5 empty] | At Bhograi end: DP RELAY OPTD,Z-1, 25KM,Bph-Gnd,Ir-63.2A,Iy-20.1KA,Ib-831.9A At Jaleswar end: DP RELAY OPTD, Z-1, 25KM,Bph-Gnd,Ir-63.2A,Iy-20.1KA,Ib-831.9A
354 | 132kVJaleswar-Jaleswar RTSS |  |  |  |  | 0.058333 | 13 | 24 | [7 empty] | 2.34 | 8760 | 99.85% | 31.356 | 20498.4
|  | 07.04.24 | 20:03 | 07.04.24 | 20:14 | 0:11 | 0 | 11 | [5 empty] | O/C, Ir-0.29kA, Ib-0.29kA
|  | 20.04.24 | 16:55 | 20.04.24 | 17:00 | 0:05 | 0 | 5 | [5 empty] | O/C, Ir-0.29kA, Ib-0.29kA
|  | 11.09.24 | 11:49 | 11.09.24 | 12:20 | 0:31 | 0 | 31 | [5 empty] | At Basta end: Distance Protection,ABCN TRIPPED,ZONE-2,Location-24.61km,IA-2.089KA,IB-2.264KA,IC-2.27KA,Van-23.35KV,Vbn-23.49KV,Vcn-21.36KV.
|  | 12.11.24 | 16:38 | 12.11.24 | 16:43 | 0:05 | 0 | 5 | [5 empty] | At Jaleswar end: Over Current, Ir=290 Amp, Ib=290 Amp.
|  | 11.12.24 | 16:23 | 11.12.24 | 16:28 | 0:05 | 0 | 5 | [5 empty] | O/C
|  | 28.01.25 | 08:36 | 28.01.25 | 8:45 | 0:09 | 0 | 9 | [5 empty] | At Jaleswar end: O/C, If- 0.27kA
|  | 3.02.25 | 08:43 | 3.02.25 | 8:51 | 0:08 | 0 | 8 | [5 empty] | At Jaleswar end: Over Current, Back-Up relay: Over current Ir= Ib=280A
|  | 7.02.25 | 16:34 | 7.02.25 | 16:39 | 0:05 | 0 | 5 | [5 empty] | At Jaleswar end: Over Current, Back-Up relay :- Over current Ir= Ib=290A
|  | 26.03.25 | 14:10 | 26.03.25 | 14:15 | 0:05 | 0 | 5 | [5 empty] | At Jaleswar end: O/C, If- 0.27kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
355 | 132 kV Jaleswar-Basta |  |  |  |  | 0.021528 | 0 | 31 | [7 empty] | 23.41 | 8760 | 99.99% | 12.0952 | 205071.6
|  | 11.09.24 | 11:49 | 11.09.24 | 12:20 | 0:31 | 0 | 31 | [5 empty] | At Basta end: Distance Protection,ABCN TRIPPED,ZONE-2,Location-24.61km,IA-2.089KA,IB-2.264KA,IC-2.27KA,Van-23.35KV,Vbn-23.49KV,Vcn-21.36KV.
356 | 132kVJayanagar-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.87 | 8760 | 100% | 0 | 393061.2
357 | 132kVJayanagar-Jayanagar RTSS |  |  |  |  | 0.68889 | 26 | 52 | [7 empty] | 39.6 | 8760 | 99.69% | 1063.92 | 346896
|  | 06.04.24 | 10:07 | 06.04.24 | 12:02 | 1:55 | 1 | 55 | [5 empty] | B-N, Zone 1, Dist- 5.57km, If- 5.13kA
|  | 18.05.24 | 13:21 | 18.05.24 | 13:30 | 0:09 | 0 | 9 | [5 empty] | At Jayanagar end: Distance Protection,Z1,R-G,DIST-66KM,If-1.18KA,
|  | 18.05.24 | 13:58 | 18.05.24 | 14:14 | 0:16 | 0 | 16 | [5 empty] | At Jayanagar end: Distance Protection,Z1,B-G,DIST-43.27KM,If-1.77KA
|  | 01.06.24 | 16:45 | 01.06.24 | 17:07 | 0:22 | 0 | 22 | [5 empty] | At Jayanagar end: Distance Protection,R-G, zone-1, distance=1.528km, Ir=8.6KA
|  | 15.06.24 | 14:47 | 15.06.24 | 14:59 | 0:12 | 0 | 12 | [5 empty] | At Jayanagar end: Distance Protection,Y-G,zone-1,dist=56.4km,Iy=1.387KA
|  | 2024-10-04 | 18:33 | 2024-10-04 | 19:44 | 1:11 | 1 | 11 | [5 empty] | At Jayanagar end: Y-N, Zone 1, Dist- 6.75km, Iy- 5.97kA
|  | 2024-10-08 | 15:59 | 2024-10-08 | 17:15 | 1:16 | 1 | 16 | [5 empty] | At Jayanagar end: Distance Protection, R-G,Z-1,Dist-35KM,If-2.044KA
|  | 2024-10-19 | 19:46 | 2024-10-20 | 2:04 | 6:18 | 6 | 18 | [5 empty] | At Jayanagar end: Distance ProtectionZ-1,Y-B-G,DIST-4.2KM,If-7.5KA
|  | 2024-10-20 | 14:28 | 2024-10-20 | 14:48 | 0:20 | 0 | 20 | [5 empty] | At Jayanagar end: Distance ProtectionZ-1,Y-B-G,DIST-74.14KM,If-1.87KA
|  | 2024-10-29 | 17:12 | 2024-10-29 | 17:20 | 0:08 | 0 | 8 | [5 empty] | At Jayanagar end: Distance ProtectionZ-1,Y-G,If-6.29KA,Dist-6.7KM
|  | 24.03.25 | 02:38 | 24.03.25 | 7:03 | 4:25 | 2 | 45 | [5 empty] | At Jayanagar end: Y-Phase jumper from 132kV Main bus to Single Isolator is snapped.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
358 | 132kV Jayanagar-Podagada |  |  |  |  | 0.74653 | 15 | 10 | [7 empty] | 38.0419 | 8760 | 99.83% | 576.9688 | 333247.044
|  | 08.04.24 | 16:20 | 08.04.24 | 16:48 | 0:28 | 0 | 28 | [5 empty] | Machkund supply failed at Machkund end.
|  | 24.04.24 | 07:11 | 24.04.24 | 07:56 | 0:45 | 0 | 20 | [5 empty] | Machkund supply failed at Machkund end.
|  | 20.04.24 | 13:24 | 20.04.24 | 14:21 | 0:57 | 0 | 57 | [5 empty] | Remote end Tripping. Machkund supply failed at Machkund end.
|  | 05.05.24 | 21:44 | 05.05.24 | 21:55 | 0:11 | 0 | 11 | [5 empty] | Machkund supply failure
|  | 06.05.24 | 14:04 | 06.05.24 | 16:08 | 2:04 | 0 | 13 | [5 empty] | Machkund supply failure
|  | 16.05.24 | 05:37 | 16.05.24 | 07:20 | 1:43 | 0 | 14 | [5 empty] | At Podagada end: Remote End Tripping,Machkund feeder tripped at Machkund end.
|  | 18.05.24 | 19:33 | 19.05.24 | 6:43 | 11:10 | 0 | 10 | [5 empty] | Machkund supply failure
|  | 23.06.24 | 11:13 | 23.06.24 | 11:19 | 0:06 | 0 | 6 | [5 empty] | At Jayanagar end: Over Current, Ir=299.3A, Iy=305.7A, Ib=313.6A , In=9.68A
|  | 08.07.24 | 15:32 | 08.07.24 | 15:59 | 0:27 | 0 | 27 | [5 empty] | At Podagada end: R-Y-B, Zone 1, Dist-20.8km, Ir= 0.18kA, Iy= 0.20kA, Ib= 0.17kA At Jayanagar end: R-Y, Zone 1, Dist-7.7km, Ir= 1.6kA, Iy= 1.45kA
|  | 03.09.24 | 12:20 | 03.09.24 | 12:24 | 0:04 | 0 | 4 | [5 empty] | At Jayanagar end: Y-N, Zone 1, Dist- 8.77km, Iy- 0.97kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
359 | 132kV Podagada-Rayagada |  |  |  |  | 1899-12-31 03:28 | 20 | 43 | [7 empty] | 72.1572 | 8760 | 99.76% | 1494.8567 | 632097.072
|  | 24.04.24 | 07:11 | 24.04.24 | 8:12 | 1:01 | 0 | 21 | [5 empty] | Machhkund supply failure
|  | 25.04.24 | 8:21 | 25.04.24 | 8:33 | 0:12 | 0 | 12 | [5 empty] | Machhkund supply failure
|  | 26.04.24 | 13:20 | 26.04.24 | 13:27 | 0:07 | 0 | 7 | [5 empty] | At Podagada end: R-N, Zone 1, Dist- 82.3km, Ir- 0.71kA At Rayagada end: E/F (R-N), Zone 1, Dist- 82.3km, Ir- 0.71kA
|  | 26.04.24 | 17:20 | 26.04.24 | 17:29 | 0:09 | 0 | 5 | [5 empty] | At Rayagada end: Zone 1, Dist- 25.43km, Ir- 0.193kA, Iy- 0.158kA, Ib- 0.264kA At Podagada end: R-N, Zone 1, Dist- 53.7km, Ir- 0.95kA
|  | 29.04.24 | 13:43 | 29.04.24 | 13:49 | 0:06 | 0 | 3 | [5 empty] | At Podagada end: R-Y-B, Zone 2, Dist- 70.9km, Ir- 0.82kA, Iy- 0.81kA, Ib- 0.77kA
|  | 29.04.24 | 13:51 | 29.04.24 | 14:52 | 1:01 | 0 | 25 | [5 empty] | At Rayagada end: Y-B, Zone 1, Dist- 41.84km, Ir- 0.218kA, Iy- 0.181kA, Ib- 0.174kA
|  | 05.05.24 | 21:44 | 05.05.24 | 21:55 | 0:11 | 0 | 11 | [5 empty] | Machkund supply failure
|  | 06.05.24 | 14:04 | 06.05.24 | 16:08 | 2:04 | 0 | 13 | [5 empty] | Machkund supply failure
|  | 14.05.24 | 17:39 | 14.05.24 | 17:46 | 0:07 | 0 | 7 | [5 empty] | At Podagada end: Distance Protection,PU Time= 440ms, Trip Time= 360ms, Zone-2, dISTANCE= 81.2KM, IL1= 0.75kA, IL2= 0.02kA, IL3=0.02kA.
|  | 16.05.24 | 05:37 | 16.05.24 | 07:20 | 1:43 | 0 | 14 | [5 empty] | At Podagada end: Remote End Tripping,Machkund feeder tripped at Machkund end.
|  | 18.05.24 | 13:21 | 18.05.24 | 13:35 | 0:14 | 0 | 8 | [5 empty] | At Podagada end: Distance Protection,PU Time= 60ms, Trip Time= 0, Dist. loop= L1-L2, IL1= 1.16kA, IL2= 1.16kA, IL3= 0.01kA, Dist= 3.2KM, Zone-1
|  | 18.05.24 | 13:29 | 18.05.24 | 15:06 | 1:37 | 0 | 14 | [5 empty] | At Podagada end: Distance Protection,PU Time= 50ms, Trip Time= 0, Dist. loop= L1-L2, IL1= 1.16kA, IL2= 1.16kA, IL3= 0.07kA, Dist= 2.8 KM, Zone-1. (After rain & thunder stopped, the said feeder charged)
|  | 18.05.24 | 19:33 | 19.05.24 | 6:43 | 11:10 | 0 | 10 | [5 empty] | Machkund supply failure
|  | 26.05.24 | 15:05 | 26.05.24 | 15:17 | 0:12 | 0 | 8 | [5 empty] | At Podagada end: Remote End Tripping,No trippings at Podagada end.
|  | 13.05.24 | 17:59 | 13.05.24 | 18:13 | 0:14 | 0 | 14 | [5 empty] | At Rayagada end: Remote End Tripping,Machkund Power supply fail from Machkund P.H end.
|  | 04.06.24 | 15:58 | 04.06.24 | 17:33 | 1:35 | 0 | 13 | [5 empty] | Machhkund supply failure
|  | 05.06.24 | 11:56 | 05.06.24 | 12:04 | 0:08 | 0 | 8 | [5 empty] | At Rayagada end: Zone 1, Dist- 19.01km, Ir- 0.23kA, Iy- 0.177kA, Ib- 0.284kA At Podagada end: R-N, Zone 1, Dist- 81.3km, Ir- 0.72kA
|  | 06.06.24 | 18:03 | 06.06.24 | 18:18 | 0:15 | 0 | 15 | [5 empty] | Machhkund supply failure
|  | 06.06.24 | 18:34 | 06.06.24 | 18:45 | 0:11 | 0 | 10 | [5 empty] | At Rayagada end:Earth Fault,132kV rayagada Buscoupler Feeder tripped on E/F relay indication. P141 back up relay operated, Ia=324.6 A, Ib=282 A, Ic=186.2 A, In=788.9 A
|  | 08.07.24 | 15:32 | 08.07.24 | 16:05 | 0:33 | 0 | 27 | [5 empty] | At Podagada end: B-Ph, Zone 1, Dist- 57.5km, Ir= 0.03kA, Iy= 0.14kA, Ib= 0.92kA
|  | 16.07.24 | 13:03 | 16.07.24 | 13:23 | 0:20 | 0 | 20 | [5 empty] | Machkund supply failure
|  | 20.07.24 | 08:49 | 20.07.24 | 9:18 | 0:29 | 0 | 29 | [5 empty] | Machkund supply failure
|  | 28.08.24 | 14:44 | 28.08.24 | 14:52 | 0:08 | 0 | 8 | [5 empty] | At Podagada end: Dist Protection,Dist- 55.4 km, Y-Ph fault, IL1= 0.34kA, IL2= 0.95kA, IL3= 0.15kA
|  | 03.09.24 | 12:20 | 03.09.24 | 12:25 | 0:05 | 0 | 5 | [5 empty] | At Rayagada end: Remote End Tripping
|  | 09.09.24 | 10:34 | 09.09.24 | 10:45 | 0:11 | 0 | 11 | [5 empty] | At Rayagada end: Remote End Tripping,MACHAKUND P.H POWER SUPPLY FAIL
|  | 14.09.24 | 10:56 | 14.09.24 | 11:15 | 0:19 | 0 | 19 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 20.09.24 | 17:03 | 20.09.24 | 17:36 | 0:33 | 0 | 33 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 22.09.24 | 17:56 | 22.09.24 | 18:14 | 0:18 | 0 | 18 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 28.09.24 | 11:36 | 28.09.24 | 11:43 | 0:07 | 0 | 7 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 29.09.24 | 01:50 | 29.09.24 | 1:58 | 0:08 | 0 | 8 | [5 empty] | At Rayagada end: Remote End Tripping,132KV Machkund Power supply fail from Machkund P.H.
|  | 2024-10-12 | 17:11 | 2024-10-12 | 17:25 | 0:14 | 0 | 14 | [5 empty] | Supply failure from Machkund
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 20 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 8 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 27 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 22 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
|  | 14.11.24 | 10:47 | 14.11.24 | 11:16 | 0:29 | 0 | 29 | [5 empty] | Machkund supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
360 | 132kV Podagada-Pottangi |  |  |  |  | 0.52431 | 13 | 48 | [7 empty] | 52 | 8760 | 99.84% | 717.6 | 455520
|  | 08.04.24 | 16:20 | 08.04.24 | 16:48 | 0:28 | 0 | 28 | [5 empty] | Machkund supply failed at Machkund end.
|  | 24.04.24 | 07:11 | 24.04.24 | 18:13 | 11:02 | 0 | 21 | [5 empty] | Machkund supply failed at Machkund end.
|  | 04.06.24 | 15:58 | 04.06.24 | 16:18 | 0:20 | 0 | 20 | [5 empty] | Machhkund supply failure
|  | 08.07.24 | 15:32 | 08.07.24 | 16:05 | 0:33 | 0 | 27 | [5 empty] | At Podagada end: B-Ph, Zone 1, Dist- 57.5km, Ir= 0.03kA, Iy= 0.14kA, Ib= 0.92kA
|  | 27.11.24 | 18:54 | 27.11.24 | 19:06 | 0:12 | 0 | 12 | [5 empty] | At Potangi end: Remote End Tripping,Source failure at Podagada end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
361 | 132kVJayanagar-Tentulikhunti |  |  |  |  | 0.05 | 1 | 12 | [7 empty] | 55.6 | 8760 | 99.99% | 66.72 | 487056
|  | 09.05.24 | 05:46 | 09.05.24 | 06:06 | 0:20 | 0 | 20 | [5 empty] | At Tentulikhunti end: Earth Fault,R&B-phase to Earth Fault, (Ir = 1.68KA, Ib=1.78KA)
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 52 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
362 | 132kVJayanagar-Borigumma |  |  |  |  | 0.046528 | 0 | 30 | [7 empty] | 39.3 | 8760 | 99.99% | 19.65 | 344268
|  | 19.04.24 | 12:30 | 19.04.24 | 12:45 | 0:15 | 0 | 15 | [5 empty] | At Jayanagar end: Zone 1, B-N, Dist- 9.28km, Ib- 0.787kA
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 15 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
363 | 132kV Borigumma-Nabarangpur |  |  |  |  | 0.045833 | 0 | 29 | [7 empty] | 66 | 8760 | 99.99% | 31.9 | 578160
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 15 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
364 | 132kV Nabarangpur-Tentulikhunti |  |  |  |  | 0.091667 | 13 | 31 | [7 empty] | 26.4 | 8760 | 99.85% | 356.84 | 231264
|  | 09.05.24 | 05:46 | 09.05.24 | 06:10 | 0:24 | 0 | 20 | [5 empty] | At Tentulikhunti end: R-B Ph, Zone 2, Ir- 0.823kA, Ib- 0.792kA
|  | 01.06.24 | 15:30 | 01.06.24 | 16:12 | 0:42 | 0 | 42 | [5 empty] | At Nabarangpur end: Distance Protection OPTD R - ph, Zone- 1, Ia=1.66KA, Ib-141A,Ic-56A,Fault distance=10.68 km, At Tentulikhunti end: Distance protection OPTD, Ia= 1.776KA, Ib=104A, Ic= 26A, Fault Distance-8.99km
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 15 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
365 | 132kVJharsuguda-Jharsuguda RTSS |  |  |  |  | 0.068056 | 13 | 38 | [7 empty] | 0.15 | 8760 | 99.84% | 2.045 | 1314
|  | 06.04.24 | 07:55 | 06.04.24 | 08:19 | 0:24 | 0 | 24 | [5 empty] | O/C, Ir- 1.402kA, Iy- 1.404kA
|  | 05.06.24 | 04:11 | 05.06.24 | 5:12 | 1:01 | 1 | 1 | [5 empty] | At Lapanga end: R-N, Zone 1, Dist- 10.6km, Ir- 8.7kA
|  | 26.09.24 | 18:17 | 26.09.24 | 18:30 | 0:13 | 0 | 13 | [5 empty] | Fault type Rph- G Fault Duration: 56.67ms Ia= 1.939 KA Ib= 1.394 KA MiCOM, 86A, 86B Tripped
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
366 | 132kVJharsuguda-Ultratech |  |  |  |  | 0.042361 | 1 | 1 | [7 empty] | 31 | 8760 | 99.99% | 31.5167 | 271560
|  | 05.06.24 | 04:11 | 05.06.24 | 5:12 | 1:01 | 1 | 1 | [5 empty] | At Lapanga end: R-N, Zone 1, Dist- 10.6km, Ir- 8.7kA
|  | 04.09.24 | 14:01 | 04.09.24 | 17:14 | 3:13 | 3 | 13 | [5 empty] | At Jharsuguda end: Zone 1, Dist- 5.73km, Iy- 7.333kA At Ultratech end: No tripping
367 | 132kV Joda- Bansapani RTSS |  |  |  |  | 0.04375 | 13 | 3 | [7 empty] | 2.99 | 8760 | 99.85% | 39.0195 | 26192.4
|  | 18.04.24 | 01:30 | 18.04.24 | 01:33 | 0:03 | 0 | 3 | [5 empty] | At Joda end: O/C, If- 0.27kA
|  | 14.04.24 | 17:21 | 14.04.24 | 17:27 | 0:06 | 0 | 6 | [5 empty] | At Joda end: Dir O/C, If- 0.27kA
|  | 21.04.24 | 09:47 | 21.04.24 | 09:51 | 0:04 | 0 | 4 | [5 empty] | O/C, If- 0.26kA
|  | 23.04.24 | 07:39 | 23.04.24 | 07:45 | 0:06 | 0 | 6 | [5 empty] | At Joda end: O/C, If- 0.27kA
|  | 24.04.24 | 17:35 | 24.04.24 | 17:39 | 0:04 | 0 | 4 | [5 empty] | At Joda end: Dir. O/C, If- 0.26kA
|  | 30.04.24 | 07:34 | 30.04.24 | 07:36 | 0:02 | 0 | 2 | [5 empty] | Dir O/C, If- 0.26kA
|  | 04.05.24 | 00:47 | 04.05.24 | 00:51 | 0:04 | 0 | 4 | [5 empty] | At Joda end: O/C, If- 0.27kA
|  | 08.05.24 | 04:16 | 08.05.24 | 04:20 | 0:04 | 0 | 4 | [5 empty] | At Joda end: O/C, If- 0.27kA
|  | 26.05.24 | 19:49 | 26.05.24 | 19:53 | 0:04 | 0 | 4 | [5 empty] | At Joda end: O/C,Tripped at Joda end only, B/U relay: Dir.O/C tripped,Fault Current: IL1=0.26KA,IL2=0.26KA
|  | 31.05.24 | 13:53 | 31.05.24 | 14:05 | 0:12 | 0 | 12 | [5 empty] | At Joda end: O/C,132kV Banspani RTSS feeder tripped on O/C with following relay indication, Ia=0.28KA, Ib=0.28KA
|  | 31.05.24 | 14:52 | 31.05.24 | 14:55 | 0:03 | 0 | 3 | [5 empty] | At Joda end: O/C,132kV Banspani RTSS feeder tripped on O/C with following relay indicationtIa=0.26KAtIb=0.26KA
|  | 04.06.24 | 04:16 | 04.06.24 | 4:20 | 0:04 | 0 | 4 | [5 empty] | At Joda end: Over Current,Tripped at Joda end only with following relay indication Relay at Joda end: B/U relay: Dir.O/C tripped,Fault Current: IL1=0.27KA,IL2=0.27KA
|  | 06.06.24 | 15:38 | 06.06.24 | 15:42 | 0:04 | 0 | 4 | [5 empty] | At Joda end: Over Current,Tripped at Joda end only with following relay indication Relay at Joda end: B/U relay: Dir.O/C tripped,Fault Current: IL1=0.27KA,IL2=0.27KA
|  | 16.06.24 | 18:17 | 16.06.24 | 18:20 | 0:03 | 0 | 3 | [5 empty] | At Joda end: Over Current,Relay at Joda end: B/U relay: Dir.O/C tripped,Fault Current: IL1=0.26KA,IL2=0.26KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
368 | 132kV Joda-FAP |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.03 | 8760 | 100% | 0 | 9022.8
369 | 132kV Joda-Kenduposi |  |  |  |  | 0.44653 | 0 | 59 | [7 empty] | 49.42 | 8760 | 99.99% | 48.5963 | 432919.2
|  | 12.05.24 | 17:04 | 12.05.24 | 17:46 | 0:42 | 0 | 35 | [5 empty] | At Joda end: Earth Fault,At Joda endDP-IZONE-IFAULTY PHASE-ANDISTANCE-13.30KM,Ia-3825AIb-100.6AIc-153.6A At Kenduposi end: DISTANCE-59.4KMIa-140AIb-130AIc-160A
|  | 20.06.24 | 22:46 | 21.06.24 | 8:47 | 10:01 | 0 | 24 | [5 empty] | At Joda end: Distance Protection, DP relay Main:Tripped phase- BN, Fault Current :Ia- 389A ,Ib-1525A,Ic-288.4A At Kenduposi end: DP Main:Tripped phase- BN, Fault Current :Ia- 360A ,Ib-430A,Ic-280A
370 | 132kV Joda-Palasponga |  |  |  |  | 1899-12-31 04:13 | 17 | 22 | [7 empty] | 41.6 | 8760 | 99.8% | 722.4533 | 364416
|  | 09.04.24 | 14:50 | 09.04.24 | 14:53 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.506kA, Iy- 0.409kA, Ib- 0.348kA
|  | 13.04.24 | 17:55 | 13.04.24 | 17:58 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.525kA, Iy- 0.414kA, Ib- 0.33kA
|  | 20.04.24 | 23:03 | 20.04.24 | 23:07 | 0:04 | 0 | 4 | [5 empty] | O/C, Zone 1, Ir- 0.501kA, Iy- 0.433kA, Ib- 0.317kA
|  | 11.05.24 | 22:18 | 11.05.24 | 22:34 | 0:16 | 0 | 16 | [5 empty] | At Palasponga end: Distance Protection,ER, IA=256A,IB=287A,IC=1244A,IG=878A At Joda end: Earth Fault,132kV Joda-Palasponga feeder tripped at Both End. Relay at Palasponga end:- Fault CurrentIa-256AIb-287AIc-1244AIg-878A Relay at Joda end:-DP Operate.B-PH faultDist- 1KM Fault Current :-Ia-213.8AIb-186.83AIc-703A
|  | 12.05.24 | 17:04 | 12.05.24 | 17:38 | 0:34 | 0 | 34 | [5 empty] | At Joda end: Earth Fault, DP-I , ZONE-1, FAULT LOOP-YN, DISTANCE-5.3954KM Ia=215.01A, Ib=7045A, Ic=228.11A At Palasponga end: DP-I ZONE-I EVENT-BGT DISTANCE-33.39KM Ia=247A Ib=403A Ic=240A
|  | 31.05.24 | 14:48 | 31.05.24 | 14:51 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: O/C, IA=537.3A, IB=472.9A, IC=346.1A, IN=0.05A,IG=3.22A
|  | 03.06.24 | 12:54 | 03.06.24 | 12:57 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=508.6A,IB=416.8A,IC=342.1A, ,IG=3.42A
|  | 02.06.24 | 18:48 | 02.06.24 | 19:05 | 0:17 | 0 | 17 | [5 empty] | At Joda end:Earth Fault, IL1=.35KArnIL2=.72KArnIL3=.32KA At Polasponga end: Remote End Tripping,IL1=0.35KA,IL2=0.72KA,IL3=0.32KA
|  | 06.06.24 | 21:10 | 06.06.24 | 21:12 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end:Over Current,AB T,IA=524.1A,IB=442.9A,IC=353.9A, IG=3.52A
|  | 09.06.24 | 15:01 | 09.06.24 | 15:08 | 0:07 | 0 | 7 | [5 empty] | At Polasponga end:Over Current,IA=490A,IB=422.4A,IC=373.3A, IG=2.15A
|  | 15.06.24 | 14:57 | 15.06.24 | 15:00 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=484.8A,IB=410.7A,IC=298.9A,IG=5.12A
|  | 16.06.24 | 16:01 | 16.06.24 | 16:04 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=527.9A,IB=446.7A,IC=359.6A,IG=4.83A
|  | 17.06.24 | 17:53 | 17.06.24 | 17:56 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=530A,IB=447A,IC=386A,IG=8.0A
|  | 20.06.24 | 23:27 | 20.06.24 | 23:51 | 0:24 | 0 | 24 | [5 empty] | At Joda end: Distance Protection,Relay at Joda end: DP relay Main: Zone -01 ,Dist-8.5364Km, Ia=4767.75A, Ib=231.52A, Ic=249.14A At Polasponga end: Distance Protection,AG T,Z-1,D=30.37KM,IA=407A, IB=238A,IC=270A, IG=526A
|  | 24.06.24 | 04:24 | 24.06.24 | 4:54 | 0:30 | 0 | 30 | [5 empty] | At Polasponga end: Over Current,IA=503.3A, IB=411.4A,IC=375.6A,IG=5.34A
|  | 14.07.24 | 19:50 | 14.07.24 | 20:00 | 0:10 | 0 | 10 | [5 empty] | At Polasponga end: O/C, Ir- 0.288kA, Iy- 0.724kA, Ib- 0.287kA At Joda end: Ir- 0.29kA, Iy- 0.72kA, Ib- 0.3kA
|  | 17.07.24 | 01:31 | 17.07.24 | 7:16 | 5:45 | 0 | 36 | [5 empty] | B-Phase CT Jumper burnt out at Polasponga end (open Circuited) no touch to Ground.
|  | 21.07.24 | 17:39 | 22.07.24 | 11:47 | 18:08 | 0 | 26 | [5 empty] | At Polasponga end: O/C, Dist- 51.7km, Ir- 0.329kA, Iy- 0.284kA, Ib- 0.334kA At Joda end: Y-B, Dist- 3.648km, Ir- 0.3kA, Iy- 8.533kA, Ib- 7.453kA
|  | 17.08.24 | 11:27 | 17.08.24 | 11:52 | 0:25 | 0 | 25 | [5 empty] | At Joda end: B-N, Ib- 9.154kA
|  | 10.09.24 | 04:26 | 10.09.24 | 4:52 | 0:26 | 0 | 26 | [5 empty] | At Palasponga end: Over Current,IA=97.0A,IB=1115.6A,IC=1021.6A,IN=0A, IG=5.95A
|  | 2024-10-30 | 22:04 | 2024-10-30 | 22:16 | 0:12 | 0 | 12 | [5 empty] | At Polasponga end: Distance Protection, BGT, Distance=11.29KM, Zone-I, IA=326A, IB=570A,IC=252A, IN=0A,IG=754A At Joda end: DP relay : Tripped phase : YN, Zone 1, Dist:31.06Km, Fault Current :Ia-318.63A ,Ib-2806A, Ic-235.26A | Polasponga, OSISL, Patnaik Steel ESIL | 00:12 00:13 | - | -
|  | 21.03.25 | 17:48 | 21.03.25 | 18:20 | 0:32 | 0 | 32 | [5 empty] | At Polasponga end: Y-N, Dist- 32.22km, Iy- 0.569kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
371 | 132kV Palasponga- Keonjhargarh RTSS |  |  |  |  | 1899-12-31 09:43 | 22 | 52 | [7 empty] | 19.43 | 8760 | 99.74% | 444.2993 | 170206.8
|  | 09.04.24 | 14:50 | 09.04.24 | 14:53 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.506kA, Iy- 0.409kA, Ib- 0.348kA
|  | 13.04.24 | 17:55 | 13.04.24 | 17:58 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.3kA, Iy- 0.243kA, Ib- 0.065kA
|  | 18.04.24 | 01:22 | 18.04.24 | 01:36 | 0:14 | 0 | 14 | [5 empty] | O/C, Ir- 0.298kA, Iy- 0.214kA, Ib- 0.092kA
|  | 20.04.24 | 23:03 | 20.04.24 | 23:07 | 0:04 | 0 | 4 | [5 empty] | O/C, Zone 1, Ir- 0.501kA, Iy- 0.433kA, Ib- 0.317kA
|  | 21.04.24 | 17:15 | 21.04.24 | 17:17 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.3kA, Iy- 0.27kA
|  | 23.04.24 | 03:31 | 23.04.24 | 03:33 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.3kA, Iy- 0.213kA
|  | 23.04.24 | 07:32 | 23.04.24 | 07:34 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.299kA, Iy- 0.252kA
|  | 29.04.24 | 13:40 | 29.04.24 | 13:42 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.02kA, Iy- 0.245kA, Ib- 0.064kA
|  | 02.05.24 | 10:49 | 02.05.24 | 10:51 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, Ir- 0.301kA, Iy- 0.27kA
|  | 03.05.24 | 17:19 | 03.05.24 | 17:21 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, Ir- 0.308Ka, Iy- 0.253kA, Ib- 0.019kA
|  | 04.05.24 | 11:52 | 04.05.24 | 11:54 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, Ir- 0.301kA, Iy- 0.208kA
|  | 07.05.24 | 10:33 | 07.05.24 | 10:35 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, Ir- 0.301kA, Iy- 0.235kA, Ib- 0.091kA
|  | 10.05.24 | 22:28 | 10.05.24 | 22:30 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, IA=300.0A, IB=222.1A, IC=89.6A,INM=7.25A, IND=5.69A
|  | 17.05.24 | 12:40 | 17.05.24 | 12:44 | 0:04 | 0 | 4 | [5 empty] | At Palasponga end: O/C,IA=300.1A,IB=214.2A,IC=102.7A, INM=6.1A,IND=3.98A
|  | 17.05.24 | 15:46 | 17.05.24 | 15:48 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C,IA=300.4A, IB=263.4A, IC=41.75A, INM=6.27A, IND=3.999A
|  | 27.05.24 | 11:30 | 27.05.24 | 11:32 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C,IA=301.5A,IB=277.5A,IC=31.80A, INM=6.307A,IND=3.73A
|  | 11.05.24 | 22:18 | 11.05.24 | 22:34 | 0:16 | 0 | 16 | [5 empty] | At Palasponga end: Distance Protection,ER, IA=256A,IB=287A,IC=1244A,IG=878A At Joda end: Earth Fault,132kV Joda-Palasponga feeder tripped at Both End. Relay at Palasponga end:- Fault CurrentIa-256AIb-287AIc-1244AIg-878A Relay at Joda end:-DP Operate.B-PH faultDist- 1KM Fault Current :-Ia-213.8AIb-186.83AIc-703A
|  | 12.05.24 | 17:04 | 12.05.24 | 17:38 | 0:34 | 0 | 34 | [5 empty] | At Joda end: Earth Fault, DP-I , ZONE-1, FAULT LOOP-YN, DISTANCE-5.3954KM Ia=215.01A, Ib=7045A, Ic=228.11A At Palasponga end: DP-I ZONE-I EVENT-BGT DISTANCE-33.39KM Ia=247A Ib=403A Ic=240A
|  | 31.05.24 | 14:48 | 31.05.24 | 14:51 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: O/C, IA=537.3A, IB=472.9A, IC=346.1A, IN=0.05A,IG=3.22A
|  | 02.06.24 | 13:52 | 02.06.24 | 13:53 | 0:01 | 0 | 1 | [5 empty] | At Polasponga end: Over Current,IA=305A,IB=295A,IC=28.65A
|  | 06.06.24 | 00:18 | 06.06.24 | 0:22 | 0:04 | 0 | 4 | [5 empty] | At Polasponga end: Over Current,IA=306A,IB=229.7A,IC=88.9A, INM=6.9A,IND=7.399A
|  | 07.06.24 | 03:58 | 07.06.24 | 4:01 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end:Over Current,IA=300.5A,IB=224.1A,IC=85.32A, INM=6.99,IND=6.166A
|  | 08.06.24 | 15:36 | 08.06.24 | 15:38 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: Over Current, IA=299A, IB=299A, IC=13.1A, INM=6.7,IND=5.69A
|  | 23.06.24 | 16:52 | 23.06.24 | 16:55 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,IA=300.6A,IB=224A,IC=92.23A,INM=7.107A,IND=6.66A
|  | 24.06.24 | 23:40 | 24.06.24 | 23:43 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,IA=299.9A, IB=224.0A,IC=90.66A,INM=6.708A,IND=5.404A
|  | 28.06.24 | 12:16 | 28.06.24 | 12:18 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: Over Current,IA=300A, IB=279.9A, IC=36.07A, INM=7.059A,IND=6.8A
|  | 28.06.24 | 12:19 | 28.06.24 | 12:21 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: Over Current,IA=300.3A, IB=271.4A, IC=36.07A, INM=7.059A,IND=6.8A
|  | 03.06.24 | 12:54 | 03.06.24 | 12:57 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=508.6A,IB=416.8A,IC=342.1A, ,IG=3.42A
|  | 02.06.24 | 18:48 | 02.06.24 | 19:05 | 0:17 | 0 | 17 | [5 empty] | At Joda end:Earth Fault, IL1=.35KArnIL2=.72KArnIL3=.32KA At Polasponga end: Remote End Tripping,IL1=0.35KA,IL2=0.72KA,IL3=0.32KA
|  | 09.06.24 | 15:01 | 09.06.24 | 15:08 | 0:07 | 0 | 7 | [5 empty] | At Polasponga end:Over Current,IA=490A,IB=422.4A,IC=373.3A, IG=2.15A
|  | 15.06.24 | 14:57 | 15.06.24 | 15:00 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=484.8A,IB=410.7A,IC=298.9A,IG=5.12A
|  | 16.06.24 | 16:01 | 16.06.24 | 16:04 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=527.9A,IB=446.7A,IC=359.6A,IG=4.83A
|  | 17.06.24 | 17:53 | 17.06.24 | 17:56 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=530A,IB=447A,IC=386A,IG=8.0A
|  | 20.06.24 | 23:27 | 20.06.24 | 23:51 | 0:24 | 0 | 24 | [5 empty] | At Joda end: Distance Protection,Relay at Joda end: DP relay Main: Zone -01 ,Dist-8.5364Km, Ia=4767.75A, Ib=231.52A, Ic=249.14A At Polasponga end: Distance Protection,AG T,Z-1,D=30.37KM,IA=407A, IB=238A,IC=270A, IG=526A
|  | 24.06.24 | 04:24 | 24.06.24 | 4:54 | 0:30 | 0 | 30 | [5 empty] | At Polasponga end: Over Current,IA=503.3A, IB=411.4A,IC=375.6A,IG=5.34A
|  | 02.07.24 | 05:05 | 02.07.24 | 5:08 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current, IA=299.9A, IB=235.8A, IC=97.09A
|  | 03.07.24 | 11:14 | 03.07.24 | 11:17 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 07.07.24 | 13:29 | 07.07.24 | 13:30 | 0:01 | 0 | 1 | [5 empty] | At Polasponga end: Over Current,IA=300.9A, IB=275.0A, IC=35.37A
|  | 10.07.24 | 18:07 | 10.07.24 | 18:10 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,IA=299.7A, IB=269.5A, IC=34.57A
|  | 16.07.24 | 13:27 | 16.07.24 | 13:30 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.22kA
|  | 21.07.24 | 13:29 | 21.07.24 | 13:31 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C
|  | 26.07.24 | 09:07 | 26.07.24 | 9:08 | 0:01 | 0 | 1 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.245kA
|  | 14.07.24 | 19:50 | 14.07.24 | 20:00 | 0:10 | 0 | 10 | [5 empty] | At Polasponga end: O/C, Ir- 0.288kA, Iy- 0.724kA, Ib- 0.287kA At Joda end: Ir- 0.29kA, Iy- 0.72kA, Ib- 0.3kA
|  | 17.07.24 | 01:31 | 17.07.24 | 7:16 | 5:45 | 0 | 36 | [5 empty] | B-Phase CT Jumper burnt out at Polasponga end (open Circuited) no touch to Ground.
|  | 21.07.24 | 17:39 | 22.07.24 | 11:47 | 18:08 | 0 | 26 | [5 empty] | At Polasponga end: O/C, Dist- 51.7km, Ir- 0.329kA, Iy- 0.284kA, Ib- 0.334kA At Joda end: Y-B, Dist- 3.648km, Ir- 0.3kA, Iy- 8.533kA, Ib- 7.453kA
|  | 02.08.24 | 18:25 | 02.08.24 | 18:27 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C, Ir- 302.6A, Iy- 257.1A, Ib- 57.60A
|  | 20.08.24 | 06:17 | 20.08.24 | 6:20 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: O/C,IA=300.3A,Ib-288.8A,IC=18.63A,INM=6.33A,IND=7.01A
|  | 22.08.24 | 16:36 | 22.08.24 | 16:38 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C,IL1=299.7A,IL2=274.3A,IL3=36.29A,INM=6.92A,IND=4.57A
|  | 23.08.24 | 09:05 | 23.08.24 | 9:07 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: O/C,IA=299.9A,Ib-239.5A,IC=74.42A,INM=6.618A,IND=6.9A
|  | 24.08.24 | 07:58 | 24.08.24 | 8:03 | 0:05 | 0 | 5 | [5 empty] | At Palasponga end: O/C,IA=301A,Ib-213A,IC=129A,INM=7.06A, IND=7.5A
|  | 17.08.24 | 11:27 | 17.08.24 | 11:52 | 0:25 | 0 | 25 | [5 empty] | At Joda end: B-N, Ib- 9.154kA
|  | 10.09.24 | 04:26 | 10.09.24 | 4:52 | 0:26 | 0 | 26 | [5 empty] | At Palasponga end: Over Current,IA=97.0A,IB=1115.6A,IC=1021.6A,IN=0A, IG=5.95A
|  | 17.09.24 | 08:04 | 17.09.24 | 8:07 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: Over Current,IA=300.2A,IB=266.5A,IC=42.85A,INM=7.405A,IND=6.986A
|  | 21.09.24 | 15:37 | 21.09.24 | 15:40 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: Over Current,IA=300.7A,IB=253.9A,IC=73.38A,INM=6.56A,IND=6.9A
|  | 2024-10-16 | 15:45 | 2024-10-16 | 15:49 | 0:04 | 0 | 4 | [5 empty] | At Polasponga end: Over Current, IA=300A,IB=210A,IC=133A,IND=7.24,INM=7.807A
|  | 2024-10-25 | 06:33 | 2024-10-25 | 8:50 | 2:17 | 2 | 17 | [5 empty] | At Polasponga end: Earth Fault, IN=95.5A,IB=99.95A,IC=1733A,INM=1747A,IND=1745A
|  | 14.11.24 | 14:31 | 14.11.24 | 14:35 | 0:04 | 0 | 4 | [5 empty] | At Palasponga end: Over Current,IA=301.7A,IB=264A,IC=54.8, IND=6.977A,INM=8.432A
|  | 27.11.24 | 07:33 | 27.11.24 | 7:35 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Over Current,IA=308.31,IB=267.2A,IC=47.8A,INM=7.038A,IND=5.807A
|  | 28.11.24 | 14:20 | 28.11.24 | 14:22 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Over Current,IA=301.1A,IB=278.5,IC=33.74A,INM=6.882A,IND=6.77A
|  | 11.12.24 | 07:49 | 11.12.24 | 8:07 | 0:18 | 0 | 18 | [5 empty] | At Palasponga end: Over Current, IA=300A,IB=230A,IC=112.7A
|  | 19.12.24 | 22:20 | 19.12.24 | 22:22 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Over Current, IA=302A,IB=223A,IC=130A
|  | 25.12.24 | 06:03 | 25.12.24 | 6:05 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Earth Fault, If- 2.178kA
|  | 7.01.25 | 19:52 | 7.01.25 | 19:54 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C
|  | 11.01.25 | 17:28 | 11.01.25 | 17:29 | 0:01 | 0 | 1 | [5 empty] | At Polasponga end: O/C
|  | 11.01.25 | 17:47 | 11.01.25 | 17:49 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C
|  | 12.01.25 | 23:20 | 12.01.25 | 23:22 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C
|  | 14.01.25 | 15:20 | 14.01.25 | 15:23 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end:Over Current, IA=303.5A, IB=249.2A, IC=71.38A
|  | 3.02.25 | 18:13 | 3.02.25 | 18:15 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Over Current IA=301.6A, IB=259.6A, IC=47.07A, INM=7.019A, IND=5.304A
|  | 12.02.25 | 16:25 | 12.02.25 | 16:29 | 0:04 | 0 | 4 | [5 empty] | At Palasponga end: Over CurrentIA=229.5A, IB=213.5A, IC=122.8A, INM=7.119A, IND=7.748A
|  | 17.02.25 | 15:34 | 17.02.25 | 15:36 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Relay Not OperatedNo Indication In Relay
|  | 18.02.25 | 07:26 | 18.02.25 | 7:27 | 0:01 | 0 | 1 | [5 empty] | At Palasponga end: Over CurrentIA=300.4A, IB=236.8A, IC=70.68A
|  | 20.02.25 | 12:20 | 20.02.25 | 12:44 | 0:24 | 0 | 24 | [5 empty] | At Palasponga end: Earth Fault, IA=2.768kA, IB=42A, IC=17.2A
|  | 26.02.25 | 17:21 | 26.02.25 | 17:23 | 0:02 | 0 | 2 | [5 empty] | At Palasponga end: Over Curren, tIA=299.8A, IB=207.4A, IC=115.3A, INM=6.603A, IND=6.707A
|  | 1.03.25 | 19:15 | 1.03.25 | 19:17 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C, Ir- 0.303kA, Iy- 0.252kA
|  | 4.03.25 | 10:22 | 4.03.25 | 10:24 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C, Ir- 0.299kA, Iy- 0.26kA
|  | 6.03.25 | 04:00 | 6.03.25 | 4:03 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.229kA
|  | 7.03.25 | 17:26 | 7.03.25 | 17:29 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.211kA
|  | 8.03.25 | 15:10 | 8.03.25 | 15:12 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.22kA
|  | 8.03.25 | 16:38 | 8.03.25 | 16:41 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: O/C, Ir- 0.314kA, Iy- 0.25kA
|  | 8.03.25 | 17:11 | 8.03.25 | 17:13 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C, Ir- 0.3kA, Iy- 0.253kA
|  | 8.03.25 | 17:23 | 8.03.25 | 17:27 | 0:04 | 0 | 4 | [5 empty] | At Polasponga end: O/C, Ir- 0.305kA, Iy- 0.253kA
|  | 13.03.25 | 04:03 | 13.03.25 | 4:12 | 0:09 | 0 | 9 | [5 empty] | At Polasponga end: O/C, Ir- 0.302kA, Iy- 0.236kA
|  | 18.03.25 | 00:07 | 18.03.25 | 0:09 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end: O/C, Ir- 0.307kA, Iy- 0.225kA
|  | 21.03.25 | 17:48 | 21.03.25 | 18:20 | 0:32 | 0 | 32 | [5 empty] | At Polasponga end: Y-N, Dist- 32.22km, Iy- 0.569kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
372 | 132 kV Palasponga - Essar |  |  |  |  | 1899-12-31 20:18 | 33 | 27 | [7 empty] | 19.093 | 8760 | 99.62% | 638.6609 | 167254.68
|  | 09.04.24 | 14:50 | 09.04.24 | 14:53 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.506kA, Iy- 0.409kA, Ib- 0.348kA
|  | 13.04.24 | 17:55 | 13.04.24 | 17:58 | 0:03 | 0 | 3 | [5 empty] | O/C, Ir- 0.3kA, Iy- 0.243kA, Ib- 0.065kA
|  | 20.04.24 | 23:03 | 20.04.24 | 23:07 | 0:04 | 0 | 4 | [5 empty] | O/C, Zone 1, Ir- 0.501kA, Iy- 0.433kA, Ib- 0.317kA
|  | 19.04.24 | 11:50 | 19.04.24 | 12:08 | 0:18 | 0 | 18 | [5 empty] | B-N, Dist- 13.6km, Iy- 2.42kA, Ib- 2.36kA
|  | 11.05.24 | 19:59 | 12.05.24 | 11:28 | 15:29 | 15 | 29 | [5 empty] | At Palasponga end: Distance Protection,IL1=0.01KA,IL2=0.01KA,IL3=0.09KA,L3-E,DIST=-159.9KM
|  | 20.05.24 | 14:21 | 20.05.24 | 14:39 | 0:18 | 0 | 18 | [5 empty] | At Palasponga end: Distance Protection,Z1, LE-E, IL1=2.1KA, IL2=0.14KA, IL3=0KA, DIST=8.0KM
|  | 11.05.24 | 22:18 | 11.05.24 | 22:34 | 0:16 | 0 | 16 | [5 empty] | At Palasponga end: Distance Protection,ER, IA=256A,IB=287A,IC=1244A,IG=878A At Joda end: Earth Fault,132kV Joda-Palasponga feeder tripped at Both End. Relay at Palasponga end:- Fault CurrentIa-256AIb-287AIc-1244AIg-878A Relay at Joda end:-DP Operate.B-PH faultDist- 1KM Fault Current :-Ia-213.8AIb-186.83AIc-703A
|  | 12.05.24 | 17:04 | 12.05.24 | 17:38 | 0:34 | 0 | 34 | [5 empty] | At Joda end: Earth Fault, DP-I , ZONE-1, FAULT LOOP-YN, DISTANCE-5.3954KM Ia=215.01A, Ib=7045A, Ic=228.11A At Palasponga end: DP-I ZONE-I EVENT-BGT DISTANCE-33.39KM Ia=247A Ib=403A Ic=240A
|  | 31.05.24 | 14:48 | 31.05.24 | 14:51 | 0:03 | 0 | 3 | [5 empty] | At Palasponga end: O/C, IA=537.3A, IB=472.9A, IC=346.1A, IN=0.05A,IG=3.22A
|  | 03.06.24 | 12:54 | 03.06.24 | 12:57 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=508.6A,IB=416.8A,IC=342.1A, ,IG=3.42A
|  | 02.06.24 | 18:48 | 02.06.24 | 19:05 | 0:17 | 0 | 17 | [5 empty] | At Joda end:Earth Fault, IL1=.35KArnIL2=.72KArnIL3=.32KA At Polasponga end: Remote End Tripping,IL1=0.35KA,IL2=0.72KA,IL3=0.32KA
|  | 06.06.24 | 21:10 | 06.06.24 | 21:12 | 0:02 | 0 | 2 | [5 empty] | At Polasponga end:Over Current,AB T,IA=524.1A,IB=442.9A,IC=353.9A, IG=3.52A
|  | 09.06.24 | 15:01 | 09.06.24 | 15:08 | 0:07 | 0 | 7 | [5 empty] | At Polasponga end:Over Current,IA=490A,IB=422.4A,IC=373.3A, IG=2.15A
|  | 15.06.24 | 14:57 | 15.06.24 | 15:00 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=484.8A,IB=410.7A,IC=298.9A,IG=5.12A
|  | 16.06.24 | 16:01 | 16.06.24 | 16:04 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=527.9A,IB=446.7A,IC=359.6A,IG=4.83A
|  | 17.06.24 | 17:53 | 17.06.24 | 17:56 | 0:03 | 0 | 3 | [5 empty] | At Polasponga end: Over Current,AB T, IA=530A,IB=447A,IC=386A,IG=8.0A
|  | 20.06.24 | 23:27 | 20.06.24 | 23:51 | 0:24 | 0 | 24 | [5 empty] | At Joda end: Distance Protection,Relay at Joda end: DP relay Main: Zone -01 ,Dist-8.5364Km, Ia=4767.75A, Ib=231.52A, Ic=249.14A At Polasponga end: Distance Protection,AG T,Z-1,D=30.37KM,IA=407A, IB=238A,IC=270A, IG=526A
|  | 24.06.24 | 04:24 | 24.06.24 | 4:54 | 0:30 | 0 | 30 | [5 empty] | At Polasponga end: Over Current,IA=503.3A, IB=411.4A,IC=375.6A,IG=5.34A
|  | 14.07.24 | 19:50 | 14.07.24 | 20:00 | 0:10 | 0 | 10 | [5 empty] | At Polasponga end: O/C, Ir- 0.288kA, Iy- 0.724kA, Ib- 0.287kA At Joda end: Ir- 0.29kA, Iy- 0.72kA, Ib- 0.3kA
|  | 17.07.24 | 01:31 | 17.07.24 | 7:16 | 5:45 | 0 | 36 | [5 empty] | B-Phase CT Jumper burnt out at Polasponga end (open Circuited) no touch to Ground.
|  | 21.07.24 | 17:39 | 22.07.24 | 11:47 | 18:08 | 0 | 26 | [5 empty] | At Polasponga end: O/C, Dist- 51.7km, Ir- 0.329kA, Iy- 0.284kA, Ib- 0.334kA At Joda end: Y-B, Dist- 3.648km, Ir- 0.3kA, Iy- 8.533kA, Ib- 7.453kA
|  | 17.08.24 | 11:27 | 17.08.24 | 11:52 | 0:25 | 0 | 25 | [5 empty] | At Joda end: B-N, Ib- 9.154kA
|  | 10.09.24 | 04:26 | 10.09.24 | 4:52 | 0:26 | 0 | 26 | [5 empty] | At Palasponga end: Over Current,IA=97.0A,IB=1115.6A,IC=1021.6A,IN=0A, IG=5.95A
|  | 2024-10-30 | 22:04 | 2024-10-30 | 22:16 | 0:12 | 0 | 12 | [5 empty] | At Polasponga end: Distance Protection, BGT, Distance=11.29KM, Zone-I, IA=326A, IB=570A,IC=252A, IN=0A,IG=754A At Joda end: DP relay : Tripped phase : YN, Zone 1, Dist:31.06Km, Fault Current :Ia-318.63A ,Ib-2806A, Ic-235.26A | Polasponga, OSISL, Patnaik Steel ESIL | 00:12 00:13 | - | -
|  | 21.03.25 | 17:48 | 21.03.25 | 18:20 | 0:32 | 0 | 32 | [5 empty] | At Polasponga end: Y-N, Dist- 32.22km, Iy- 0.569kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
373 | 132kV OPCL-Kamakhyanagar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 54.2 | 8760 | 100% | 0 | 474792
374 | 132kV Kamakhyanagar-Goda |  |  |  |  | 0.075 | 1 | 27 | [7 empty] | 25.551 | 8760 | 99.98% | 37.0489 | 223826.76
|  | 05.05.24 | 12:05 | 05.05.24 | 13:32 | 1:27 | 1 | 16 | [5 empty] | At Kamakhyanagar end: O/C, Ib- 0.4kA
|  | 02.06.24 | 19:54 | 02.06.24 | 20:15 | 0:21 | 0 | 11 | [5 empty] | At Kamakhyanagar end: Distance Protection,i1=938.6A,i2=25.2A,i3=74.09A , distance=20.6km At Goda end: Tripped on E/F in R-Phase, Zone-I, Ir:5.99KA,Iy:27.97A,Ib:8.37A, In : 5.95KA
375 | 132kV Goda-Kalarangi |  |  |  |  | 0.041667 | 1 | 0 | [7 empty] | 10.326 | 8760 | 99.99% | 10.326 | 90455.76
|  | 07.06.24 | 16:03 | 07.06.24 | 17:03 | 1:00 | 1 | 0 | [5 empty] | At Goda end: Tripped on E/F in R & Y-Phase, Zone-I, Ir:6.2KA,Iy6.35KA,Ib:115A,Dist : 8.2km. At Kalarangi end: Y- G , Ir: 96A,Iy : 91A, Ib :119A, Dist :none
376 | 132kV Kalarangi-Duburi |  |  |  |  | 0.09375 | 2 | 15 | [7 empty] | 39.7 | 8760 | 99.97% | 89.325 | 347772
|  | 02.06.24 | 20:18 | 02.06.24 | 20:43 | 0:25 | 0 | 25 | [5 empty] | At Duburi end: Distance Protection,Distant Protection RelayrnStart Phase - C N,Tripped Phase - A B C, ZONE-1, FAULT LOCATION = 6.289KM, Ia=52.14A,Ib=70.55A, Ic=3.99KA,Van=74.57KV,Vbn=75.96KV, Vcn=31.63KV , Fault Resistance= 1.005 ohm, Relay Trip time =79.96ms
|  | 07.06.24 | 15:39 | 07.06.24 | 17:29 | 1:50 | 1 | 50 | [5 empty] | At Duburi end: Distance Protection,
377 | 132kV Kamakhya Nagar - Kamakhya Nagar RTSS |  |  |  |  | 0.060417 | 1 | 16 | [7 empty] | 4.94 | 8760 | 99.99% | 6.2573 | 43274.4
|  | 05.05.24 | 12:05 | 05.05.24 | 13:32 | 1:27 | 1 | 16 | [5 empty] | At Kamakhyanagar end: O/C, Ib- 0.4kA
378 | 132kV Katapalli-Sambalpur |  |  |  |  | 0.019444 | 0 | 28 | [7 empty] | 21.85 | 8760 | 99.99% | 10.1967 | 191406
|  | 23.05.24 | 19:14 | 23.05.24 | 19:29 | 0:15 | 0 | 15 | [5 empty] | At Sambalpur end:Tripped on Z2, Z3, Bph E/F, Ia=645A, Ib=514A,Ic=2802A, Ig=2178A, Fault dist.=23.04KM, fault duration= 435.348ms No tripping at Katapali end
|  | 26.03.25 | 15:16 | 26.03.25 | 15:29 | 0:13 | 0 | 13 | [5 empty] | At Katapali end: O/C, Ir- 0.53kA, Iy- 0.58kA, Ib- 0.56kA
379 | 132kV Katapalli-RTSS Godhbhaga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 10.66 | 8760 | 100% | 0 | 93381.6
380 | 132kV Kendrapada-Marshaghai |  |  |  |  | 0.0625 | 13 | 30 | [7 empty] | 16.2 | 8760 | 99.85% | 218.7 | 141912
|  | 20.06.24 | 12:41 | 20.06.24 | 12:48 | 0:07 | 0 | 7 | [5 empty] | At Marshaghai end: Remote End Tripping,source fail
|  | 29.09.24 | 22:41 | 29.09.24 | 23:00 | 0:19 | 0 | 19 | [5 empty] | At Marshaghai end: Relay Not Operated,incoming failure
|  | 29.09.24 | 23:01 | 29.09.24 | 23:09 | 0:08 | 0 | 8 | [5 empty] | At Marshaghai end: Relay Not Operated,source failure
|  | 29.09.24 | 23:16 | 29.09.24 | 23:19 | 0:03 | 0 | 3 | [5 empty] | At Marshaghai end: Relay Not Operated,source failure
|  | 27.12.24 | 22:32 | 27.12.24 | 22:51 | 0:19 | 0 | 19 | [5 empty] | At Kendrapara end: Tripped on M/R
|  | 31.12.24 | 9:00 | 31.12.24 | 9:17 | 0:17 | 0 | 17 | [5 empty] | At Kendrapara end: TRIPPED ON B/U RELAY, Ia-21.43A,Ib-53.53A,Ic-868A At Marshaghai end: L3 TO EARTH FAULT
|  | 18.03.25 | 7:45 | 18.03.25 | 8:02 | 0:17 | 0 | 17 | [5 empty] | At Kendrapara end: Zone 4, Ir- 2.038kA, Ib- 2.046kA No tripping at Marshaghai end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
381 | 132kV Marshaghai-Paradeep |  |  |  |  | 0.12153 | 12 | 58 | [7 empty] | 19.61 | 8760 | 99.85% | 254.2763 | 171783.6
|  | 20.06.24 | 12:41 | 20.06.24 | 12:48 | 0:07 | 0 | 7 | [5 empty] | At Marshaghai end: Remote End Tripping,source fail
|  | 12.08.24 | 15:56 | 12.08.24 | 17:33 | 1:37 | 0 | 25 | [5 empty] | Source failure at Paradeep end
|  | 29.09.24 | 22:41 | 29.09.24 | 23:52 | 1:11 | 0 | 26 | [5 empty] | At Marshaghai end: Distance Protection,Distance-Zone-1(1.5 km), IL3 =2.15 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
382 | 132kV Marshaghai-Kendrapara RTSS |  |  |  |  | 0.092361 | 13 | 18 | [7 empty] | 14.08 | 8760 | 99.85% | 187.264 | 123340.8
|  | 20.06.24 | 12:41 | 20.06.24 | 12:48 | 0:07 | 0 | 7 | [5 empty] | At Marshaghai end: Remote End Tripping,source fail
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
|  | 27.12.24 | 22:32 | 27.12.24 | 22:51 | 0:19 | 0 | 19 | [5 empty] | At Kendrapara end: Tripped on M/R
|  | 31.12.24 | 9:00 | 31.12.24 | 9:17 | 0:17 | 0 | 17 | [5 empty] | At Kendrapara end: TRIPPED ON B/U RELAY, Ia-21.43A,Ib-53.53A,Ic-868A At Marshaghai end: L3 TO EARTH FAULT
|  | 19.02.25 | 18:24 | 19.02.25 | 18:34 | 0:10 | 0 | 10 | [5 empty] | At Marshaghai end: DP relay operated, R-phase fault current. IL1-5.84 KA,IL2-0.0KA,IL3-0 KA, DISTANCE- 0.6 KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
383 | 132kV Kendrapada-Paradeep |  |  |  |  | 1899-12-31 04:05 | 14 | 4 | [7 empty] | 15.77 | 8760 | 99.84% | 221.8313 | 138145.2
|  | 14.05.24 | 16:24 | 14.05.24 | 16:45 | 0:21 | 0 | 16 | [5 empty] | At Kendrapara end: Distance Protection,Tripped on DP with M/R, Zone-4, Distance=502mtrs., IR=1.85kA, IY=203A, IB=170A
|  | 20.06.24 | 12:41 | 20.06.24 | 12:51 | 0:10 | 0 | 8 | [5 empty] | At Kendrapara end: Over Current,TRIPPED ON MASTER TRIP RELAY WITH IR=500A, IY=90A, IB=197.4A
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
|  | 29.09.24 | 22:42 | 29.09.24 | 23:16 | 0:34 | 0 | 23 | [5 empty] | Earth Fault
|  | 27.12.24 | 22:32 | 28.12.24 | 19:22 | 20:50 | 0 | 19 | [5 empty] | At Kendrapara end: Tripped on M/R At Paradeep end: No tripping
|  | 31.12.24 | 9:00 | 31.12.24 | 13:34 | 4:34 | 0 | 17 | [5 empty] | At Kendrapara end: TRIPPED ON DP RELAY ZONE-1,DISTANCE-16.74KM,Ia-33.28A,Ib-35.34A,Ic-2.304KA At Paradeep end: B-Ph to G, Zone I, Dist-11.91 kms, Ir=34.82 A, Iy=27.76 A, Ib=4.06 kA
|  | 18.03.25 | 7:45 | 18.03.25 | 8:01 | 0:16 | 0 | 16 | [5 empty] | At Kendrapara end: Zone 4, Ir- 2.166kA, Ib- 2.170kA No tripping at Paradeep end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
384 | 132kV Kendrapada-Pattamundai |  |  |  |  | 0.16597 | 14 | 17 | [7 empty] | 19.1 | 8760 | 99.84% | 272.8117 | 167316
|  | 08.05.24 | 15:58 | 08.05.24 | 16:52 | 0:54 | 0 | 49 | [5 empty] | At Kendrapara end: R-N, Zone 1, Dist- 10.88km, Ir- 4.15kA At Pattamundai end: R-N, Zone 1, Dist- 11.34km, Ir- 2kA
|  | 14.05.24 | 16:24 | 14.05.24 | 16:40 | 0:16 | 0 | 16 | [5 empty] | At Kendrapara end: Zone-4, distance=503mtrs, IR=1.8kA, IY=29.79A, IB=153.4A
|  | 20.06.24 | 12:41 | 20.06.24 | 12:51 | 0:10 | 0 | 8 | [5 empty] | At Kendrapara end: Over Current,TRIPPED ON MASTER TRIP RELAY WITH IR=500A, IY=90A, IB=197.4A
|  | 12.08.24 | 15:56 | 12.08.24 | 17:48 | 1:52 | 0 | 25 | [5 empty] | At Pattamundai end: O/C (R-Y-B) , Ir- 0.53kA, Iy- 0.54kA, Ib- 0.52kA
|  | 29.09.24 | 22:43 | 29.09.24 | 23:06 | 0:23 | 0 | 23 | [5 empty] | At Pattamundai end: Over Current,Directional O/C(R,Y,B) Ir=0.41kA, Iy=0.39kA, Ib=0.43kA
|  | 18.03.25 | 7:45 | 18.03.25 | 8:09 | 0:24 | 0 | 16 | [5 empty] | At Kendrapara end: Zone 4, Ir- 1.862kA, Ib- 1.942kA No tripping at Pattamundai end
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
385 | 132kV Pattamundai-Olavar Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 23.94 | 8760 | 100% | 0 | 209714.4
386 | 132kV Pattamundai-Olavar Ckt -II |  |  |  |  | 0.11111 | 0 | 0 | [7 empty] | 23.94 | 8760 | 100% | 0 | 209714.4
387 | 132kV Pattamundai-Rajnagar Ckt - I |  |  |  |  | 0.055556 | 1 | 20 | [7 empty] | 22.286 | 8760 | 99.98% | 29.7147 | 195225.36
|  | 08.05.24 | 16:06 | 08.05.24 | 16:55 | 0:49 | 0 | 49 | [5 empty] | At Pattamundai end: B-N, Zone 1, Dist- 6.9km, Ib- 1.83kA At Rajnagar end: B-N, Zone 1, Dist- 11km, Ib- 0.5kA
|  | 2024-10-19 | 16:27 | 2024-10-19 | 16:58 | 0:31 | 0 | 31 | [5 empty] | At Pattamundai end: Distance Protection, Zone 1, Dist=14.1km , Ir=0.07kA,Iy=0.07kA & Ib=2.17kA At Rajnagar end: Distance Protection, Zone 1, Dist=4.6km , Ir=0.08kA,Iy=0.07kA & Ib=1.28kA
388 | 132kV Pattamundai-Rajnagar Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 22.286 | 8760 | 100% | 0 | 195225.36
389 | 132kV Olavar - Chandabali Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.5 | 8760 | 100% | 0 | 109500
390 | 132kV Olavar - Chandabali Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.5 | 8760 | 100% | 0 | 109500
391 | 132kV Dhamara - Chandabali Ckt - I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.373 | 8760 | 100% | 0 | 239787.48
392 | 132kV Dhamara - Chandabali Ckt - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.373 | 8760 | 100% | 0 | 239787.48
393 | 132kV Therubali-Muniguda-Vedant Alumina |  |  |  |  | 0.0083333 | 0 | 12 | [7 empty] | 76.15 | 8760 | 100% | 15.23 | 667074
|  | 16.07.24 | 07:30 | 16.07.24 | 7:42 | 0:12 | 0 | 12 | [5 empty] | At Therubali end: E/F (Y-N), Zone 1, Dist- 3.79km, Iy- 6.6kA
394 | 132kV Vedant Alumina-Kesinga |  |  |  |  | 0.16944 | 14 | 26 | [7 empty] | 57.28 | 8760 | 99.84% | 826.7413 | 501772.8
|  | 12.05.24 | 16:47 | 12.05.24 | 17:12 | 0:25 | 0 | 16 | [5 empty] | At Kesinga end: Earth Fault,Earth Fault, in B phase,Fault Current 1.72 KA,Distance Pick up-44.62 KM From Local End
|  | 14.05.24 | 11:09 | 14.05.24 | 12:44 | 1:35 | 0 | 6 | [5 empty] | At Kesinga end: O/C,O/C, Fault Current R Phase-1.74 KA, Y Phase-1.49 KA, B Phase-235.2A,Distance Pick up 62.6 KM from Local end
|  | 25.05.24 | 8:56 | 25.05.24 | 09:02 | 0:06 | 0 | 6 | [5 empty] | At Kesinga end: O/C,O/C, R-2.2KA,Y-0.01KA,B-0.01KA
|  | 13.07.24 | 08:54 | 13.07.24 | 9:17 | 0:23 | 0 | 23 | [5 empty] | At Kesinga end: O/C, Iy- 3.14kA
|  | 16.07.24 | 18:18 | 16.07.24 | 19:53 | 1:35 | 1 | 35 | [5 empty] | At Kesinga end: Dist- 57.13km, Ir- 0.147kA, Iy- 0.223kA, Ib- 1.417kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
395 | 132kV Kesinga-Bhawanipatna |  |  |  |  | 0.34444 | 15 | 24 | [7 empty] | 39.81 | 8760 | 99.82% | 613.074 | 348735.6
|  | 14.04.24 | 12:07 | 14.04.24 | 12:26 | 0:19 | 0 | 14 | [5 empty] | E/F, Ir- 0.115kA, Iy- 0.438kA, Ib- 0.124kA
|  | 15.04.24 | 15:08 | 15.04.24 | 15:14 | 0:06 | 0 | 6 | [5 empty] | Over Excitation, O/C
|  | 19.05.24 | 11:57 | 19.05.24 | 12:10 | 0:13 | 0 | 13 | [5 empty] | TRIPPED ON E/F AND NO P/S AT Bhawanipatna END
|  | 07.05.24 | 07:15 | 07.05.24 | 8:59 | 1:44 | 0 | 52 | [5 empty] | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  | 01.06.24 | 15:03 | 01.06.24 | 19:06 | 4:03 | 0 | 8 | [5 empty] | At Kesinga end: Earth Fault,DP, local end 14.41 kms
|  | 19.06.24 | 12:03 | 19.06.24 | 12:12 | 0:09 | 0 | 9 | [5 empty] | At Kesinga end: Earth Fault, Master Trip Operated
|  | 20.06.24 | 06:00 | 20.06.24 | 6:06 | 0:06 | 0 | 6 | [5 empty] | At Kesinga end: Over Current
|  | 20.06.24 | 14:17 | 20.06.24 | 14:35 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Earth Fault,E/F, R phase= 563Amp
|  | 19.06.24 | 11:28 | 19.06.24 | 11:58 | 0:30 | 0 | 30 | [5 empty] | At Junagarh end: Remote End Tripping, 132kV Kesinga Junagarh incomer tripped from both ends.
|  | 11.07.24 | 11:22 | 11.07.24 | 11:35 | 0:13 | 0 | 13 | [5 empty] | At Bhawanipatna end: Dist Protection,tripped due to tree loaded truck passing the line
|  | 11.07.24 | 12:41 | 11.07.24 | 13:05 | 0:24 | 0 | 24 | [5 empty] | At Kesinga end: E/F, Ir- 0.212kA, Iy- 0.916kA, Ib- 0.125kA
|  | 30.01.25 | 12:18 | 30.01.25 | 12:29 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Over Current, B phase Over Current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
396 | 132kV Bhawanipatna-Junagarh |  |  |  |  | 0.28542 | 17 | 39 | [7 empty] | 24.76 | 8760 | 99.8% | 437.014 | 216897.6
|  | 14.04.24 | 12:07 | 14.04.24 | 12:22 | 0:15 | 0 | 15 | [5 empty] | Zone 2, Dist- 51.62km, Ir- 0.209kA, Iy- 0.629kA, Ib- 0.159kA
|  | 15.04.24 | 15:08 | 15.04.24 | 15:22 | 0:14 | 0 | 14 | [5 empty] | Zone 2, Dist- 29.28km, Ir- 0.265kA, Iy- 0.82kA, Ib- 0.228kA
|  | 19.05.24 | 11:57 | 19.05.24 | 12:16 | 0:19 | 0 | 13 | [5 empty] | At Junagarh end: Earth Fault,R & Y ph E/F, Ia=0.2kA, Ib=0.7kA, Ic=0.14kA
|  | 24.05.24 | 11:31 | 24.05.24 | 11:36 | 0:05 | 0 | 5 | [5 empty] | At Junagarh end: O/C,Y & B ph O/C, Ia=0.11kA, Ib=0.29kA, Ic=0.27kA
|  | 24.05.24 | 12:05 | 24.05.24 | 12:06 | 0:01 | 0 | 1 | [5 empty] | At Junagarh end: O/C,IA=0.11 kA IB=0.26 kA IC=0.23 kA
|  | 24.05.24 | 12:46 | 24.05.24 | 12:48 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 24.05.24 | 13:11 | 24.05.24 | 13:13 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 07.05.24 | 07:15 | 07.05.24 | 8:14 | 0:59 | 0 | 52 | [5 empty] | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  | 01.06.24 | 15:03 | 01.06.24 | 16:03 | 1:00 | 0 | 8 | [5 empty] | At Junagarh end: Distance Protection, Trip phase A B C, Ia=363.3A, Ib=173.7A, Ic=198.8A, Fault Distance=56.19km
|  | 19.06.24 | 12:03 | 19.06.24 | 12:12 | 0:09 | 0 | 9 | [5 empty] | At Kesinga end: Earth Fault, Master Trip Operated
|  | 20.06.24 | 06:00 | 20.06.24 | 6:06 | 0:06 | 0 | 6 | [5 empty] | At Kesinga end: Over Current
|  | 20.06.24 | 14:17 | 20.06.24 | 14:35 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Earth Fault,E/F, R phase= 563Amp
|  | 19.06.24 | 11:28 | 19.06.24 | 11:58 | 0:30 | 0 | 30 | [5 empty] | At Junagarh end: Remote End Tripping, 132kV Kesinga Junagarh incomer tripped from both ends.
|  | 11.07.24 | 11:22 | 11.07.24 | 11:42 | 0:20 | 0 | 13 | [5 empty] | At Junagarh end: Y ph E/F, Zone 2, Dist-27.45km, Iy- 719A
|  | 11.07.24 | 12:41 | 11.07.24 | 13:05 | 0:24 | 0 | 24 | [5 empty] | At Kesinga end: E/F, Ir- 0.212kA, Iy- 0.916kA, Ib- 0.125kA
|  | 1.03.25 | 9:51 | 1.03.25 | 10:15 | 0:24 | 0 | 24 | [5 empty] | E/F
|  | 25.03.25 | 9:02 | 25.03.25 | 10:38 | 1:36 | 1 | 36 | [5 empty] | Supply failure
|  | 25.03.25 | 17:31 | 25.03.25 | 17:38 | 0:07 | 0 | 7 | [5 empty] | Supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
397 | 132kV Kesinga-Junagarh |  |  |  |  | 0.17917 | 14 | 23 | [7 empty] | 53.3 | 8760 | 99.84% | 766.6317 | 466908
|  | 07.05.24 | 07:15 | 07.05.24 | 08:12 | 0:57 | 0 | 51 | [5 empty] | At Junagarh end: Y-B, Dist- 50.6km, SOTF
|  | 01.06.24 | 15:53 | 01.06.24 | 16:02 | 0:09 | 0 | 9 | [5 empty] | At Junagarh end: Remote End Tripping, At Kesinga end: DP Relay zone-1, distance- 24.5Kms, B-phase 2.439KAmp
|  | 19.06.24 | 11:28 | 19.06.24 | 13:52 | 2:24 | 0 | 35 | [5 empty] | At Junagarh end: Distance Protection,Y ph E/F, Zone -I, Fault Distance=10.7km
|  | 11.07.24 | 11:22 | 11.07.24 | 11:35 | 0:13 | 0 | 13 | [5 empty] | At Bhawanipatna end: Dist Protection,tripped due to tree loaded truck passing the line
|  | 11.07.24 | 12:41 | 11.07.24 | 13:05 | 0:24 | 0 | 24 | [5 empty] | At Kesinga end: E/F, Ir- 0.212kA, Iy- 0.916kA, Ib- 0.125kA
|  | 30.01.25 | 12:18 | 30.01.25 | 12:29 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Over Current, B phase Over Current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
398 | 132kV Junagarh - Brundabahal |  |  |  |  | 0.024306 | 0 | 35 | [7 empty] | 26.82 | 6060 | 99.99% | 15.645 | 162529.2
|  | 30.01.25 | 12:18 | 30.01.25 | 12:29 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Over Current, B phase Over Current
|  | 1.03.25 | 9:51 | 1.03.25 | 10:15 | 0:24 | 0 | 24 | [5 empty] | E/F
399 | 132kV Bhawanipatna- Lanjigarh RTSS |  |  |  |  | 0.87986 | 17 | 41 | [7 empty] | 34.18 | 8760 | 99.8% | 604.4163 | 299416.8
|  | 01.04.24 | 17:54 | 01.04.24 | 17:57 | 0:03 | 0 | 3 | [5 empty] | O/C, Iy- 0.261kA, Ib- 0.258kA
|  | 01.04.24 | 21:46 | 01.04.24 | 21:48 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.265kA, Iy- 0.259kA
|  | 03.04.24 | 09:28 | 03.04.24 | 09:30 | 0:02 | 0 | 2 | [5 empty] | O/C, Iy- 0.271kA, Ib- 0.266kA
|  | 06.04.24 | 20:56 | 06.04.24 | 20:58 | 0:02 | 0 | 2 | [5 empty] | O/C, Iy- 0.264kA, Ib- 0.259kA
|  | 08.04.24 | 15:35 | 08.04.24 | 15:40 | 0:05 | 0 | 5 | [5 empty] | O/C, If- 0.266kA
|  | 21.04.24 | 02:07 | 21.04.24 | 02:10 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 30.04.24 | 16:08 | 30.04.24 | 16:10 | 0:02 | 0 | 2 | [5 empty] | O/C, Iy- 0.264kA, Ib- 0.259kA
|  | 30.04.24 | 17:05 | 30.04.24 | 17:07 | 0:02 | 0 | 2 | [5 empty] | O/C, Ir- 0.264kA, Ib- 0.259kA
|  | 14.04.24 | 12:07 | 14.04.24 | 12:22 | 0:15 | 0 | 14 | [5 empty] | Zone 2, Dist- 51.62km, Ir- 0.209kA, Iy- 0.629kA, Ib- 0.159kA
|  | 15.04.24 | 15:08 | 15.04.24 | 15:22 | 0:14 | 0 | 14 | [5 empty] | Zone 2, Dist- 29.28km, Ir- 0.265kA, Iy- 0.82kA, Ib- 0.228kA
|  | 07.05.24 | 16:17 | 07.05.24 | 16:21 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 10.05.24 | 6:07 | 10.05.24 | 6:09 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 11.05.24 | 6:02 | 11.05.24 | 6:04 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 11.05.24 | 18:57 | 11.05.24 | 18:59 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON O/C
|  | 13.05.24 | 10:37 | 13.05.24 | 10:43 | 0:06 | 0 | 6 | [5 empty] | TRIPPED ON O/C
|  | 13.05.24 | 10:49 | 13.05.24 | 10:52 | 0:03 | 0 | 3
|  | 14.05.24 | 19:18 | 14.05.24 | 19:20 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 15.05.24 | 5:04 | 15.05.24 | 5:07 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 18.05.24 | 17:44 | 18.05.24 | 17:46 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON O/C
|  | 19.05.24 | 17:17 | 19.05.24 | 17:19 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON O/C
|  | 22.05.24 | 13:00 | 22.05.24 | 13:04 | 0:04 | 0 | 4 | [5 empty] | TRIPPED ON O/C
|  | 26.05.24 | 22:09 | 26.05.24 | 22:12 | 0:03 | 0 | 3 | [5 empty] | TRIPPED ON O/C
|  | 28.05.24 | 13:37 | 28.05.24 | 13:39 | 0:02 | 0 | 2 | [5 empty] | TRIPPED ON O/C
|  | 28.05.24 | 15:19 | 28.05.24 | 15:21 | 0:02 | 0 | 2
|  | 29.05.24 | 12:19 | 29.05.24 | 12:23 | 0:04 | 0 | 4 | [5 empty] | TRIPPED ON O/C
|  | 18.05.24 | 14:42 | 18.05.24 | 14:54 | 0:12 | 0 | 12 | [5 empty] | TRRIPED ON ZONE-I DISTANCE PROTECTION
|  | 19.05.24 | 11:57 | 19.05.24 | 12:16 | 0:19 | 0 | 19 | [5 empty] | At Junagarh end: Earth Fault,R & Y ph E/F, Ia=0.2kA, Ib=0.7kA, Ic=0.14kA
|  | 24.05.24 | 11:31 | 24.05.24 | 11:36 | 0:05 | 0 | 5 | [5 empty] | At Junagarh end: O/C,Y & B ph O/C, Ia=0.11kA, Ib=0.29kA, Ic=0.27kA
|  | 24.05.24 | 12:05 | 24.05.24 | 12:06 | 0:01 | 0 | 1 | [5 empty] | At Junagarh end: O/C,IA=0.11 kA IB=0.26 kA IC=0.23 kA
|  | 24.05.24 | 12:46 | 24.05.24 | 12:48 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 24.05.24 | 13:11 | 24.05.24 | 13:13 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
|  | 01.06.24 | 15:03 | 01.06.24 | 19:06 | 4:03 | 0 | 8 | [5 empty] | At Kesinga end: Earth Fault,DP, local end 14.41 kms
|  | 06.06.24 | 15:31 | 06.06.24 | 15:33 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: Over Current,Ia=0, Ib=266.8A, Ic=261.6A, In= 5.2A
|  | 07.06.24 | 12:33 | 07.06.24 | 12:35 | 0:02 | 0 | 2 | [5 empty] | At BhawanipAt na end:Over Current,Ia=0, Ib=263.6A, Ic=259.6A, In=5.2A
|  | 08.06.24 | 14:46 | 08.06.24 | 14:48 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: Over Current,IA=0, IB=266.4A, IC=263.6A, IN=5.2A
|  | 12.06.24 | 19:54 | 12.06.24 | 19:56 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: Over Current,IA=0, IB=267.2A, IC=262.0A, IN=5.6A
|  | 14.06.24 | 10:41 | 14.06.24 | 10:43 | 0:02 | 0 | 2 | [5 empty] | At BhawanipAt na end:Over Current,IA=0, IB=264.8A, IC=260.4A, IN=5.2A
|  | 19.06.24 | 08:09 | 19.06.24 | 8:11 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: Over Current,IA=0, IB=267.6A, IC=262.8A, IN=5.2A
|  | 19.06.24 | 12:03 | 19.06.24 | 12:12 | 0:09 | 0 | 9 | [5 empty] | At Kesinga end: Earth Fault, Master Trip Operated
|  | 20.06.24 | 06:00 | 20.06.24 | 6:06 | 0:06 | 0 | 6 | [5 empty] | At Kesinga end: Over Current
|  | 20.06.24 | 14:17 | 20.06.24 | 14:35 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Earth Fault,E/F, R phase= 563Amp
|  | 19.06.24 | 11:28 | 19.06.24 | 11:58 | 0:30 | 0 | 30 | [5 empty] | At Junagarh end: Remote End Tripping, 132kV Kesinga Junagarh incomer tripped from both ends.
|  | 11.07.24 | 11:22 | 11.07.24 | 11:35 | 0:13 | 0 | 13 | [5 empty] | At Bhawanipatna end: Dist Protection,tripped due to tree loaded truck passing the line
|  | 11.07.24 | 12:41 | 11.07.24 | 13:05 | 0:24 | 0 | 24 | [5 empty] | At Kesinga end: E/F, Ir- 0.212kA, Iy- 0.916kA, Ib- 0.125kA
|  | 30.07.24 | 16:14 | 30.07.24 | 16:18 | 0:04 | 0 | 4 | [5 empty] | At Bhawanipatna end: E/F
|  | 27.08.24 | 19:10 | 27.08.24 | 19:12 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: O/C,IA=0 A, Ib-314.8 A, IC=310.4 A, IN=5.6 A
|  | 30.08.24 | 20:11 | 30.08.24 | 20:13 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: O/C,IA=0 A, Ib-321.2 A, IC=316.4 A, IN=5.6 A
|  | 07.09.24 | 7:19 | 07.09.24 | 7:23 | 0:04 | 0 | 4 | [5 empty] | At Bhawanipatna end: Over Current
|  | 12.09.24 | 6:28 | 12.09.24 | 6:32 | 0:04 | 0 | 4 | [5 empty] | At Bhawanipatna end: Over Current
|  | 15.01.25 | 20:28 | 15.01.25 | 20:35 | 0:07 | 0 | 7 | [5 empty] | At Bhawanipatna end: E/F
|  | 30.01.25 | 12:18 | 30.01.25 | 12:29 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Over Current, B phase Over Current
|  | 22.03.25 | 14:36 | 22.03.25 | 14:39 | 0:03 | 0 | 3 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
400 | 132kV Bhawanipatna- Bhawanipatna RTSS |  |  |  |  | 1899-12-31 00:10 | 20 | 31 | [7 empty] | 2.102 | 8760 | 99.77% | 43.126 | 18413.52
|  | 08.04.24 | 08:49 | 08.04.24 | 08:52 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 14.04.24 | 12:07 | 14.04.24 | 12:22 | 0:15 | 0 | 15 | [5 empty] | Zone 2, Dist- 51.62km, Ir- 0.209kA, Iy- 0.629kA, Ib- 0.159kA
|  | 15.04.24 | 15:08 | 15.04.24 | 15:22 | 0:14 | 0 | 6 | [5 empty] | Zone 2, Dist- 29.28km, Ir- 0.265kA, Iy- 0.82kA, Ib- 0.228kA
|  | 02.04.24 | 08:35 | 02.04.24 | 08:41 | 0:06 | 0 | 6 | [5 empty] | O/C, Iy- 0.269kA, Ib- 0.259kA
|  | 30.04.24 | 02:33 | 30.04.24 | 02:37 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 30.04.24 | 03:04 | 30.04.24 | 03:08 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 18.05.24 | 14:42 | 18.05.24 | 14:54 | 0:12 | 0 | 6 | [5 empty] | TRRIPED ON ZONE-I DISTANCE PROTECTION
|  | 19.05.24 | 11:57 | 19.05.24 | 12:10 | 0:13 | 0 | 13 | [5 empty] | TRIPPED ON E/F AND NO P/S AT Bhawanipatna END
|  | 24.05.24 | 11:31 | 24.05.24 | 11:36 | 0:05 | 0 | 5 | [5 empty] | At Junagarh end: O/C,Y & B ph O/C, Ia=0.11kA, Ib=0.29kA, Ic=0.27kA
|  | 24.05.24 | 12:05 | 24.05.24 | 12:06 | 0:01 | 0 | 1 | [5 empty] | At Junagarh end: O/C,IA=0.11 kA IB=0.26 kA IC=0.23 kA
|  | 24.05.24 | 12:46 | 24.05.24 | 12:48 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 24.05.24 | 13:11 | 24.05.24 | 13:13 | 0:02 | 0 | 2 | [5 empty] | POWER SUPPLY FAIL FROM Junagarh END
|  | 07.05.24 | 5:52 | 07.05.24 | 6:00 | 0:08 | 0 | 8 | [5 empty] | Fault at Railway end
|  | 07.05.24 | 6:00 | 07.05.24 | 8:47 | 2:47 | 2 | 47 | [5 empty] | Fault at Railway end
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
|  | 01.06.24 | 15:03 | 01.06.24 | 19:06 | 4:03 | 0 | 8 | [5 empty] | At Kesinga end: Earth Fault,DP, local end 14.41 kms
|  | 19.06.24 | 12:03 | 19.06.24 | 12:12 | 0:09 | 0 | 9 | [5 empty] | At Kesinga end: Earth Fault, Master Trip Operated
|  | 20.06.24 | 06:00 | 20.06.24 | 6:06 | 0:06 | 0 | 6 | [5 empty] | At Kesinga end: Over Current
|  | 20.06.24 | 14:17 | 20.06.24 | 14:35 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Earth Fault,E/F, R phase= 563Amp
|  | 19.06.24 | 11:28 | 19.06.24 | 11:58 | 0:30 | 0 | 30 | [5 empty] | At Junagarh end: Remote End Tripping, 132kV Kesinga Junagarh incomer tripped from both ends.
|  | 11.07.24 | 11:22 | 11.07.24 | 11:35 | 0:13 | 0 | 13 | [5 empty] | At Bhawanipatna end: Dist Protection,tripped due to tree loaded truck passing the line
|  | 11.07.24 | 12:41 | 11.07.24 | 13:05 | 0:24 | 0 | 24 | [5 empty] | At Kesinga end: E/F, Ir- 0.212kA, Iy- 0.916kA, Ib- 0.125kA
|  | 01.08.24 | 07:47 | 01.08.24 | 7:52 | 0:05 | 0 | 5 | [5 empty] | At Bhawanipatna end: O/C
|  | 30.08.24 | 12:45 | 30.08.24 | 12:51 | 0:06 | 0 | 6 | [5 empty] | At Bhawanipatna end: O/C,IA=60 A, Ib-0 A, IC=60 A
|  | 02.09.24 | 01:10 | 02.09.24 | 1:30 | 0:20 | 0 | 20 | [5 empty] | O/C
|  | 02.09.24 | 3:29 | 02.09.24 | 3:32 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 24.09.24 | 12:54 | 24.09.24 | 12:58 | 0:04 | 0 | 4 | [5 empty] | At Bhawanipatna end: Over Current
|  | 26.09.24 | 3:03 | 26.09.24 | 3:07 | 0:04 | 0 | 4 | [5 empty] | At Bhawanipatna end: Over Current
|  | 2.11.24 | 17:34 | 2.11.24 | 17:38 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 1.12.24 | 2:39 | 1.12.24 | 2:42 | 0:03 | 0 | 3 | [5 empty] | O/C
|  | 30.01.25 | 12:18 | 30.01.25 | 12:29 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Over Current, B phase Over Current
|  | 16.01.25 | 2:31 | 16.01.25 | 2:33 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: O/C
|  | 22.01.25 | 8:05 | 22.01.25 | 8:16 | 0:11 | 0 | 11 | [5 empty] | At Bhawanipatna end: Tripped on O/C
|  | 4.02.25 | 22:51 | 4.02.25 | 22:56 | 0:05 | 0 | 5 | [5 empty] | At Bhawanipatna end: O/C
|  | 7.02.25 | 2:27 | 7.02.25 | 2:30 | 0:03 | 0 | 3 | [5 empty] | At Bhawanipatna end: O/C
|  | 7.02.25 | 3:12 | 7.02.25 | 3:14 | 0:02 | 0 | 2 | [5 empty] | At Bhawanipatna end: O/C
|  | 31.03.25 | 0:23 | 31.03.25 | 0:45 | 0:22 | 0 | 22 | [5 empty] | O/C
|  | 31.03.25 | 0:50 | 31.03.25 | 0:55 | 0:05 | 0 | 5 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
401 | 132kV Kesinga-Kesinga RTSS |  |  |  |  | 0.54583 | 1 | 36 | [7 empty] | 4.952 | 8760 | 99.98% | 7.9232 | 43379.52
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
|  | 26.06.24 | 17:03 | 26.06.24 | 17:48 | 0:45 | 0 | 45 | [5 empty] | At Kesinga end: Distance Protection,DP Relay zone-1, distance- 0.63Kms, O/C, R-phase 6.05K Amp
402 | 132kV Kesinga-Powmex |  |  |  |  | 0.61736 | 14 | 41 | [7 empty] | 14.53 | 8760 | 99.83% | 213.3488 | 127282.8
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
|  | 28.07.24 | 22:53 | 28.07.24 | 23:43 | 0:50 | 0 | 20 | [5 empty] | At Kesinga end: E/F, Ir- 0.095kA, Iy- 0.185kA, Ib- 0.19kA
|  | 07.08.24 | 18:18 | 07.08.24 | 18:33 | 0:15 | 0 | 15 | [5 empty] | At Kesinga end: E/F, Ir- 0.089kA, Iy- 0.097kA, Ib- 0.102kA
|  | 03.09.24 | 21:06 | 03.09.24 | 21:29 | 0:23 | 0 | 15 | [5 empty] | At Kesinga end: Earth Fault,Master Trip relay operated
|  | 12.09.24 | 22:50 | 12.09.24 | 23:06 | 0:16 | 0 | 16 | [5 empty] | At Kesinga end: Earth Fault,Master Trip Relay Operated
|  | 2024-10-12 | 04:57 | 2024-10-12 | 5:29 | 0:32 | 0 | 32 | [5 empty] | At Kesinga end: Earth Fault, Master Trip Relay Operated
|  | 2024-10-19 | 22:46 | 2024-10-19 | 22:58 | 0:12 | 0 | 12 | [5 empty] | At Kesinga end: Earth FaultR-80 A,Y-92 A,B-98 A,IN-273 A
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
403 | 132kV Kesinga- Vento Solar ckt-I |  |  |  |  | 0.51458 | 0 | 51 | [7 empty] | 5.74 | 8760 | 99.99% | 4.879 | 50282.4
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
404 | 132kV Kesinga- Vento Solar ckt-II |  |  |  |  | 0.51458 | 0 | 51 | [7 empty] | 5.74 | 8760 | 99.99% | 4.879 | 50282.4
|  | 07.05.24 | 07:15 | 08.05.24 | 19:36 | 12:21 | 0 | 51 | [5 empty] | At Kesinga end: E/F, B-Ph conductor of 132kV POWMEX Feeder snapped
405 | 132kV Kharagprasad-Meramundali RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1.17 | 8760 | 100% | 0 | 10249.2
406 | 132kV Kharagprasad-MGM |  |  |  |  | 0.29653 | 7 | 7 | [7 empty] | 7.14 | 8760 | 99.92% | 50.813 | 62546.4
|  | 30.04.24 | 12:55 | 30.04.24 | 19:41 | 6:46 | 6 | 46 | [5 empty] | Y-B Ph, Zone 2, Dist- 6.034km, Iy- 7.205kA, Ib- 6.810kA
|  | 28.08.24 | 12:31 | 28.08.24 | 12:52 | 0:21 | 0 | 21 | [5 empty] | At Kharagprasad end: O/C and Earth Fault(B-ph to Ground Fault). Ir=15.65A Iy-18.41 A , Ib-442.51 A Fault Duration-181 ms.
407 | 132kV Kharagprasad-Nabhabharat Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
408 | 132kV Kharagprasad-Nabhabharat Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.577 | 8760 | 100% | 0 | 5054.52
409 | 132kV Kharagprasad-Samal Metallic (SGEL) |  |  |  |  | 0.10556 | 2 | 32 | [7 empty] | 1.03 | 8760 | 99.97% | 2.6093 | 9022.8
|  | 24.05.24 | 13:58 | 24.05.24 | 16:30 | 2:32 | 2 | 32 | [5 empty] | At Kharagprasad end: Distance Protection,fault type LG fault Ir=8.33 KA ,Distance of fault = 0.3 KM
410 | 132kV Kuchei PG- Bangiriposhi Ckt-I |  |  |  |  | 0.11458 | 14 | 45 | [7 empty] | 31.13 | 8760 | 99.83% | 459.1675 | 272698.8
|  | 06.05.24 | 19:01 | 06.05.24 | 19:53 | 0:52 | 0 | 52 | [5 empty] | At Baripada PG end: Directional O/C, Ir- 0.18kA, Iy- 0.32kA, Ib- 2.79kA
|  | 11.05.24 | 14:21 | 11.05.24 | 14:59 | 0:38 | 0 | 38 | [5 empty] | At Bangriposi end: Remote End Tripping, At Baripada End:-B/U Relay I>>Dir.Trip-L1, Directional O/C Trip, IL1-2.646KA, IL2-0.342KA, IL3-0.457KA & IN-1.848KA
|  | 22.07.24 | 01:13 | 22.07.24 | 1:44 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG end: Directional O/C, Ir-0.39kA, Iy-0.32kA, Ib-0.26kA
|  | 31.07.24 | 15:12 | 31.07.24 | 15:56 | 0:44 | 0 | 44 | [5 empty] | At Baripada PG end: O/C & E/F (Y-N), Zone 1, Dist- 10.12km, Iy- 5.6kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
411 | 132kV Kuchei PG- Bangiriposhi Ckt-II |  |  |  |  | 0.052083 | 1 | 15 | [7 empty] | 31.256 | 8760 | 99.99% | 39.07 | 273802.56
|  | 22.07.24 | 01:13 | 22.07.24 | 1:44 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG end: Directional O/C, Ir-0.39kA, Iy-0.32kA, Ib-0.26kA
|  | 31.07.24 | 15:12 | 31.07.24 | 15:56 | 0:44 | 0 | 44 | [5 empty] | At Baripada PG end: O/C & E/F (Y-N), Zone 1, Dist- 10.12km, Iy- 5.6kA
412 | 132kV Bangiriposhi- Rairangapur |  |  |  |  | 0.16111 | 15 | 49 | [7 empty] | 34.2 | 8760 | 99.82% | 540.93 | 299592
|  | 06.05.24 | 19:01 | 06.05.24 | 19:53 | 0:52 | 0 | 52 | [5 empty] | At Baripada PG end: Directional O/C, Ir- 0.18kA, Iy- 0.32kA, Ib- 2.79kA
|  | 11.05.24 | 14:21 | 11.05.24 | 15:02 | 0:41 | 0 | 38 | [5 empty] | At Bangriposi end: Distance Protection, DP Relay O/C & E/F Trip, Zone-1, Dist.-5.6KM, Fault Loop: L1-E, IL1-2.34KA, IL2-0.22KA & IL3-0.33KA.
|  | 23.06.24 | 13:20 | 23.06.24 | 13:48 | 0:28 | 0 | 28 | [5 empty] | At Rairangpur end: Z4, dist-2.846km, Ia=398.3A,Ib=718.5A, Ic=1.769KA At Bangiriposi end: Backup relay, E/F,L3-E, IL1=0.01KA, IL2=0.01KA, IL3=1.35KA
|  | 22.07.24 | 01:13 | 22.07.24 | 1:44 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG end: Directional O/C, Ir-0.39kA, Iy-0.32kA, Ib-0.26kA
|  | 31.07.24 | 15:12 | 31.07.24 | 15:56 | 0:44 | 0 | 44 | [5 empty] | At Baripada PG end: O/C & E/F (Y-N), Zone 1, Dist- 10.12km, Iy- 5.6kA
|  | 17.08.24 | 00:42 | 17.08.24 | 0:57 | 0:15 | 0 | 15 | [5 empty] | At Bangriposi end: R-N, Zone 1, Dist- 13.3km, Ir- 3.06kA At Rairangpur end: R-N, Zone 1, Dist- 23.9km, Ir- 0.442kA
|  | 18.03.25 | 4:58 | 18.03.25 | 5:19 | 0:21 | 0 | 21 | [5 empty] | At Bangiriposi end: Y-N, Zone 1, Dist- 21.4km, Iy- 2.57kA At Rairangpur end: Y-N, Zone 1, Dist- 20.48km, Iy- 0.395kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
413 | 132kV Rairangapur- Karanjia |  |  |  |  | 0.27222 | 17 | 36 | [7 empty] | 70.74 | 8760 | 99.8% | 1245.024 | 619682.4
|  | 06.05.24 | 19:01 | 06.05.24 | 19:53 | 0:52 | 0 | 28 | [5 empty] | At Baripada PG end: Directional O/C, Ir- 0.18kA, Iy- 0.32kA, Ib- 2.79kA
|  | 11.05.24 | 14:21 | 11.05.24 | 15:03 | 0:42 | 0 | 42 | [5 empty] | At Bangriposi end: Distance Protection, DP Relay O/C & E/F Trip, Zone-1, Dist.-5.6KM, Fault Loop: L1-E, IL1-2.34KA, IL2-0.22KA & IL3-0.33KA.
|  | 23.06.24 | 13:20 | 23.06.24 | 14:01 | 0:41 | 0 | 28 | [5 empty] | At Rairangpur end: Z4, dist-19.08KM, Ia=96.08A, Ib=249.3A,Ic=176.6A
|  | 22.07.24 | 01:13 | 22.07.24 | 1:44 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG end: Directional O/C, Ir-0.39kA, Iy-0.32kA, Ib-0.26kA
|  | 31.07.24 | 15:12 | 31.07.24 | 15:56 | 0:44 | 0 | 26 | [5 empty] | At Baripada PG end: O/C & E/F (Y-N), Zone 1, Dist- 10.12km, Iy- 5.6kA
|  | 14.08.24 | 16:38 | 14.08.24 | 16:47 | 0:09 | 0 | 9 | [5 empty] | At Karanjia end: R-B, Ir- 0.39kA, Iy- 0.29kA, Ib- 0.37kA, Dist- 50.2km At Rairangpur end: R-B, Zone 1, Ir- 1.529kA, Ib- 1.621kA, Dist-38.88km
|  | 27.08.24 | 19:47 | 27.08.24 | 20:01 | 0:14 | 0 | 14 | [5 empty] | At kAranjia end: Earth Fault,Dist pick up=L3-E, IL1=0.16kA, IL2=0.37kA, IL3=0.27kA, Dist-64.8km At Rairangpur end: IA=137.1A,Ib-378.3A,IC=1.907kA
|  | 17.08.24 | 00:42 | 17.08.24 | 0:57 | 0:15 | 0 | 15 | [5 empty] | At Bangriposi end: R-N, Zone 1, Dist- 13.3km, Ir- 3.06kA At Rairangpur end: R-N, Zone 1, Dist- 23.9km, Ir- 0.442kA
|  | 21.08.24 | 12:40 | 21.08.24 | 12:53 | 0:13 | 0 | 13 | [5 empty] | At kAranjia end: Dist Protection,Dist pick up=L2-E, IL1=0.28kA, IL2=0.28kA, IL3=0.35kA, Dist-30.2km
|  | 23.09.24 | 15:12 | 23.09.24 | 15:54 | 0:42 | 0 | 42 | [5 empty] | At Rairangpur end: Zone-1, Y-Phase,Dist=22.64KM,IA=318.8A,IB=1.753KA,IC=174.8A,Van=72.79KV,Vbn=27.72KV,Vcn=75.54KV At Karanjia end: Zone-1, Y-Phase,Dist=57.9KM,IL1=0.32KA,IB=0.26KA,IC=0.19KA
|  | 2024-10-09 | 16:39 | 2024-10-09 | 16:56 | 0:17 | 0 | 16 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=5ms, Distance pick up=L1-L2, IL1=0.33KA, IL2=0.27KA, IL3=0.35KA, Distance=59km At Rairangpur end: R-ph, Y-ph, Zone 1, Distance-27.23 KM, Ia=1.776KA, Ib=1.723 KA, Ic=342.9 A
|  | 18.11.24 | 19:09 | 18.11.24 | 19:20 | 0:11 | 0 | 11 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=ms, Distance pick up=L2-E, Rsec=4.96ohm, Xsec=8.39ohm, Rpri=14.88ohm, Xpri=25.18ohm, Distance=60.8kmrn At Rairangpur End: DP relay: Trip time=ms, Distance pick up=L2-E, IL1=283.6A, IL2=1.889KA, IL3=142.0A, Distance=16.07km
|  | 18.11.24 | 21:55 | 18.11.24 | 22:05 | 0:10 | 0 | 10 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=ms, Distance pick up=L2-E, Rsec=4.96ohm, Xsec=8.39ohm, Rpri=14.88ohm, Xpri=25.18ohm, Distance=60.8km At Rairangpur End: DP relay: Trip time=ms, Distance pick up=L2-E, IL1=294.6A, IL2=1.841KA, IL3=136.3A, Distance=16.15km
|  | 25.01.25 | 03:06 | 25.01.25 | 3:36 | 0:30 | 0 | 30 | [5 empty] | At Rairangpur end: Distance Protection, Y-Phase ,Z1,Dist=13.64KM,IL1=278.3A,IL2=2.069KA,IL3=146.7A No relay Indication at Karanjia GSS
|  | 18.03.25 | 4:58 | 18.03.25 | 5:19 | 0:21 | 0 | 21 | [5 empty] | At Bangiriposi end: Y-N, Zone 1, Dist- 21.4km, Iy- 2.57kA At Rairangpur end: Y-N, Zone 1, Dist- 20.48km, Iy- 0.395kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
414 | 132kV Karanjia-Dhenkikote |  |  |  |  | 0.30139 | 18 | 31 | [7 empty] | 40.7 | 8760 | 99.79% | 753.6283 | 356532
|  | 06.05.24 | 19:01 | 06.05.24 | 19:53 | 0:52 | 0 | 28 | [5 empty] | At Baripada PG end: Directional O/C, Ir- 0.18kA, Iy- 0.32kA, Ib- 2.79kA
|  | 11.05.24 | 14:21 | 11.05.24 | 15:06 | 0:45 | 0 | 45 | [5 empty] | At Bangriposi end: Distance Protection, DP Relay O/C & E/F Trip, Zone-1, Dist.-5.6KM, Fault Loop: L1-E, IL1-2.34KA, IL2-0.22KA & IL3-0.33KA.
|  | 07.06.24 | 18:14 | 07.06.24 | 18:40 | 0:26 | 0 | 26 | [5 empty] | At Karanjia end: Distance Protection,Zone 1, B phase-N, Distance= 26.06kms, Ia=72.06A, Ib=102.5A, Ic=1.062kA
|  | 22.07.24 | 01:13 | 22.07.24 | 1:44 | 0:31 | 0 | 31 | [5 empty] | At Baripada PG end: Directional O/C, Ir-0.39kA, Iy-0.32kA, Ib-0.26kA
|  | 31.07.24 | 15:12 | 31.07.24 | 15:56 | 0:44 | 0 | 26 | [5 empty] | At Baripada PG end: O/C & E/F (Y-N), Zone 1, Dist- 10.12km, Iy- 5.6kA
|  | 14.08.24 | 16:38 | 14.08.24 | 16:47 | 0:09 | 0 | 9 | [5 empty] | At Karanjia end: R-B, Ir- 0.39kA, Iy- 0.29kA, Ib- 0.37kA, Dist- 50.2km At Rairangpur end: R-B, Zone 1, Ir- 1.529kA, Ib- 1.621kA, Dist-38.88km
|  | 27.08.24 | 19:47 | 27.08.24 | 20:01 | 0:14 | 0 | 14 | [5 empty] | At kAranjia end: Earth Fault,Dist pick up=L3-E, IL1=0.16kA, IL2=0.37kA, IL3=0.27kA, Dist-64.8km At Rairangpur end: IA=137.1A,Ib-378.3A,IC=1.907kA
|  | 17.08.24 | 00:42 | 17.08.24 | 0:57 | 0:15 | 0 | 15 | [5 empty] | At Bangriposi end: R-N, Zone 1, Dist- 13.3km, Ir- 3.06kA At Rairangpur end: R-N, Zone 1, Dist- 23.9km, Ir- 0.442kA
|  | 21.08.24 | 12:40 | 21.08.24 | 12:53 | 0:13 | 0 | 13 | [5 empty] | At kAranjia end: Dist Protection,Dist pick up=L2-E, IL1=0.28kA, IL2=0.28kA, IL3=0.35kA, Dist-30.2km
|  | 2024-10-09 | 16:39 | 2024-10-09 | 16:56 | 0:17 | 0 | 16 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=5ms, Distance pick up=L1-L2, IL1=0.33KA, IL2=0.27KA, IL3=0.35KA, Distance=59km At Rairangpur end: R-ph, Y-ph, Zone 1, Distance-27.23 KM, Ia=1.776KA, Ib=1.723 KA, Ic=342.9 A
|  | 18.11.24 | 19:09 | 18.11.24 | 19:20 | 0:11 | 0 | 11 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=ms, Distance pick up=L2-E, Rsec=4.96ohm, Xsec=8.39ohm, Rpri=14.88ohm, Xpri=25.18ohm, Distance=60.8kmrn At Rairangpur End: DP relay: Trip time=ms, Distance pick up=L2-E, IL1=283.6A, IL2=1.889KA, IL3=142.0A, Distance=16.07km
|  | 18.11.24 | 21:55 | 18.11.24 | 22:05 | 0:10 | 0 | 10 | [5 empty] | At Karanjia end: Distance Protection, DP relay: Trip time=ms, Distance pick up=L2-E, Rsec=4.96ohm, Xsec=8.39ohm, Rpri=14.88ohm, Xpri=25.18ohm, Distance=60.8km At Rairangpur End: DP relay: Trip time=ms, Distance pick up=L2-E, IL1=294.6A, IL2=1.841KA, IL3=136.3A, Distance=16.15km
|  | 25.01.25 | 03:06 | 25.01.25 | 3:36 | 0:30 | 0 | 30 | [5 empty] | At Rairangpur end: Distance Protection, Y-Phase ,Z1,Dist=13.64KM,IL1=278.3A,IL2=2.069KA,IL3=146.7A No relay Indication at Karanjia GSS
|  | 5.02.25 | 14:37 | 5.02.25 | 14:46 | 0:09 | 0 | 9 | [5 empty] | At Karanjia end: Remote End Tripping, no relay indication
|  | 19.02.25 | 14:40 | 19.02.25 | 16:07 | 1:27 | 1 | 27 | [5 empty] | Source failure from Karanjia end
|  | 18.03.25 | 4:58 | 18.03.25 | 5:19 | 0:21 | 0 | 21 | [5 empty] | At Bangiriposi end: Y-N, Zone 1, Dist- 21.4km, Iy- 2.57kA At Rairangpur end: Y-N, Zone 1, Dist- 20.48km, Iy- 0.395kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
415 | 132kV Karanjia-Turumunga |  |  |  |  | 0.019444 | 0 | 22 | [7 empty] | 35.443 | 8760 | 100% | 12.9958 | 310480.68
|  | 21.08.24 | 12:40 | 21.08.24 | 12:59 | 0:19 | 0 | 13 | [5 empty] | At kAranjia end: Dist Protection,Dist pick up=L2-E, IL1=0.12kA, IL2=1.17kA, IL3=0.16kA, Dist-25.1km At Rairangpur end: DIR E/F TRIP,IA=1.409kA,Ib-1.045kA,IC=428.7A
|  | 5.02.25 | 14:37 | 5.02.25 | 14:46 | 0:09 | 0 | 9 | [5 empty] | At Karanjia end: Remote End Tripping, no relay indication
416 | 132kV Turumunga-Palasponga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 111.125 | 8760 | 100% | 0 | 973455
417 | 132kV Kuchinda-SHIVA (Kutra) |  |  |  |  | 0.12569 | 1 | 27 | [7 empty] | 110 | 8760 | 99.98% | 159.5 | 963600
|  | 01.06.24 | 19:10 | 01.06.24 | 22:00 | 2:50 | 1 | 16 | [5 empty] | At Kuchinda end: Distance Protection, Zone-1, Tripped ph R, Fault Location=32.94km,Ir=1.278kA, Iy=52.35A, Ib=19.48A, fault resistance=8.860 ohm At Kutra end: E/F,O/C, Tripped phR, Fault distance=25.01km, Ir=2937.09A, Iy=77.35A, Ib=33.15A, In=2888.47A
|  | 05.06.24 | 11:36 | 05.06.24 | 11:47 | 0:11 | 0 | 11 | [5 empty] | At Kuchinda end: Distance Protection,Disntance trip ZONE-1, Tripped ph Y,rnFault distance=2.3km,rnIr=13.39A, Iy=4097.34A, Ib=57.46A, In=3975.79A
418 | 132kV SHIVA (Kutra)-Rajgangpur |  |  |  |  | 0.034722 | 0 | 15 | [7 empty] | 23 | 8760 | 100% | 5.75 | 201480
|  | 23.02.25 | 11:41 | 23.02.25 | 12:31 | 0:50 | 0 | 15 | [5 empty] | At Rajgangpur end: Earth Fault, BGT,ZONE-I,DP OPERATED, DISTANCE-3.84 KM ,IA=74 A,IB=6369 A,IC=106 A,IG=6548 A
419 | 132kV SHIVA (Kutra)-SHIVA Cement |  |  |  |  | 0.12569 | 1 | 56 | [7 empty] | 3.01 | 8760 | 99.98% | 5.8193 | 26367.6
|  | 01.06.24 | 19:10 | 01.06.24 | 22:00 | 2:50 | 1 | 45 | [5 empty] | At Kuchinda end: Distance Protection, Zone-1, Tripped ph R, Fault Location=32.94km,Ir=1.278kA, Iy=52.35A, Ib=19.48A, fault resistance=8.860 ohm At Kutra end: E/F,O/C, Tripped phR, Fault distance=25.01km, Ir=2937.09A, Iy=77.35A, Ib=33.15A, In=2888.47A
|  | 05.06.24 | 11:36 | 05.06.24 | 11:47 | 0:11 | 0 | 11 | [5 empty] | At Kuchinda end: Distance Protection,Disntance trip ZONE-1, Tripped ph Y,rnFault distance=2.3km,rnIr=13.39A, Iy=4097.34A, Ib=57.46A, In=3975.79A
420 | 132kV Kuchinda-Rajgangpur 'T' to Bamra RTSS |  |  |  |  | 0.24722 | 0 | 30 | [7 empty] | 10 | 8760 | 99.99% | 5 | 87600
|  | 05.06.24 | 04:12 | 05.06.24 | 10:08 | 5:56 | 0 | 30 | [5 empty] | D/P:-started phase-BC-N, tripped phase-ABC,FD-13.72KM, FD-304.1ms, Zone-4, IL1-111.7A, IL2-414.7A, IL3-431Amp
421 | 132kV Lapanga - Rengali RTSS |  |  |  |  | 1899-12-31 04:35 | 40 | 35 | [7 empty] | 12.31 | 8760 | 99.54% | 499.5808 | 107835.6
|  | 25.05.24 | 04:32 | 25.05.24 | 14:18 | 9:46 | 9 | 46 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L1-E ZONE-1 IL1-10.988KA IL2-0.4A IL3-2.8A DIST-4.988KM FAULT DURATION-96mSec MAIN-2 NO FAULT RECORDED
|  | 01.06.24 | 21:02 | 01.06.24 | 22:06 | 1:04 | 1 | 4 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L1-L3-E ZONE-1 IL1-7.479KA IL3-7.480KA DIST-11.52KM FD-500msec
|  | 13.06.24 | 19:40 | 13.06.24 | 20:03 | 0:23 | 0 | 23 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L1-L3 ZONE-1 IL1-6.4KA IL2-0KA IL3-6.47KA DIST-5.812KM
|  | 26.02.25 | 23:03 | 27.02.25 | 16:25 | 17:22 | 17 | 22 | [5 empty] | At Lapanga end: ZONE-1, DIST-3.454KM FD-96ms IR-1.3KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
422 | 132kV Machkund PH-Jaynagar |  |  |  |  | 0.14931 | 29 | 22 | [5 empty] | As per OERC Regulation 2014, outage hour affecting power evacuation is multiplied by factor 2. |  | 42.6 | 8760 | 99.66% | 1251.02 | 373176
|  | 08.04.24 | 16:20 | 08.04.24 | 16:48 | 0:28 | 0 | 56 | [5 empty] | Machkund supply failed at Machkund end.
|  | 20.04.24 | 13:24 | 20.04.24 | 14:21 | 0:57 | 1 | 54 | [5 empty] | Machkund supply failed at Machkund end.
|  | 24.04.24 | 07:11 | 24.04.24 | 8:12 | 1:01 | 0 | 42 | [5 empty] | Machkund supply failed at Machkund end.
|  | 25.04.24 | 8:21 | 25.04.24 | 8:33 | 0:12 | 0 | 24 | [5 empty] | Machkund supply failed at Machkund end.
|  | 20.04.24 | 13:24 | 20.04.24 | 14:21 | 0:57 | 1 | 54 | [5 empty] | Machkund supply failed at Machkund end.
|  | 05.05.24 | 21:44 | 05.05.24 | 21:55 | 0:11 | 0 | 22 | [5 empty] | Machkund supply failure
|  | 06.05.24 | 14:04 | 06.05.24 | 16:08 | 2:04 | 0 | 26 | [5 empty] | Machkund supply failure
|  | 16.05.24 | 05:37 | 16.05.24 | 07:20 | 1:43 | 0 | 28 | [5 empty] | At Podagada end: Remote End Tripping,Machkund feeder tripped at Machkund end.
|  | 18.05.24 | 19:33 | 19.05.24 | 6:43 | 11:10 | 0 | 20 | [5 empty] | Machkund supply failure
|  | 04.06.24 | 15:58 | 04.06.24 | 17:33 | 1:35 | 0 | 26 | [5 empty] | Machhkund supply failure
|  | 06.06.24 | 18:03 | 06.06.24 | 18:18 | 0:15 | 0 | 30 | [5 empty] | Machhkund supply failure
|  | 16.07.24 | 13:03 | 16.07.24 | 13:23 | 0:20 | 0 | 40 | [5 empty] | Machkund supply failure
|  | 20.07.24 | 08:49 | 20.07.24 | 9:18 | 0:29 | 0 | 58 | [5 empty] | Machkund supply failure
|  | 03.09.24 | 12:20 | 03.09.24 | 12:25 | 0:05 | 0 | 10 | [5 empty] | At Rayagada end: Remote End Tripping
|  | 09.09.24 | 10:34 | 09.09.24 | 10:45 | 0:11 | 0 | 22 | [5 empty] | At Rayagada end: Remote End Tripping,MACHAKUND P.H POWER SUPPLY FAIL
|  | 14.09.24 | 10:56 | 14.09.24 | 11:15 | 0:19 | 0 | 38 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 20.09.24 | 17:03 | 20.09.24 | 17:36 | 0:33 | 1 | 6 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 22.09.24 | 17:56 | 22.09.24 | 18:14 | 0:18 | 0 | 36 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 28.09.24 | 11:36 | 28.09.24 | 11:43 | 0:07 | 0 | 14 | [5 empty] | At Rayagada end: Remote End Tripping,MACHHAKUND P.H POWER SUPPLY FAIL
|  | 29.09.24 | 01:50 | 29.09.24 | 1:58 | 0:08 | 0 | 16 | [5 empty] | At Rayagada end: Remote End Tripping,132KV Machkund Power supply fail from Machkund P.H.
|  | 2024-10-12 | 17:11 | 2024-10-12 | 17:25 | 0:14 | 0 | 28 | [5 empty] | Supply failure from Machkund
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 40 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 16 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 54 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 44 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
|  | 14.11.24 | 10:47 | 14.11.24 | 11:16 | 0:29 | 0 | 58 | [5 empty] | Machkund supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
423 | 132kV Machkund PH- Machkund RTSS |  |  |  |  | 0 | 0 | 0 | [7 empty] | 107 | 8760 | 100% | 0 | 937320
424 | 132kV Mendhasal-Khurda |  |  |  |  | 0 | 0 | 0 | [7 empty] | 17.6 | 8760 | 100% | 0 | 154176
425 | 132kV Meramundali-BRG |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.55 | 8760 | 100% | 0 | 31098
426 | 132kV Meramundali- RML (DSP) |  |  |  |  | 0.11667 | 2 | 48 | [7 empty] | 10.53 | 8760 | 99.97% | 29.484 | 92242.8
|  | 31.01.25 | 14:03 | 31.01.25 | 16:17 | 2:14 | 2 | 14 | [5 empty] | At Meramundali end: Z1,Iy-9.2 kA,Ib-9.2 kA,7.4 KM At Rungta end: Z1,Iy-1.3 kA, Ib-1.3 kA, 1.27 KM
|  | 8.03.25 | 02:13 | 8.03.25 | 2:47 | 0:34 | 0 | 34 | [5 empty] | At Meramundali end: O/C, Ir- 0.216kA, Iy- 0.219kA, Ib- 0.215kA
427 | 132kV Meramundali-Chainpal Ckt-I |  |  |  |  | 0.093056 | 0 | 34 | [7 empty] | 1.728 | 8760 | 99.99% | 0.9792 | 15137.28
|  | 05.05.24 | 11:44 | 05.05.24 | 13:58 | 2:14 | 0 | 34 | [5 empty] | At Meramundali end: O/C, Iy- 10.57kA At Chainpal end: Zone 2, Dist- 7.63km, Iy- 3.6kA
428 | 132kV Meramundali-Chainpal Ckt-II |  |  |  |  | 0.091667 | 1 | 11 | [7 empty] | 1.728 | 8760 | 99.99% | 2.0448 | 15137.28
|  | 05.05.24 | 11:44 | 05.05.24 | 12:42 | 0:58 | 0 | 34 | [5 empty] | At Chainpal end: E/F, Iy- 4.5kA
|  | 19.09.24 | 10:48 | 19.09.24 | 12:02 | 1:14 | 0 | 37 | [5 empty] | At Chainpal end: Distance Protection,ZONE-1, L2-N, DISTANCE=5.12KM, IA=0.53kA, IB=0.39kA, IC=0.23kA At Meramundali end: Distance Protection,Remote End Tripping,Y-E, Z1, Iy-12.4 kA,Z1, Ir-533 A, Iy- 390 A, Ib- 230 A
429 | 132kV Meramundali-Dhenkanal |  |  |  |  | 0.15 | 13 | 29 | [7 empty] | 51.12 | 8760 | 99.85% | 689.268 | 447811.2
|  | 26.05.24 | 08:51 | 26.05.24 | 09:31 | 0:40 | 0 | 3 | [5 empty] | At Dhenkanal end: Distance Protection,Z-4, Distance=1.018Km, Ia=2.52KA, Ib=342.5A, Ic=587.5A No tripping at Meramundali end.
|  | 17.06.24 | 16:20 | 17.06.24 | 17:58 | 1:38 | 0 | 15 | [5 empty] | At Dhenkanal grid end-: DP relay operated with indication:- Z-2, Dist.=32.53 kM, Ir=1.255KA, Iy=7 A, Ib=7A At Meramundali grid end-: DP relay operated with indication- Z-1, R-N, Dist=6.75Km, Ir=7.97KA
|  | 13.07.24 | 12:56 | 13.07.24 | 13:13 | 0:17 | 0 | 10 | [5 empty] | At Dhenkanal end: Zone 1, Dist-16.72km, Ir- 1.826kA At Meramundali end: E/F (R-N), Zone 1, Ir- 2.537kA
|  | 11.01.25 | 18:08 | 11.01.25 | 18:43 | 0:35 | 0 | 35 | [5 empty] | At Meramundali end: R-N, Zone 1, Ir- 3.85kA, Dist- 24.6km At Dhenkanal end: R-N, Ir- 1.35kA, Zone 1, Dist- 16.65km
|  | 12.02.25 | 11:47 | 12.02.25 | 11:59 | 0:12 | 0 | 12 | [5 empty] | At Meramundali end: Distance ProtectionA/R unsucessful: Before A/R: Z1, Ir-3.4 KA, 24.82 KM After A/R: SOTF At Dhenkanal end: No tripping
|  | 22.03.25 | 19:18 | 22.03.25 | 19:32 | 0:14 | 0 | 14 | [5 empty] | At Dhenkanal end: Y-N, Iy- 2.193kA, Zone 1, Dist- 4.57km At Meramundali end: Y-N, Iy- 3.01kA, Zone 1, Dist- 37.6km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
430 | 132kV Meramundali-Kharagprasad Ckt-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
431 | 132kV Meramundali-Kharagprasad Ckt-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 5.517 | 8760 | 100% | 0 | 48328.92
432 | 132kV Meramundali- RML (FAD) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 7.468 | 8760 | 100% | 0 | 65419.68
433 | 132kV Meramundali-Khajuriakata |  |  |  |  | 0.0097222 | 0 | 14 | [7 empty] | 33.5 | 8760 | 100% | 7.8167 | 293460
|  | 21.07.24 | 5:36 | 21.07.24 | 5:46 | 0:10 | 0 | 10 | [5 empty] | At Meramundali end: R-N, Ir- 3.4kA, Dist- 31.99km, Zone 1
|  | 7.02.25 | 12:20 | 7.02.25 | 12:24 | 0:04 | 0 | 4 | [5 empty] | At Khajuriakata end: Rph-N ,Z-1,Ir-1.491kA,Dist-11.5kM At Meramundali end: R-N, Z1, 16.837 KM Ir -5.57 KA, In -5.08 KA
434 | 132KV Dhenkanal-Nuapatna-Khajuriakata "T" feeder |  |  |  |  | 0.072222 | 13 | 40 | [7 empty] | 2.4 | 8760 | 99.84% | 32.8 | 21024
|  | 06.05.24 | 17:27 | 06.05.24 | 17:47 | 0:20 | 0 | 20 | [5 empty] | At Khajuriakata end: B-N, Zone 1, Dist- 13.2km, Ib- 1.825kA At Dhenkanal end: B-N, Zone 1, Dist- 16.78km, Ib- 1.65kA
|  | 08.05.24 | 17:56 | 08.05.24 | 18:03 | 0:07 | 0 | 7 | [5 empty] | At Khajuriakata end: Distance Protection,Z-1,Bph-N,Ib-1.841KA,Dist-35.3km
|  | 26.05.24 | 08:51 | 26.05.24 | 08:54 | 0:03 | 0 | 3 | [5 empty] | At Khajuriakata end: O/C,Rph-Yph-Bph O/C
|  | 17.06.24 | 16:20 | 17.06.24 | 16:35 | 0:15 | 0 | 15 | [5 empty] | At Khajuriakata end: Over Current,Z-2,R-g, Dist-65.5 KM, Ir-1.262 KA
|  | 13.07.24 | 12:56 | 13.07.24 | 13:07 | 0:11 | 0 | 10 | [5 empty] | At Khajuriakata end: R-N, Zone 1, Ir-1.206kA,Dist-50.4km
|  | 18.07.24 | 19:50 | 18.07.24 | 19:57 | 0:07 | 0 | 7 | [5 empty] | At Khajuriakata end: O/C (R-N), Ir- 3.187kA, Zone 1, Dist- 2.7km
|  | 18.07.24 | 21:29 | 18.07.24 | 21:31 | 0:02 | 0 | 2 | [5 empty] | At Khajuriakata end: O/C (R-N), Ir- 3.19kA, Zone 1, Dist- 2.7km
|  | 11.01.25 | 18:08 | 11.01.25 | 18:30 | 0:22 | 0 | 22 | [5 empty] | At Khajuriakata end: R-N, Zone 1, Dist- 142.9km, Ir- 0.631kA No tripping at Dhenkanal end.
|  | 22.03.25 | 19:18 | 22.03.25 | 19:35 | 0:17 | 0 | 14 | [5 empty] | At Khajuriakata end: Y-N, Iy- 1.459kA, Zone 1, Dist- 40.9km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
435 | 132kV Khajuriakata-Nuapatna |  |  |  |  | 0 | 0 | 0 | [7 empty] | 83.99 | 8760 | 100% | 0 | 735752.4
436 | 132kV Nuapatna-Arati Steel |  |  |  |  | 0 | 0 | 0 | [7 empty] | 66.9 | 8760 | 100% | 0 | 586044
437 | 132kV Mohana-Digapahandi |  |  |  |  | 0.070833 | 13 | 42 | [7 empty] | 29.48 | 8760 | 99.84% | 403.876 | 258244.8
|  | 22.04.24 | 10:38 | 22.04.24 | 11:01 | 0:23 | 0 | 23 | [5 empty] | At Digapahandi end: E/F (B Ph), Ib- 1.04kA
|  | 29.04.24 | 16:06 | 29.04.24 | 16:16 | 0:10 | 0 | 10 | [5 empty] | At Mohana end: E/F (Y Ph), Zone 1, Dist- 40.79km, Iy- 1.612kA At Digapahandi end: E/F (Y Ph), Zone 1, Dist- 40.79km, Iy- 1.612kA
|  | 06.05.24 | 15:19 | 06.05.24 | 15:25 | 0:06 | 0 | 6 | [5 empty] | At Digapahandi end: Ir- 0.06kA, Iy- 0.7kA, Ib- 0.03kA
|  | 06.05.24 | 15:32 | 06.05.24 | 16:10 | 0:38 | 0 | 38 | [5 empty] | At Digapahandi end: Ir- 0.06kA, Iy- 0.8kA, Ib- 0.03kA
|  | 06.05.24 | 16:34 | 06.05.24 | 16:44 | 0:10 | 0 | 10 | [5 empty] | At Mohana end: Ir- 0.079kA, Iy- 0.493kA, Ib- 0.064kA, Dist- 59.5km
|  | 14.05.24 | 15:06 | 15.05.24 | 15:21 | 0:15 | 0 | 15 | [5 empty] | At Digapahandi end: Earth Fault,B/u relay optd. Ia-0.05A, Ib-0.54KA, Ic-0.03KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
438 | 132kV Muniguda-Bissamcuttack RTSS |  |  |  |  | 0.20486 | 16 | 55 | [7 empty] | 13.85 | 8760 | 99.81% | 234.2958 | 121326
|  | 01.04.24 | 17:53 | 01.04.24 | 17:54 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.266kA, Iy- 0.264kA
|  | 02.04.24 | 20:35 | 02.04.24 | 20:36 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.266kA, Iy- 0.264kA
|  | 04.04.24 | 20:31 | 04.04.24 | 20:32 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.27kA, Iy- 0.268kA
|  | 06.04.24 | 20:57 | 06.04.24 | 20:58 | 0:01 | 0 | 1 | [5 empty] | O/C, Iy- 0.266kA, Ib- 0.264kA
|  | 08.04.24 | 15:37 | 08.04.24 | 15:38 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.267kA, Iy- 0.264kA
|  | 08.04.24 | 15:55 | 08.04.24 | 15:56 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.266kA, Iy- 0.264kA
|  | 09.04.24 | 20:03 | 09.04.24 | 20:04 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.268kA, Iy- 0.265kA
|  | 21.04.24 | 17:27 | 21.04.24 | 17:34 | 0:07 | 0 | 7 | [5 empty] | E/F, Ir- 3.68kA
|  | 28.04.24 | 08:15 | 28.04.24 | 08:19 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 30.04.24 | 17:05 | 30.04.24 | 17:06 | 0:01 | 0 | 1 | [5 empty] | O/C, Ir- 0.264kA, Ib- 0.262kA
|  | 13.05.24 | 10:37 | 13.05.24 | 10:38 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=269 A
|  | 17.05.24 | 09:43 | 17.05.24 | 09:44 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=267 A
|  | 20.05.24 | 05:40 | 20.05.24 | 05:41 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=267 A
|  | 21.05.24 | 08:33 | 21.05.24 | 08:34 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=270 A
|  | 24.05.24 | 12:47 | 24.05.24 | 12:49 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C,I=265 A
|  | 23.05.24 | 12:02 | 23.05.24 | 12:03 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=267 A
|  | 26.05.24 | 05:38 | 26.05.24 | 05:40 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C,I= 263 A
|  | 28.05.24 | 09:06 | 28.05.24 | 09:08 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C,I=267 A
|  | 31.05.24 | 18:32 | 31.05.24 | 18:33 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,I=267.5 A
|  | 04.06.24 | 20:20 | 04.06.24 | 20:22 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current, Ir=264A, Iy=261A
|  | 05.06.24 | 18:18 | 05.06.24 | 18:20 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=264A
|  | 06.06.24 | 00:04 | 06.06.24 | 0:06 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end:Over Current,I=262A
|  | 06.06.24 | 16:25 | 06.06.24 | 16:26 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=264.8A
|  | 06.06.24 | 16:34 | 06.06.24 | 16:36 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end:Over Current,I=267.2A
|  | 07.06.24 | 12:34 | 07.06.24 | 12:36 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end:Over Current,I=266A
|  | 07.06.24 | 13:05 | 07.06.24 | 13:06 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=268.8A
|  | 07.06.24 | 15:07 | 07.06.24 | 15:08 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=266A
|  | 08.06.24 | 10:04 | 08.06.24 | 10:05 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end:Over Current,I=268A
|  | 08.06.24 | 11:50 | 08.06.24 | 11:51 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end:Over Current,I=267A
|  | 08.06.24 | 11:58 | 08.06.24 | 11:59 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=268A
|  | 08.06.24 | 12:04 | 08.06.24 | 12:06 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=267.6A
|  | 08.06.24 | 15:55 | 08.06.24 | 15:57 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=268A
|  | 08.06.24 | 16:11 | 08.06.24 | 16:13 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=267.6A
|  | 09.06.24 | 09:10 | 09.06.24 | 9:12 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=266A
|  | 09.06.24 | 10:04 | 09.06.24 | 10:05 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=267.6A
|  | 09.06.24 | 16:04 | 09.06.24 | 16:06 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=269.2A
|  | 09.06.24 | 23:35 | 09.06.24 | 23:37 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 10.06.24 | 00:16 | 10.06.24 | 0:18 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 10.06.24 | 01:33 | 10.06.24 | 1:35 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 14.06.24 | 12:43 | 14.06.24 | 12:45 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,I=267.4A
|  | 18.06.24 | 15:04 | 18.06.24 | 15:05 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,I=267.6A
|  | 19.06.24 | 11:37 | 19.06.24 | 11:39 | 0:02 | 0 | 2 | [5 empty] | O/C
|  | 19.06.24 | 11:46 | 19.06.24 | 11:47 | 0:01 | 0 | 1 | [5 empty] | O/C
|  | 07.07.24 | 08:22 | 07.07.24 | 8:23 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ia=268A
|  | 08.07.24 | 08:13 | 08.07.24 | 8:15 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,Ia=267 A, Ib=265 A
|  | 16.07.24 | 07:30 | 16.07.24 | 7:42 | 0:12 | 0 | 12 | [5 empty] | At Therubali end: E/F (Y-N), Zone 1, Dist- 3.79km, Iy- 6.6kA
|  | 16.07.24 | 08:53 | 16.07.24 | 8:54 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C, Ir- 0.263kA, Iy- 0.261kA
|  | 02.08.24 | 6:03 | 02.08.24 | 6:05 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C
|  | 02.08.24 | 06:11 | 02.08.24 | 6:12 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C
|  | 10.08.24 | 14:45 | 10.08.24 | 14:47 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C, Ir- 0.268kA
|  | 10.08.24 | 20:26 | 10.08.24 | 20:28 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C, Ir- 0.276kA
|  | 17.08.24 | 12:20 | 17.08.24 | 12:22 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C, Ir- 267.2A
|  | 22.08.24 | 07:11 | 22.08.24 | 7:12 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C,Ia=266.8 A, Ib-264 A
|  | 26.08.24 | 07:18 | 26.08.24 | 7:20 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C,Ia=265A, Ib-263 A
|  | 06.09.24 | 22:53 | 06.09.24 | 22:54 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ir=267A
|  | 07.09.24 | 18:01 | 07.09.24 | 18:02 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ir=267A
|  | 15.09.24 | 22:57 | 15.09.24 | 23:00 | 0:03 | 0 | 3 | [5 empty] | OC/EF
|  | 16.09.24 | 2:07 | 16.09.24 | 2:10 | 0:03 | 0 | 3 | [5 empty] | OC/EF
|  | 16.09.24 | 5:27 | 16.09.24 | 5:32 | 0:05 | 0 | 5 | [5 empty] | OC/EF
|  | 22.09.24 | 22:42 | 22.09.24 | 22:44 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,Ir=267.6A
|  | 24.09.24 | 196:44 | 24.09.24 | 17:20 | 0:36 | 0 | 36 | [5 empty] | OC/EF
|  | 2024-10-12 | 10:28 | 2024-10-12 | 10:29 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over CurrentIa= 265 A, Ib= 262 A
|  | 2024-10-24 | 19:08 | 2024-10-24 | 19:09 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over CurrentIa=267 A, Ib=265 A
|  | 2024-10-26 | 10:39 | 2024-10-26 | 10:40 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over CurrentIa=268 A, Ib=270 A
|  | 2024-10-27 | 18:46 | 2024-10-27 | 18:47 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over CurrentIa=265 A, Ib=263 A
|  | 2024-10-29 | 16:46 | 2024-10-29 | 16:47 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over CurrentIa=267 A, Ib=264 A
|  | 8.11.24 | 10:28 | 8.11.24 | 10:29 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current, Ia=266.8A, Ib=264.4A
|  | 9.11.24 | 10:05 | 9.11.24 | 10:07 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,Ia=267A Ib=265A
|  | 9.11.24 | 21:59 | 9.11.24 | 22:00 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ia=268 Ib=266
|  | 2024-11-13 | 0.82917 | 2024-11-13 | 0.83056 | 0:02 | 0 | 2 | [5 empty] | OC/EF
|  | 14.11.24 | 14:50 | 14.11.24 | 14:51 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ia=267A Ib=265A
|  | 18.11.24 | 18:16 | 18.11.24 | 18:24 | 0:08 | 0 | 8 | [5 empty] | OC/EF
|  | 20.11.24 | 15:37 | 20.11.24 | 15:38 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ia=272A Ib=270A
|  | 2024-11-22 | 12:00 | 2024-11-22 | 12:08 | 0:08 | 0 | 8 | [5 empty] | OC/EF
|  | 2024-11-29 | 14:40 | 2024-11-29 | 14:44 | 0:04 | 0 | 4 | [5 empty] | O/C, E/F
|  | 2024-11-29 | 15:00 | 2024-11-29 | 15:55 | 0:55 | 0 | 55 | [5 empty] | O/C, E/F
|  | 2024-11-29 | 17:12 | 2024-11-29 | 17:50 | 0:38 | 0 | 38 | [5 empty] | O/C, E/F
|  | 30.11.24 | 19:58 | 30.11.24 | 20:00 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,Ia=269A Ib=266A
|  | 15.12.24 | 18:18 | 15.12.24 | 18:20 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current,Ir=275.6 A, Iy=272.8 A
|  | 27.12.24 | 05:49 | 27.12.24 | 5:50 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current,Ir=269 A, Iy=266 A
|  | 1.01.25 | 14:45 | 1.01.25 | 14:47 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C
|  | 15.01.25 | 18:27 | 15.01.25 | 18:29 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: O/C
|  | 15.01.25 | 18:42 | 15.01.25 | 18:44 | 0:02 | 0 | 2
|  | 16.01.25 | 17:09 | 16.01.25 | 17:10 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: Over Current, Ir=271.6A
|  | 25.01.25 | 20:42 | 25.01.25 | 20:44 | 0:02 | 0 | 2 | [5 empty] | At Muniguda end: Over Current, Ir=269.6A
|  | 28.01.25 | 19:47 | 28.01.25 | 19:48 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C
|  | 28.01.25 | 19:54 | 28.01.25 | 19:55 | 0:01 | 0 | 1 | [5 empty] | At Muniguda end: O/C
|  | 25.03.25 | 09:20 | 25.03.25 | 9:24 | 0:04 | 0 | 4 | [5 empty] | At Muniguda end: O/C, If- 0.37kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
439 | 132kV Narendrapur-Berhampur Ckt -I |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 11.31 | 8760 | 100% | 1.508 | 99075.6
|  | 21.08.24 | 18:57 | 21.08.24 | 19:05 | 0:08 | 0 | 8 | [5 empty] | At Narendrapur end: Overcurrent & E/F Relay operated. Relay:- B-phase to E/F.IL3= 1.42kAmp
440 | 132kV Narendrapur-Berhampur Ckt - II |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 11.31 | 8760 | 100% | 1.508 | 99075.6
|  | 21.08.24 | 18:57 | 21.08.24 | 19:05 | 0:08 | 0 | 8 | [5 empty] | At Narendrapur end: Overcurrent & E/F Relay operated. Relay:- B-phase to E/F.IL3= 1.42kAmp
441 | 132kV Narendrapur-Chatrapur-I |  |  |  |  | 0.12083 | 0 | 30 | [7 empty] | 13.28 | 8760 | 99.99% | 6.64 | 116332.8
|  | 30.12.24 | 08:15 | 30.12.24 | 11:09 | 2:54 | 0 | 30 | [5 empty] | At Chatrapur end: A/R Lockout B-N, Zone 1, Dist- 0.81km, Ib- 5.706kA No tripping at Narendrapur end.
442 | 132kV Narendrapur-Chatrapur-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 13.28 | 8760 | 100% | 0 | 116332.8
443 | 132kV Narendrapur-Jagannathpur RTSS |  |  |  |  | 0.024306 | 12 | 35 | [7 empty] | 0.51 | 8760 | 99.86% | 6.4175 | 4467.6
|  | 31.05.24 | 18:27 | 31.05.24 | 18:47 | 0:20 | 0 | 20 | [5 empty] | At Narendrapur end: O/C,Tripped on R-Ph,B-Ph O/C,Ir-1KAmp,Ib-1Kmp
|  | 23.07.24 | 12:53 | 23.07.24 | 12:56 | 0:03 | 0 | 3 | [5 empty] | At Narendrapur end: O/C (R-B), Ir- 1.08kA, Ib- 1.08kA
|  | 31.07.24 | 17:28 | 31.07.24 | 17:32 | 0:04 | 0 | 4 | [5 empty] | At Narendrapur end: O/C, Ir- 1kA, Ib- 1kA
|  | 09.09.24 | 07:24 | 09.09.24 | 7:26 | 0:02 | 0 | 2 | [5 empty] | At Narendrapur end: Over Current,Tripped on R-ph & B-ph O/C (Ir=1.07KA,Ib=1.07KA)
|  | 27.01.25 | 11:59 | 27.01.25 | 12:05 | 0:06 | 0 | 6 | [5 empty] | At Narendrapur end: Over Current, Tripped on R-ph & B-ph O/C.(Ir=1.01KA,Ib=1.01KA)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
444 | 132kV NBVL-Hind Metals |  |  |  |  | 0 | 0 | 0 | [7 empty] | 1 | 8760 | 100% | 0 | 8760
445 | 132kV Nimapara-Konark |  |  |  |  | 0.057639 | 13 | 8 | [7 empty] | 19.91 | 8760 | 99.85% | 261.4847 | 174411.6
|  | 26.04.24 | 07:25 | 26.04.24 | 08:00 | 0:35 | 0 | 26 | [5 empty] | R-N, Zone 4, Dist- 0.674km, Ir- 1.77kA
|  | 17.06.24 | 16:29 | 17.06.24 | 16:59 | 0:30 | 0 | 30 | [5 empty] | At Chandaka end: Distance Protection,A-B-N, Z-1, D=9.49KM, 5.86KA, 5.576KA, 202.8A
|  | 04.07.24 | 17:10 | 04.07.24 | 17:28 | 0:18 | 0 | 12 | [5 empty] | At Chandaka end: Y-N, Zone 2, Dist- 52.67km, Iy- 1.872kA At Nimapara end: Y-N, Zone 4, Dist- 0.491km, Iy- 1.7kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
446 | 132kV Nimapara-Puri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 29.6 | 8760 | 100% | 0 | 259296
447 | 132kV Nimapara-Samagara |  |  |  |  | 0.39722 | 13 | 13 | [7 empty] | 27.6 | 8760 | 99.85% | 364.78 | 241776
|  | 06.04.24 | 11:09 | 06.04.24 | 13:21 | 2:12 | 0 | 28 | [5 empty] | At Nimapara end: B-N, Zone 1, Dist- 20.66km, Ib- 2.45kA At Samangara end: B-N, Zone 1, Dist- 12.4km, Ib- 0.5kA
|  | 26.04.24 | 07:26 | 26.04.24 | 07:45 | 0:19 | 0 | 19 | [5 empty] | Zone 1, Dist- 21.1km, Ir- 0.54kA
|  | 18.04.24 | 10:18 | 18.04.24 | 17:19 | 7:01 | 0 | 26 | [5 empty] | At Samangara end: Zone 1. Dist- 12.1km, Ib- 0.56kA At Nimapara end: B-N, Zone 1. Dist- 21.46km, Ib- 2.257kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
448 | 132kV ICCL- Mania |  |  |  |  | 0.59653 | 14 | 16 | [7 empty] | 18.32 | 8760 | 99.84% | 261.3653 | 160483.2
|  | 03.04.24 | 13:04 | 03.04.24 | 13:13 | 0:09 | 0 | 9 | [5 empty] | At Choudwar end: Zone 1, Ir- 0.501kA, Iy- 0.792kA, Ib- 4.86kA, Dist- 4.537km At Bidanasi end: E/F (Y-N), Zone 1, Dist- 7.44km, Iy- 5.9kA
|  | 19.04.24 | 18:23 | 19.04.24 | 20:54 | 2:31 | 0 | 26 | [5 empty] | Source failure
|  | 19.04.24 | 12:21 | 19.04.24 | 16:42 | 4:21 | 0 | 45 | [5 empty] | Remote end Tripping
|  | 19.05.24 | 16:22 | 19.05.24 | 17:11 | 0:49 | 0 | 15 | [5 empty] | At ICCL SW Station end: O/C,Earth Fault,Distance Protection,If=1.628kA,Y-phase,Zone-1 Dist-2.089km At Mania end: Remote End Tripping,No tripping at Mania
|  | 2024-10-18 | 13:00 | 2024-10-18 | 19:02 | 6:02 | 0 | 17 | [5 empty] | At Mania end: Remote end Tripping,no fault at Mania GSS
|  | 12.02.25 | 07:49 | 12.02.25 | 8:16 | 0:27 | 0 | 24 | [5 empty] | At Choudwar end: Over Current At TS Alloys: O/C , E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
449 | 132kV Mania- OCL |  |  |  |  | 0.82431 | 13 | 47 | [7 empty] | 4.063 | 8760 | 99.84% | 56.0017 | 35591.88
|  | 03.04.24 | 13:04 | 03.04.24 | 13:13 | 0:09 | 0 | 9 | [5 empty] | At Choudwar end: Zone 1, Ir- 0.501kA, Iy- 0.792kA, Ib- 4.86kA, Dist- 4.537km At Bidanasi end: E/F (Y-N), Zone 1, Dist- 7.44km, Iy- 5.9kA
|  | 19.04.24 | 18:23 | 19.04.24 | 18:59 | 0:36 | 0 | 26 | [5 empty] | Source failure
|  | 19.04.24 | 12:21 | 19.04.24 | 12:50 | 0:29 | 0 | 24 | [5 empty] | Remote end Tripping
|  | 28.07.24 | 17:45 | 28.07.24 | 18:15 | 18:15 | 0 | 30 | [5 empty] | Supply failure
|  | 2024-10-18 | 13:00 | 2024-10-18 | 13:18 | 0:18 | 0 | 18 | [5 empty] | At Mania end: Remote end Tripping, no fault at Mania GSS
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
450 | 132kV OCL-Salipur |  |  |  |  | 0.024306 | 0 | 10 | [7 empty] | 38.41 | 8760 | 100% | 6.4017 | 336471.6
|  | 08.05.24 | 16:37 | 08.05.24 | 17:12 | 0:35 | 0 | 10 | [5 empty] | At Salipur end: Distance Protection,Tripped on DP, Zone-1, distance=17.05km, IR=72.9A, IY=2.96kA, IB=2.91kA, IN=26A At Kendrapara end: Distance Protection,Tripped on DP, Zone-1, distance=17.05km, IR=72.9A, IY=2.96kA, IB=2.91kA, IN=26A
451 | 132kV ICCL-Bahugram |  |  |  |  | 1900-01-01 09:45 | 66 | 18 | [7 empty] | 21.14 | 8760 | 99.24% | 1401.582 | 185186.4
|  | 19.08.24 | 17:50 | 20.08.24 | 11:01 | 17:11 | 17 | 6 | [5 empty] | At ICCL SW Station end: Dist Protection,B-Ph, Zone-2,Dist-23km, If=3.4kA
|  | 2024-10-06 | 15:49 | 2024-10-07 | 1:38 | 9:49 | 9 | 49 | [5 empty] | At ICCL SW Station end: Distance Protection,Earth Fault,Over Current, Zone 1 ,13.5km , Top conductor,B-Ph e/f, IF=4.68KA (IL1=0.21KA, IL2=0.22KA, IL3=4.68KA)
|  | 2024-10-26 | 23:47 | 2024-10-27 | 15:42 | 15:55 | 15 | 55 | [5 empty] | At ICCL SW Station end: Distance Protection,Earth Fault,Over CurrentZone -1, Dist- 17.1 km,B-ph E/F,B-ph O/C, If = 3.84KA (IL1= 0.19KA, IL2=0.38KA, IL3=3.84KA)
|  | 21.02.25 | 17:47 | 21.02.25 | 22:24 | 4:37 | 1 | 15 | [5 empty] | At ICCL end: O/C (R Ph), Zone 1, Dist- 14.2km, Ir- 4.02kA At Bahugram end: Zone 1, Dist- 6.22km, Ir-0.162kA, Iy- 0.16kA, Ib- 0.162kA
|  | 19.02.25 | 03:10 | 19.02.25 | 13:23 | 10:13 | 10 | 13 | [5 empty] | At Bahugram end: Distance Protection,Remote End TrippingIa=158.8A,Ib=189.6A,Ic=170.5A, Zone-1,Dist=10.95km At ICCL SW Station end: Distance Protection,Over Current,Ia=0.18kA,Ib=0.21kA,Ic=5.83kA,Zone-1,Dist=9.6km
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
452 | 132kV Bahugram-Salipur |  |  |  |  | 0.7125 | 17 | 6 | [7 empty] | 10.83 | 8760 | 99.8% | 185.193 | 94870.8
|  | 19.08.24 | 17:50 | 20.08.24 | 10:56 | 17:06 | 17 | 6 | [5 empty] | At Salipur end: Dist Protection,C N, Zone 1, Frequency: 49.87 Hz, Fault Duration: 78.54 ms, Relay Trip Time: 80.21 ms, Fault loc.: 1.25 km, Ia = 82.9 A, Ib = 219.5 A, Ic = 1.6 kA, Van = 84.3 kV, Vbn = 83.1 kV, Vcn = 5.8 kV, Fault Resistance = 3.9 Ohm
453 | 132kV Paradeep-Tirtol |  |  |  |  | 0.0875 | 13 | 11 | [7 empty] | 38.43 | 8760 | 99.85% | 506.6355 | 336646.8
|  | 16.04.24 | 12:51 | 16.04.24 | 13:17 | 0:26 | 0 | 26 | [5 empty] | At Paradeep end: O/C (R & B ph), Zone 2, Dist- 35.4km, Ir- 2.2kA, Ib- 2.5kA No tripping at Tirtol end
|  | 20.06.24 | 14:12 | 20.06.24 | 14:20 | 0:08 | 0 | 8 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir=205.576 A , Iy = 3.26 kA , Ib= 116.531 A,Y-Ph to G, Zone -I, Dist-17.7 kms At Tirtol end: Distance Protection,ZONE-1, B-N, IA=208.8A, IB=148.0A, IC=127.0A, FAULT DISTANCE- 9.306 KMS.
|  | 19.07.24 | 17:28 | 19.07.24 | 17:40 | 0:12 | 0 | 12 | [5 empty] | At Tirtol end: Zone 1, Y-N, Ir- 0.279kA, Iy- 0.179kA, Ib- 0.127kA, Dist- 16.53km At Paradeep end: E/F (Y-N), Zone 1, Dist- 13.4km, Iy- 4.6kA
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
454 | 132kV Tirtol- Jagatsinghpur |  |  |  |  | 0.022917 | 0 | 30 | [7 empty] | 29.26 | 8760 | 99.99% | 14.63 | 256317.6
|  | 16.04.24 | 12:51 | 16.04.24 | 13:24 | 0:33 | 0 | 30 | [5 empty] | At Paradeep end: O/C (R & B ph), Zone 2, Dist- 35.4km, Ir- 2.2kA, Ib- 2.5kA No tripping at Tirtol end
455 | 132kVJagatsinghpur-Gorakhnath RTSS |  |  |  |  | 0.083333 | 0 | 42 | [7 empty] | 16.53 | 8760 | 99.99% | 11.571 | 144802.8
|  | 16.04.24 | 12:51 | 16.04.24 | 13:24 | 0:33 | 0 | 30 | [5 empty] | At Paradeep end: O/C (R & B ph), Zone 2, Dist- 35.4km, Ir- 2.2kA, Ib- 2.5kA No tripping at Tirtol end
|  | 2024-10-07 | 14:59 | 2024-10-07 | 16:26 | 1:27 | 0 | 12 | [5 empty] | Tripped on O/C in Y-ph & E/F. Indications on DP Relay: Trip in Zone 2, Fault Location: 32.35km, Current: IR=288.4A, IY=3.459kA, IB=3.345kA, Van=74.12kV, Vbn=54.44kV, Vcn=52.83kV
456 | 132kV Paradeep- Siju RTSS |  |  |  |  | 0.13472 | 0 | 30 | [7 empty] | 5.081 | 8760 | 99.99% | 2.5405 | 44509.56
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
457 | 132kV Paradeep- IFFCO - I |  |  |  |  | 0.079167 | 0 | 5 | [7 empty] | 7.171 | 8760 | 100% | 0.59758 | 62817.96
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
458 | 132kV Paradeep- IFFCO - II |  |  |  |  | 0.13472 | 0 | 30 | [7 empty] | 7.171 | 8760 | 99.99% | 3.5855 | 62817.96
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
459 | 132kV Paradeep-PPL-I |  |  |  |  | 0.13472 | 0 | 30 | [7 empty] | 6.2 | 8760 | 99.99% | 3.1 | 54312
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
460 | 132kV Paradeep-PPL-II |  |  |  |  | 0.13472 | 0 | 30 | [7 empty] | 6.2 | 8760 | 99.99% | 3.1 | 54312
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
461 | 132kV Paradeep-PPT-I |  |  |  |  | 0.17083 | 13 | 22 | [7 empty] | 7.65 | 8760 | 99.85% | 102.255 | 67014
|  | 10.05.24 | 15:36 | 10.05.24 | 16:01 | 0:25 | 0 | 25 | [5 empty] | At Paradeep end: Earth Fault,Tripped on O/C and E/F on R-Phase , Ir-5.21KAmp
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
|  | 25.03.25 | 9:37 | 25.03.25 | 10:04 | 0:27 | 0 | 27 | [5 empty] | O/C (R-Y-B), Ir- 1.17kA, Iy- 1.2kA, Ib- 1.23kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
462 | 132kV Paradeep-PPT-II |  |  |  |  | 0.47639 | 13 | 22 | [7 empty] | 7.65 | 8760 | 99.85% | 102.255 | 67014
|  | 10.05.24 | 15:36 | 10.05.24 | 17:27 | 1:51 | 0 | 25 | [5 empty] | At Paradeep end: Earth Fault,Tripped on E/F on B-Phase and O/C, Ib- 10.26KAmp
|  | 20.06.24 | 12:41 | 20.06.24 | 14:35 | 1:54 | 0 | 5 | [5 empty] | At Paradeep end: Over Current,Earth Fault,Ir= 4.14 kA , Iy= 385 A , Ib= 676.4 A,R-Ph to G ,Zone-I, Dist-11.57 kms
|  | 12.08.24 | 15:56 | 12.08.24 | 17:16 | 1:20 | 0 | 25 | [5 empty] | At New Duburi end: O/C (Y-B Ph), Zone 4, Dist- 2.5km, Ir- 0.42kA, Iy- 0.78kA, Ib- 0.82kA
|  | 25.03.25 | 9:45 | 25.03.25 | 16:06 | 6:21 | 0 | 27 | [5 empty] | O/C (R-Y-B), Ir- 6.21kA, Iy- 5.28kA, Ib- 5.86kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
463 | 132kV Patnagarh-Padampur - I |  |  |  |  | 0.56806 | 16 | 14 | [7 empty] | 44.24 | 8760 | 99.81% | 718.1627 | 387542.4
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 19.06.24 | 16:47 | 19.06.24 | 20:36 | 3:49 | 0 | 44 | [5 empty] | At Padampur end: Earth Fault,Tripped due to jumper snapped at loc 156
|  | 20.07.24 | 21:08 | 20.07.24 | 21:32 | 0:24 | 0 | 24 | [5 empty] | At Padampur end: R-N, Ir- 0.315kA, Iy- 0.192kA, Ib- 0.481kA, Zone 1, Dist- 32.39km
|  | 18.08.24 | 07:01 | 18.08.24 | 7:32 | 0:31 | 0 | 31 | [5 empty] | At Padampur end: R-N, Ir- 1.597kA, Dist- 3.07km, Zone 4
|  | 19.08.24 | 11:27 | 19.08.24 | 11:41 | 0:14 | 0 | 14 | [5 empty] | At Padampur end: Dist Protection,PH-AB,Ia-1.986kA, Ib-1.760kA,Ic-321.4A, Dist:-824.2Meter, Zone4,
|  | 24.08.24 | 01:51 | 24.08.24 | 2:09 | 0:18 | 0 | 18 | [5 empty] | At Padampur end: AN,Ia-315.2A,Ib-168.3A,Ic-427A,Zone 1,Dist-35.64km,Zone1
|  | 27.08.24 | 19:19 | 27.08.24 | 19:55 | 0:36 | 0 | 36 | [5 empty] | At Padampur end: Dist Protection,PH-AN,Ia-257A,Ib-245A,Ic-504A,Zone 2
|  | 15.01.25 | 7:03 | 15.01.25 | 13:50 | 6:47 | 0 | 35 | [5 empty] | At Padampur end: R-N, Ir- 0.44kA, Iy- 0.342kA, Ib- 0.627kA, Zone 1, Dist- 2.3km
|  | 8.02.25 | 16:28 | 8.02.25 | 16:33 | 0:05 | 0 | 5 | [5 empty] | At Bolangir New end: Over CurrentIa=389A, Ib=400A, Ic=396A
|  | 22.02.25 | 17:50 | 22.02.25 | 18:02 | 0:12 | 0 | 12 | [5 empty] | Source failure
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
464 | 132kV Patnagarh-Padampur - II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 44.64 | 180 | 100% | 0 | 8035.2
465 | 132kV Padampur-Padampur Solar |  |  |  |  | 0.20208 | 13 | 23 | [7 empty] | 10.5 | 8760 | 99.85% | 140.525 | 91980
|  | 25.04.24 | 10:44 | 25.04.24 | 11:04 | 0:20 | 0 | 4 | [5 empty] | Tripped due to overloading from Kesinga
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 19.06.24 | 16:47 | 19.06.24 | 20:36 | 3:49 | 0 | 44 | [5 empty] | At Padampur end: Earth Fault,Tripped due to jumper snapped at loc 156
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
466 | 132kV Padampur-Nuapada-I |  |  |  |  | 1899-12-31 14:51 | 17 | 47 | [7 empty] | 68 | 8760 | 99.8% | 1209.2667 | 595680
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | Tripped due to overloading from Kesinga
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 07.06.24 | 17:59 | 07.06.24 | 18:09 | 0:10 | 0 | 10 | [5 empty] | At Nuapada end: Distance Protection,Distance protection operated, zone-1,distance:50kM, Ia:1.192Amp, Ib:: 878 Amp, Ic: 953.5Amp,
|  | 26.06.24 | 20:44 | 26.06.24 | 20:58 | 0:14 | 0 | 14 | [5 empty] | At Padampur end: Distance Protection,Tripped due to Distance protection operated. Zone2, 77.53KM Ia=87.75A, Ib=60.42A, Ic=99.64A At Nuapada end: Earth Fault,tripped on E/F, Started phase:N, Tripped phase:N, Ia=94.09A, Ib=57.09A Ic=130.9A,In=231.5A
|  | 19.06.24 | 16:47 | 19.06.24 | 20:36 | 3:49 | 0 | 21 | [5 empty] | At Padampur end: Earth Fault,Tripped due to jumper snapped at loc 156
|  | 20.07.24 | 21:08 | 20.07.24 | 21:32 | 0:24 | 0 | 24 | [5 empty] | At Padampur end: R-N, Ir- 0.315kA, Iy- 0.192kA, Ib- 0.481kA, Zone 1, Dist- 32.39km
|  | 18.08.24 | 07:01 | 18.08.24 | 7:40 | 7:40 | 0 | 23 | [5 empty] | At Padampur end: R-N, Ir- 1.99kA, Zone 1 At Nuapada end: R-N, Zone 1, Dist- 51.38km, Ir- 0.118kA
|  | 19.08.24 | 11:27 | 19.08.24 | 11:42 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,SOURCE FAILURE
|  | 24.08.24 | 01:51 | 24.08.24 | 2:09 | 0:18 | 0 | 18 | [5 empty] | At Nuapada end: Remote End Tripping
|  | 27.08.24 | 19:19 | 27.08.24 | 19:55 | 0:36 | 0 | 10 | [5 empty] | At Padampur end: Dist Protection,PH-AN,Ia-257A,Ib-245A,Ic-504A,Zone 2
|  | 29.08.24 | 09:23 | 29.08.24 | 9:34 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Dist Protection,Zone 1, Dist 47.24km, Started ph B,C tripped ph ABC Ia 149.7A, Ib 1.29kA Ic 1.61LA
|  | 20.08.24 | 03:13 | 20.08.24 | 3:25 | 0:12 | 0 | 12 | [5 empty] | At Nuapada end: Dist Protection,Zone 1, started phase A,N, tripped ph ABC, Dist 28.10 km Ia 155A Ib 110.8A Ic 212A At Padampur end: Dist Protection,Zone 1, started phase A,N, tripped ph ABC, Dist 28.10 km Ia 155A Ib 110.8A Ic 212A
|  | 30.08.24 | 22:29 | 30.08.24 | 22:55 | 0:26 | 0 | 5 | [5 empty] | At Padampur end: Dist Protection,Zone 1, started ph BN, tripped Ph ABC, Ia 412.7A, Ib 172.4A, Ic 122.6A At Nuapada end: Dist Protection,Zone 1, started ph BN, tripped Ph ABC, Ia 412.7A, Ib 172.4A, Ic 122.6A
|  | 25.09.24 | 04:44 | 25.09.24 | 4:59 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,sousrece
|  | 24.09.24 | 17:55 | 24.09.24 | 18:02 | 0:07 | 0 | 7 | [5 empty] | At Nuapada end: Earth Fault,started ph N, Tripped phase N, Ia 409 A, Ib 178A, Ic 121 A, IN 653 A
|  | 24.09.24 | 18:03 | 25.09.24 | 10:20 | 16:17 | 1 | 4 | [5 empty] | At Nuapada end: Earth Fault,Started Ph N, Tripped Ph N, IA 97A, IB 103A, IC 35A, IN 50 A
|  | 15.01.25 | 7:03 | 15.01.25 | 13:50 | 6:47 | 0 | 35 | [5 empty] | At Padampur end: R-N, Ir- 0.44kA, Iy- 0.342kA, Ib- 0.627kA, Zone 1, Dist- 2.3km
|  | 17.01.25 | 10:43 | 17.01.25 | 10:51 | 0:08 | 0 | 8 | [5 empty] | At Padampur end: Tripped due to O/C. Tripped Phase:A, Ia=400.2A, Ib=372.2A, Ic=295.1A,In= 9.9A.
|  | 8.02.25 | 16:28 | 8.02.25 | 16:33 | 0:05 | 0 | 5 | [5 empty] | At Bolangir New end: Over CurrentIa=389A, Ib=400A, Ic=396A
|  | 22.02.25 | 17:50 | 22.02.25 | 18:02 | 0:12 | 0 | 12 | [5 empty] | Source failure
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
467 | 132kV Padampur-Nuapada-II |  |  |  |  | 0.89861 | 16 | 4 | [7 empty] | 68 | 8760 | 99.82% | 1092.5333 | 595680
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | Tripped due to overloading from Kesinga
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 17 | [5 empty] | Remote end Tripping
|  | 07.06.24 | 17:59 | 07.06.24 | 18:09 | 0:10 | 0 | 10 | [5 empty] | At Nuapada end: Distance Protection,Distance protection operated, zone-1,distance:50kM, Ia:1.192Amp, Ib:: 878 Amp, Ic: 953.5Amp,
|  | 26.06.24 | 20:44 | 26.06.24 | 20:58 | 0:14 | 0 | 14 | [5 empty] | At Padampur end: Distance Protection,Tripped due to Distance protection operated. Zone2, 77.53KM Ia=87.75A, Ib=60.42A, Ic=99.64A At Nuapada end: Earth Fault,tripped on E/F, Started phase:N, Tripped phase:N, Ia=94.09A, Ib=57.09A Ic=130.9A,In=231.5A
|  | 19.06.24 | 16:47 | 19.06.24 | 20:36 | 3:49 | 0 | 21 | [5 empty] | At Padampur end: Earth Fault,Tripped due to jumper snapped at loc 156
|  | 20.07.24 | 21:08 | 20.07.24 | 21:32 | 0:24 | 0 | 24 | [5 empty] | At Padampur end: R-N, Ir- 0.315kA, Iy- 0.192kA, Ib- 0.481kA, Zone 1, Dist- 32.39km
|  | 01.08.24 | 20:34 | 01.08.24 | 20:52 | 0:18 | 0 | 18 | [5 empty] | At Nuapada end: O/C, Ir- 0.528kA, Ib- 0.53kA
|  | 18.08.24 | 07:01 | 18.08.24 | 7:40 | 7:40 | 0 | 23 | [5 empty] | At Padampur end: R-N, Ir- 1.99kA, Zone 1 At Nuapada end: R-N, Zone 1, Dist- 51.38km, Ir- 0.118kA
|  | 19.08.24 | 11:27 | 19.08.24 | 11:42 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,SOURCE FAILURE
|  | 27.08.24 | 19:19 | 27.08.24 | 19:55 | 0:36 | 0 | 10 | [5 empty] | At Padampur end: Dist Protection,PH-AN,Ia-257A,Ib-245A,Ic-504A,Zone 2
|  | 29.08.24 | 09:23 | 29.08.24 | 9:34 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Dist Protection,Zone 1, Dist 47.24km, Started ph B,C tripped ph ABC Ia 149.7A, Ib 1.29kA Ic 1.61LA
|  | 15.01.25 | 7:03 | 15.01.25 | 13:50 | 6:47 | 0 | 35 | [5 empty] | At Padampur end: R-N, Ir- 0.44kA, Iy- 0.342kA, Ib- 0.627kA, Zone 1, Dist- 2.3km
|  | 17.01.25 | 10:43 | 17.01.25 | 10:51 | 0:08 | 0 | 8 | [5 empty] | At Padampur end: Tripped due to O/C. Tripped Phase:A, Ia=400.2A, Ib=372.2A, Ic=295.1A,In= 9.9A.
|  | 8.02.25 | 16:28 | 8.02.25 | 16:33 | 0:05 | 0 | 5 | [5 empty] | At Bolangir New end: Over CurrentIa=389A, Ib=400A, Ic=396A
|  | 22.02.25 | 17:50 | 22.02.25 | 18:02 | 0:12 | 0 | 12 | [5 empty] | Source failure
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
468 | 132 kV Purusottampur-Chatrapur |  |  |  |  | 0.011111 | 0 | 16 | [7 empty] | 15.45 | 8760 | 100% | 4.12 | 135342
|  | 19.06.24 | 11:16 | 19.06.24 | 11:32 | 0:16 | 0 | 16 | [5 empty] | At Chatrapur end: Over Current,B/U Relay O/C(R phase),E/F M/R Operated IR=1.44KA,IY=0.09KA,IB=0.12KA
469 | 132kV Rairakhole- Rairakhole RTSS |  |  |  |  | 0.92153 | 15 | 14 | [7 empty] | 3.5 | 8760 | 99.83% | 53.3167 | 30660
|  | 05.04.24 | 18:29 | 05.04.24 | 19:08 | 0:39 | 0 | 10 | [5 empty] | At Maneswar end: Zone 1, Dist- 14.9km, Ir- 2.98kA
|  | 20.05.24 | 21:21 | 20.05.24 | 21:52 | 0:31 | 0 | 20 | [5 empty] | At Rairakhol end: Distance Protection,Zone- Z1, 2.11 KM, R-phase to Earth, Ir-6 KA
|  | 31.05.24 | 13:30 | 31.05.24 | 18:58 | 5:28 | 0 | 25 | [5 empty] | At Rairakhol end: Distance Protection,Zone-1 , Distance -39.9KM, Current IL1-0.37KA, IL2-1.8KA, IL3-0.22KA, faukt loop- IL2-E At Maneswar end: Distance Protection,Y ph, Z-1, Distance=39.9 km, pu time- 50 ms, trip time - 1 ms . Ir= 0.37 kA, Iy= 1.8 kA, Ib=0.22 kA
|  | 01.06.24 | 13:53 | 01.06.24 | 19:15 | 5:22 | 0 | 7 | [5 empty] | At Rairakhol end: Distance Protection, distance-43.3 km, Ir=0.35 kA,Iy=1.67 kA, Ib=0.22 kA, distance pick up - 50 ms
|  | 01.06.24 | 19:56 | 01.06.24 | 20:06 | 0:10 | 0 | 10 | [5 empty] | At Rairakhol end: Over Current,Directional over current & earth fault operated, Trip A/B , LBB initiated, Ir=0.54 kA, Iy=0.54 kA, Ib=0.52 kA
|  | 01.06.24 | 20:47 | 01.06.24 | 23:22 | 2:35 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance-17.8 km, trip time-0 ms, Y & B ph , pu time - 53 ms, LE 2-3. Ir=0.22 kA, Iy=3.16 kA, Ib=3.39 kA
|  | 28.08.24 | 19:51 | 28.08.24 | 20:30 | 0:39 | 0 | 31 | [5 empty] | At Rairakhol end: Remote End Tripping,Incoming power supply to Boinda from Angul grid end failed.
|  | 17.09.24 | 0:33 | 17.09.24 | 0:48 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection,Distance -24.38KM, Current IL1-227.1A, IL2-138.2A, IL3-268.3A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 51.69ms At Boinda end: Distance -21.877KM, Current IL1-1739.51A, IL2-124.43A, IL3-266.12A, fault loop- IL1-E , Zone-1, General trip
|  | 25.09.24 | 03:31 | 25.09.24 | 3:43 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection, Distance -25.61KM, Current IL1-170.7A, IL2-161.7A, IL3-297.7A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 46.70ms At Boinda end: Distance -21.845KM, Current IL1-1778.20A, IL2-150.45A, IL3-295.88A, fault loop- IL1-E , Zone-1, General trip
|  | 09.09.24 | 20:45 | 09.09.24 | 20:57 | 0:12 | 0 | 12 | [5 empty] | At Rairakhol end: Distance Protection At Boinda end: Distance -30.979KM, Current IL1-174.76A, IL2-1194.06A, IL3-49.11A, fault loop- IL2-E , Zone-1, General trip
|  | 21.09.24 | 04:17 | 21.09.24 | 4:32 | 0:15 | 0 | 15 | [5 empty] | At Rairakhol end: Distance Protection, Distance -27.43KM, Current IL1-281.4A, IL2-88.38A, IL3-272.8A, fault loop- IL1-E , Zone-1, General trip, Fault duration- 50.01ms At Boinda end: Distance -21.456KM, Current IL1-1725.99A, IL2-70.21A, IL3-260A, fault loop- IL1-E , Zone-1, General trip
|  | 2024-10-03 | 02:53 | 2024-10-03 | 3:07 | 0:14 | 0 | 14 | [5 empty] | At Rairakhol end: B-N, Zone 1, Dist- 28.05km, Ib- 0.123kA At Boinda end: B-N, Zone 1, Dist- 21.68km, Ib- 1.63kA
|  | 8.01.25 | 07:13 | 8.01.25 | 12:48 | 5:35 | 0 | 11 | [5 empty] | At Boinda end: Zone 1, Dist- 12.31km, Y-N, Iy- 1.26kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
470 | 132kV Rajgangpur-OCL |  |  |  |  | 0.16875 | 13 | 29 | [7 empty] | 0.5 | 8760 | 99.85% | 6.7417 | 4380
|  | 15.06.24 | 22:25 | 16.06.24 | 1:25 | 3:00 | 0 | 26 | [5 empty] | At Rajgangpur end: Earth Fault,R-PH,Z1 PU/Z1 TRIP, ZONE-1, IR=1.178 KA, IY=164.7 A, IB=301.6 A, DISTANCE=0 KM, FD=61.81 ms,RTT=80.19 ms MASTER TRIP RELAY OPERATED At Bamra end: Over Current,Fault type=O/C , R-Y-B-phase operated, F.D- 611ms,RTT=541ms, Ia= 2.193KA, Ib= 145.5A, Ic= 292.9A,
|  | 11.07.24 | 15:19 | 11.07.24 | 15:36 | 0:17 | 0 | 17 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.389kA, Iy- 0.401kA, Ib- 0.315kA
|  | 11.07.24 | 17:02 | 11.07.24 | 17:14 | 0:12 | 0 | 12 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.399kA, Iy- 0.392kA, Ib- 0.33kA
|  | 31.01.25 | 12:22 | 31.01.25 | 12:33 | 0:11 | 0 | 11 | [5 empty] | At Rajgangpur end: Over Current, RTT= 640 s, IA=201 A,IB=201 A,IC=217 A,IG=2 A rn
|  | 16.02.25 | 18:17 | 16.02.25 | 18:30 | 0:13 | 0 | 13 | [5 empty] | At Rajgangpur end: O/C, IA=251 A,IB=254 A,IC=252 A
|  | 26.03.25 | 15:16 | 26.03.25 | 15:26 | 0:10 | 0 | 10 | [5 empty] | At Rairakhol end: Remote End Tripping
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
471 | 132kV Rajgangapur-Rajgangapur RTSS Ckt-I |  |  |  |  | 0.15347 | 13 | 7 | [7 empty] | 4.2 | 8760 | 99.85% | 55.09 | 36792
|  | 15.06.24 | 22:25 | 16.06.24 | 1:25 | 3:00 | 0 | 26 | [5 empty] | At Rajgangpur end: Earth Fault,R-PH,Z1 PU/Z1 TRIP, ZONE-1, IR=1.178 KA, IY=164.7 A, IB=301.6 A, DISTANCE=0 KM, FD=61.81 ms,RTT=80.19 ms MASTER TRIP RELAY OPERATED At Bamra end: Over Current,Fault type=O/C , R-Y-B-phase operated, F.D- 611ms,RTT=541ms, Ia= 2.193KA, Ib= 145.5A, Ic= 292.9A,
|  | 11.07.24 | 15:19 | 11.07.24 | 15:36 | 0:17 | 0 | 17 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.389kA, Iy- 0.401kA, Ib- 0.315kA
|  | 11.07.24 | 17:02 | 11.07.24 | 17:14 | 0:12 | 0 | 12 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.399kA, Iy- 0.392kA, Ib- 0.33kA
|  | 9.12.24 | 07:30 | 9.12.24 | 7:42 | 0:12 | 0 | 12 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
472 | 132kV Rajgangapur-Rajgangapur RTSS Ckt -II |  |  |  |  | 1899-12-31 20:51 | 65 | 55 | [7 empty] | 4.2 | 8760 | 99.25% | 276.85 | 36792
|  | 15.06.24 | 22:25 | 16.06.24 | 1:25 | 3:00 | 0 | 26 | [5 empty] | At Rajgangpur end: Earth Fault,R-PH,Z1 PU/Z1 TRIP, ZONE-1, IR=1.178 KA, IY=164.7 A, IB=301.6 A, DISTANCE=0 KM, FD=61.81 ms,RTT=80.19 ms MASTER TRIP RELAY OPERATED At Bamra end: Over Current,Fault type=O/C , R-Y-B-phase operated, F.D- 611ms,RTT=541ms, Ia= 2.193KA, Ib= 145.5A, Ic= 292.9A,
|  | 11.07.24 | 15:19 | 11.07.24 | 15:36 | 0:17 | 0 | 17 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.389kA, Iy- 0.401kA, Ib- 0.315kA
|  | 11.07.24 | 17:02 | 11.07.24 | 17:14 | 0:12 | 0 | 12 | [5 empty] | At Bamra end: O/C (R-Y-B), Ir- 0.399kA, Iy- 0.392kA, Ib- 0.33kA
|  | 9.12.24 | 07:30 | 9.12.24 | 7:42 | 0:12 | 0 | 12 | [5 empty] | O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
473 | 132kV Rajgangpur-Rourkela |  |  |  |  | 0 | 0 | 0 | [7 empty] | 27.1 | 8760 | 100% | 0 | 237396
474 | 132kV Ranasinghpur-Badagada (Kesura) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 34.23 | 8760 | 100% | 0 | 299854.8
475 | 132kV TS Alloys-Choudwar |  |  |  |  | 1899-12-31 16:28 | 52 | 15 | [7 empty] | 22.6 | 8760 | 99.4% | 1180.85 | 197976
|  | 07.04.24 | 18:30 | 07.04.24 | 18:49 | 0:19 | 0 | 18 | [5 empty] | At Choudwar end: O/C (B Ph), E/F, Zone 1, Dist- 5.637km, Ib- 5.176kA At T S Alloys end: O/C (B Ph)
|  | 25.05.24 | 16:43 | 25.05.24 | 17:00 | 0:17 | 0 | 9 | [5 empty] | At Choudwar end: Distance Protection, Ia=126.8A, Ib=4.326kA, Ic=480A, zone=1, loc=12.66km . At TS Alloys end: Ia=140.9A,Ib=2.887kA, Ic=495.1A, loc=6.936km, zone=1
|  | 25.06.24 | 17:07 | 25.06.24 | 17:13 | 0:06 | 0 | 6 | [5 empty] | At Choudwar end: Distance Protection,Zone1, location: 6.49km, Ia-188.4A, Ib- 5.887kA, Ic- 75.58A at Choudwar end. At TS Alloys end tripped on O/C Y phase.
|  | 13.07.24 | 12:57 | 13.07.24 | 13:14 | 0:17 | 0 | 17 | [5 empty] | At TS Alloys end: O/C (R-Y Ph)
|  | 14.07.24 | 12:30 | 14.07.24 | 13:09 | 0:39 | 0 | 39 | [5 empty] | At Choudwar end: Zone 1, Dist- 1.606km, Ir- 401.8A, Iy- 484.9A, Ib- 4.428kA At TS Alloys end: O/C (B Ph), tripped due to touching of a hyva to the conductor
|  | 28.07.24 | 17:45 | 29.07.24 | 1:42 | 7:57 | 7 | 57 | [5 empty] | At Choudwar end: Zone 1, Dist- 8.587km, Ir- 6.147kA, Iy- 5.823kA, Ib- 6.010kA At TS Alloys end- O/C (B Ph)
|  | 17.08.24 | 16:32 | 18.08.24 | 19:27 | 26:55 | 26 | 55 | [5 empty] | At Choudwar end: O/C (R Ph), Zone 1, Dist- 11.42km, Ir- 4.549kA At TS Alloys end: O/C (R Ph), Zone 1, Dist- 9.35km, Ir- 2.306kA
|  | 17.08.24 | 11:04 | 17.08.24 | 11:30 | 0:26 | 0 | 26 | [5 empty] | At Choudwar end: O/C (Y-B), Zone 3, Dist- 52.83km, Iy- 2.067kA, Ib- 2.197kA At TS Alloys end: No tripping
|  | 2024-10-18 | 13:00 | 2024-10-18 | 15:27 | 2:27 | 2 | 27 | [5 empty] | At Choudwar end:No tripping At TS Alloys end: Zone 1, dist- 19.03km, Ia-0.467kA, Ib-1.097kA, Ic-2.076kA
|  | 6.01.25 | 12:44 | 6.01.25 | 13:02 | 0:18 | 0 | 18 | [5 empty] | At Choudwar end: O/C At TS Alloys: O/C (R Ph)
|  | 6.01.25 | 13:13 | 6.01.25 | 13:33 | 0:20 | 0 | 20 | [5 empty] | At Choudwar end: O/C At TS Alloys: O/C (R Ph)
|  | 12.02.25 | 07:49 | 12.02.25 | 8:16 | 0:27 | 0 | 23 | [5 empty] | At Choudwar end: Over Current At TS Alloys: O/C , E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
476 | 132kV TS Alloys-Ultratech |  |  |  |  | 0.030556 | 0 | 44 | [7 empty] | 22.067 | 8760 | 99.99% | 16.1825 | 193306.92
|  | 17.08.24 | 11:04 | 17.08.24 | 11:48 | 0:44 | 0 | 44 | [5 empty] | At TS Alloys end: No tripping At Ultratech end: O/C (Y-B), Zone 1, Dist- 1.3km, Iy- 1.61kA, Ib- 1.66kA
477 | 132kV Ultratech-Arati Steel |  |  |  |  | 0.042361 | 0 | 44 | [7 empty] | 18.704 | 8760 | 99.99% | 13.7163 | 163847.04
|  | 17.08.24 | 11:04 | 17.08.24 | 12:05 | 1:01 | 0 | 44 | [5 empty] | At Ultratech end: No tripping At Aarti end: Zone 1, Dist- 13.41km, Ir- 0.018kA, Iy- 1.39kA, Ib- 1.39kA
478 | 132kV Rayagada-Akhusingh |  |  |  |  | 0.24514 | 15 | 41 | [7 empty] | 49.2 | 8760 | 99.82% | 771.62 | 430992
|  | 04.06.24 | 15:58 | 04.06.24 | 17:42 | 1:44 | 0 | 13 | [5 empty] | Machhkund supply failure
|  | 06.06.24 | 18:03 | 06.06.24 | 18:20 | 0:17 | 0 | 15 | [5 empty] | Machhkund supply failure
|  | 06.06.24 | 18:34 | 06.06.24 | 18:56 | 0:22 | 0 | 10 | [5 empty] | At Rayagada end:Earth Fault,132kV Rayagada Buscoupler CB tripped on E/F relay indication. Back up relay operated Ia=324.6 A, Ib=282 A, Ic=186.2 A, In=788.9 A
|  | 08.07.24 | 15:32 | 08.07.24 | 16:05 | 0:33 | 0 | 27 | [5 empty] | At Podagada end: B-Ph, Zone 1, Dist- 57.5km, Ir= 0.03kA, Iy= 0.14kA, Ib= 0.92kA
|  | 16.07.24 | 13:03 | 16.07.24 | 13:23 | 0:20 | 0 | 13 | [5 empty] | Machkund supply failure
|  | 20.07.24 | 08:49 | 20.07.24 | 9:18 | 0:29 | 0 | 18 | [5 empty] | Machkund supply failure
|  | 28.08.24 | 14:44 | 28.08.24 | 14:52 | 0:08 | 0 | 8 | [5 empty] | At Podagada end: Dist Protection,Dist- 55.4 km, Y-Ph fault, IL1= 0.34kA, IL2= 0.95kA, IL3= 0.15kA
|  | 2024-10-12 | 17:11 | 2024-10-12 | 17:25 | 0:14 | 0 | 14 | [5 empty] | Supply failure from Machkund
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 20 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 8 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 27 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 22 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
|  | 14.11.24 | 10:47 | 14.11.24 | 11:16 | 0:29 | 0 | 26 | [5 empty] | Machkund supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
479 | 132kV Rayagada-Rayagada RTSS |  |  |  |  | 1899-12-31 17:44 | 26 | 12 | [7 empty] | 2.646 | 8760 | 99.7% | 69.3252 | 23178.96
|  | 24.04.24 | 07:11 | 24.04.24 | 8:12 | 1:01 | 0 | 21 | [5 empty] | Machkund supply failed at Machkund end.
|  | 25.04.24 | 8:21 | 25.04.24 | 8:33 | 0:12 | 0 | 12 | [5 empty] | Machkund supply failed at Machkund end.
|  | 20.04.24 | 16:57 | 20.04.24 | 17:25 | 0:28 | 0 | 28 | [5 empty] | At Therubali end: E/F (B-N), Ib- 3.6kA
|  | 29.04.24 | 13:43 | 29.04.24 | 13:49 | 0:06 | 0 | 3 | [5 empty] | At Podagada end: R-Y-B, Zone 2, Dist- 70.9km, Ir- 0.82kA, Iy- 0.81kA, Ib- 0.77kA
|  | 29.04.24 | 13:51 | 29.04.24 | 14:52 | 1:01 | 0 | 25 | [5 empty] | At Rayagada end: Y-B, Zone 1, Dist- 41.84km, Ir- 0.218kA, Iy- 0.181kA, Ib- 0.174kA
|  | 05.05.24 | 21:44 | 05.05.24 | 21:55 | 0:11 | 0 | 11 | [5 empty] | Machkund supply failure
|  | 06.05.24 | 14:04 | 06.05.24 | 16:08 | 2:04 | 0 | 13 | [5 empty] | Machkund supply failure
|  | 02.06.24 | 20:39 | 03.06.24 | 14:20 | 17:41 | 0 | 45 | [5 empty] | At Rayagada end: Earth Fault,B-Phase E/F, Ib=9.8KA, Ig=9.8KA At Therubali end: Earth Fault,B-Phase E/F, Ib=9.8KA, Ig=9.8KA
|  | 15.07.24 | 17:31 | 15.07.24 | 17:34 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 16.07.24 | 12:43 | 16.07.24 | 12:48 | 0:05 | 0 | 5 | [5 empty] | O/C (R Ph)
|  | 16.07.24 | 18:17 | 16.07.24 | 18:20 | 0:03 | 0 | 3 | [5 empty] | O/C (R Ph)
|  | 16.07.24 | 18:27 | 16.07.24 | 18:32 | 0:05 | 0 | 5 | [5 empty] | O/C (R Ph)
|  | 16.07.24 | 18:54 | 16.07.24 | 19:02 | 0:08 | 0 | 8 | [5 empty] | O/C (R Ph)
|  | 17.07.24 | 07:31 | 17.07.24 | 7:34 | 0:03 | 0 | 3 | [5 empty] | O/C (R-B Ph)
|  | 17.07.24 | 07:45 | 17.07.24 | 7:48 | 0:03 | 0 | 3 | [5 empty] | O/C (R-B Ph)
|  | 17.07.24 | 08:08 | 17.07.24 | 8:11 | 0:03 | 0 | 3 | [5 empty] | O/C (R-B Ph)
|  | 19.07.24 | 06:22 | 19.07.24 | 6:25 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 19.07.24 | 10:11 | 19.07.24 | 18:14 | 8:03 | 0 | 37 | [5 empty] | At Therubali end: Earth Fault, YG,Iy=5.645kA, At Rayagada end: Earth Fault,Snapping of jumper,No data recorded at Rayagada end.
|  | 19.07.24 | 11:39 | 19.07.24 | 11:47 | 0:08 | 0 | 8 | [5 empty] | O/C (R-B Ph)
|  | 21.07.24 | 09:41 | 21.07.24 | 9:43 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C ( R-B Ph)
|  | 21.07.24 | 16:56 | 21.07.24 | 17:00 | 0:04 | 0 | 4 | [5 empty] | At Rayagada end: O/C ( R-B Ph)
|  | 25.07.24 | 01:33 | 25.07.24 | 1:34 | 0:01 | 0 | 1 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 25.07.24 | 17:12 | 25.07.24 | 17:14 | 0:02 | 0 | 2 | [5 empty] | O/C (R-B Ph)
|  | 25.07.24 | 21:03 | 25.07.24 | 21:05 | 0:02 | 0 | 2 | [5 empty] | O/C (R-B Ph)
|  | 26.07.24 | 02:59 | 26.07.24 | 3:01 | 0:02 | 0 | 2 | [5 empty] | O/C (R-B Ph)
|  | 26.07.24 | 21:28 | 26.07.24 | 21:31 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 27.07.24 | 18:17 | 27.07.24 | 18:19 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 27.07.24 | 21:13 | 27.07.24 | 21:16 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 28.07.24 | 06:10 | 28.07.24 | 6:13 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 28.07.24 | 22:27 | 28.07.24 | 22:31 | 0:04 | 0 | 4 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 29.07.24 | 07:20 | 29.07.24 | 7:23 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 30.07.24 | 07:39 | 30.07.24 | 7:41 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,Over Current R & B ph
|  | 03.08.24 | 13:04 | 03.08.24 | 13:07 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-B Ph)
|  | 04.08.24 | 14:04 | 04.08.24 | 14:13 | 0:09 | 0 | 9 | [5 empty] | At Rayagada end: O/C (R-B Ph)
|  | 06.08.24 | 07:51 | 06.08.24 | 7:54 | 0:03 | 0 | 3 | [5 empty] | O/C (R-B)
|  | 06.08.24 | 14:01 | 06.08.24 | 14:03 | 0:02 | 0 | 2 | [5 empty] | O/C (R-B)
|  | 06.08.24 | 14:06 | 06.08.24 | 14:08 | 0:02 | 0 | 2 | [5 empty] | O/C (R-B)
|  | 10.08.24 | 18:03 | 10.08.24 | 18:05 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C, R & B Ph
|  | 15.08.24 | 15:43 | 15.08.24 | 15:46 | 0:03 | 0 | 3 | [5 empty] | O/C (R-B)
|  | 15.08.24 | 16:02 | 15.08.24 | 16:07 | 0:05 | 0 | 5
|  | 16.08.24 | 15:13 | 16.08.24 | 15:16 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C, R & B PHASE
|  | 17.08.24 | 05:45 | 17.08.24 | 5:47 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 17.08.24 | 06:11 | 17.08.24 | 6:13 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 17.08.24 | 07:18 | 17.08.24 | 7:21 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 17.08.24 | 07:41 | 17.08.24 | 7:44 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 17.08.24 | 08:35 | 17.08.24 | 8:37 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 17.08.24 | 16:00 | 17.08.24 | 16:02 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 19.08.24 | 06:05 | 19.08.24 | 6:06 | 0:01 | 0 | 1 | [5 empty] | At Rayagada end: O/C, R & B PHASE
|  | 19.08.24 | 0:00 | 19.08.24 | 6:02 | 6:02 | 6 | 2 | [5 empty] | At Rayagada end: O/C, R & B PHASE
|  | 28.08.24 | 09:01 | 28.08.24 | 9:04 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C,R & B PHASE
|  | 28.08.24 | 13:09 | 28.08.24 | 13:11 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: O/C, R & B PHASE
|  | 04.09.24 | 08:54 | 04.09.24 | 8:57 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-Y)
|  | 04.09.24 | 17:57 | 04.09.24 | 18:00 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: O/C (R-B)
|  | 05.09.24 | 22:34 | 05.09.24 | 22:36 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,R & B PHASE
|  | 07.09.24 | 22:36 | 07.09.24 | 22:38 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 08.09.24 | 16:58 | 08.09.24 | 17:02 | 0:04 | 0 | 4 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 08.09.24 | 19:37 | 08.09.24 | 19:39 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,R & B PHASE
|  | 08.09.24 | 20:00 | 08.09.24 | 20:02 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 12.09.24 | 07:26 | 12.09.24 | 7:28 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 18.09.24 | 07:38 | 18.09.24 | 7:41 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 18.09.24 | 07:43 | 18.09.24 | 7:45 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 24.09.24 | 06:57 | 24.09.24 | 7:00 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 26.09.24 | 01:27 | 26.09.24 | 1:29 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 26.09.24 | 01:45 | 26.09.24 | 1:46 | 0:01 | 0 | 1 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 26.09.24 | 19:27 | 26.09.24 | 19:30 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current,OVER CURRENT R & B PHASE
|  | 30.09.24 | 00:52 | 30.09.24 | 0:54 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,R-B Phase O/C relay indication. Backup P141 operated. Ia=219.3A, Ic=220.1A
|  | 30.09.24 | 22:15 | 30.09.24 | 22:17 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,R-B Phase O/C relay indication. Backup P141 operated. Ia=219.2A, Ic=220.2A
|  | 2024-10-06 | 02:43 | 2024-10-06 | 2:46 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-06 | 07:38 | 2024-10-06 | 7:40 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-08 | 18:07 | 2024-10-08 | 18:09 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-08 | 20:45 | 2024-10-08 | 20:49 | 0:04 | 0 | 4 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-08 | 20:57 | 2024-10-08 | 21:01 | 0:04 | 0 | 4 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-09 | 15:01 | 2024-10-09 | 15:04 | 0:03 | 0 | 3 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-10 | 12:27 | 2024-10-10 | 12:29 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current, R & B PHASE
|  | 2024-10-12 | 17:18 | 2024-10-12 | 17:20 | 0:02 | 0 | 2 | [5 empty] | At Rayagada end: Over Current,R & B PHASE
|  | 2024-10-23 | 10:13 | 2024-10-23 | 10:33 | 0:20 | 0 | 20 | [5 empty] | Supply failure from Machkund
|  | 2024-10-26 | 12:00 | 2024-10-26 | 12:08 | 0:08 | 0 | 8 | [5 empty] | Supply failure from Machkund
|  | 2024-10-14 | 06:51 | 2024-10-14 | 7:18 | 0:27 | 0 | 27 | [5 empty] | At Rayagada end: Remote end TrippingMACHHAKUND P.H POWER SUPPLY FAILURE
|  | 2024-10-31 | 12:37 | 2024-10-31 | 12:59 | 0:22 | 0 | 22 | [5 empty] | At Rayagada end: Remote end Tripping, 132KV Machkund PS fail from Machkund P.H
|  | 14.11.24 | 10:47 | 14.11.24 | 11:16 | 0:29 | 0 | 29 | [5 empty] | Machkund supply failure
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
480 | 132kV Rayagada-VBC Ferro |  |  |  |  | 0 | 0 | 0 | [7 empty] | 0.3 | 8760 | 100% | 0 | 2628
481 | 132kV Rourkela-Bhalulata RTSS |  |  |  |  | 1900-01-02 00:48 | 84 | 51 | [7 empty] | 23.89 | 8760 | 99.03% | 2027.0665 | 209276.4
|  | 11.05.24 | 16:52 | 11.05.24 | 17:00 | 0:08 | 0 | 8 | [5 empty] | At Rourkela end: O/C,tripped on BGT, DP relay details: zone 1,location 39.36KM,Ia=338A,Ib=2320A,Ic=283A,Ig=1698A. At BK Steel end: Location 26KM , I a=312A,Ib=684A,Ic=336A.SN 17.
|  | 11.05.24 | 19:24 | 11.05.24 | 20:46 | 1:22 | 1 | 22 | [5 empty] | At Rourkela end: Distance Protection,Rourkela End: ABCT Zone-1, Location: 43.40 km, Ia=3196 A, Ib=3189 A, Ic=3191 A, Ig=218 A.
|  | 31.05.24 | 20:17 | 31.05.24 | 20:46 | 0:29 | 0 | 29 | [5 empty] | At Rourkela end: Distance Protection,DP RELAY: EVENT: ABT, ZONE 1, LOCATION- 2.39KM IA=7276A, IB=7396A,IC=134 A , IN=0, IG=406A
|  | 05.06.24 | 21:11 | 06.06.24 | 12:30 | 15:19 | 15 | 19 | [5 empty] | At Rourkela end: Earth Fault,trip time 21:11 Fault details: zone 1 ,CGT, location 2.10,IA=199A,IB=84A,IC=9183A,IN=1A,IG=9194A. TEST CHARGED AT 21:55HRS FAULT DETAILS:ZONE 1 ,CGT, LOCATION 2.00,IA=14A,IB=15A, IC=9308A.IN=1A, IG=9318A.
|  | 15.06.24 | 20:57 | 15.06.24 | 22:43 | 1:46 | 1 | 46 | [5 empty] | At Rourkela end: Over Current,ABCT,ZONE 1,LOCATION 50.17,IA=2540A, IB=2701A,IC=2552A, IN=0A, IG=165A,
|  | 09.07.24 | 06:38 | 09.07.24 | 6:56 | 0:18 | 0 | 18 | [5 empty] | At Rourkela end: E/F (B-N), Dist- 36.34km, Ib- 2.126kA
|  | 31.07.24 | 22:10 | 31.07.24 | 23:14 | 1:04 | 1 | 4 | [5 empty] | At Rourkela end: O/C, Dist- 37.11km, Ir- 3.359kA, Iy- 3.78kA, Ib- 3.452kA
|  | 03.08.24 | 01:06 | 03.08.24 | 20:02 | 18:56 | 18 | 56 | [5 empty] | At Rourkela end: E/F,B-N, Ib- 1.044kA, Dist- 65.63km
|  | 28.08.24 | 2:00 | 28.08.24 | 2:36 | 0:36 | 0 | 36 | [5 empty] | At Rourkela end: O/C (R-Y-B), Zone 1, Dist- 45.99km, Ir- 2.886kA, Iy- 3.165kA, Ib- 2.916kA
|  | 07.09.24 | 23:12 | 07.09.24 | 23:29 | 0:17 | 0 | 17 | [5 empty] | At Rourkela end: Over Current,ABCT,LOCATION=48.03,IA=2650A,IB=278.6A,IC=2718A,IN=0A,IG=274A,TRIP,ZONE 1.
|  | 11.09.24 | 16:53 | 11.09.24 | 17:10 | 0:17 | 0 | 17 | [5 empty] | At Rourkela end: O/C (R-Y), Ir- 2.816kA, Iy- 2.73kA
|  | 11.09.24 | 17:10 | 11.09.24 | 17:36 | 0:26 | 0 | 26 | [5 empty] | At Rourkela end: E/F (Y-N), Iy- 1.288kA, Dist- 37.29km
|  | 11.09.24 | 17:36 | 12.09.24 | 12:53 | 19:17 | 19 | 17 | [5 empty] | At Rourkela end: E/F (Y-N), Iy- 1.609kA, Dist- 37.29km
|  | 12.09.24 | 13:00 | 12.09.24 | 14:19 | 1:19 | 1 | 19 | [5 empty] | At Rourkela end: Earth Fault,BGT, Dist 1.36,IA=12A,IB=5974.0A,IC=3A,IN=1A,IG=5964A,TRIP ZONE 1 GROUP 2.
|  | 4.02.25 | 15:57 | 4.02.25 | 17:09 | 1:12 | 1 | 12 | [5 empty] | At Rourkela end: Y-N, Zone 1, Dist- 1.33km, Iy- 5.598kA
|  | 7.03.25 | 06:43 | 7.03.25 | 7:25 | 0:42 | 0 | 42 | [5 empty] | At Rourkela end: R-B, Zone 1, Dist- 77.5km, Ir- 1.84kA, Ib- 1.888kA
|  | 16.03.25 | 11:16 | 16.03.25 | 12:11 | 0:55 | 0 | 55 | [5 empty] | At Rourkela end: R-Y, Dist- 60.01km, Ir- 2.1kA, Iy- 2.202kA, Zone 1
|  | 21.03.25 | 16:30 | 21.03.25 | 17:35 | 1:05 | 1 | 5 | [5 empty] | At Rourkela end: R-N, Dist- 51.56km, Ir- 1.737kA
|  | 21.03.25 | 17:35 | 22.03.25 | 0:55 | 7:20 | 7 | 23 | [5 empty] | At Rourkela end: R-Y-B, Dist- 48.77km, Zone 1, Ir- 2.85kA, Iy- 2.898kA, Ib- 2.69kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
482 | 132 kV New Bolangir - Bolangir Ckt - I |  |  |  |  | 0.16944 | 13 | 57 | [7 empty] | 3.78 | 8760 | 99.84% | 52.731 | 33112.8
|  | 04.04.24 | 20:02 | 04.04.24 | 20:12 | 0:10 | 0 | 10 | [5 empty] | At Bolangir New end: O/C, Ir- 1.41kA At Bolangir Old end: O/C (Y-N), Zone 1, Dist- 3.946km, Iy- 4.285kA
|  | 19.04.24 | 16:27 | 19.04.24 | 18:08 | 1:41 | 0 | 23 | [5 empty] | Distance Protection, Ia- 532A, Ib-2.813kA, Ic-2.514kA, Distance- 34.54km
|  | 11.06.24 | 16:54 | 11.06.24 | 17:07 | 0:13 | 0 | 13 | [5 empty] | Supply failure
|  | 11.06.24 | 17:37 | 11.06.24 | 17:47 | 0:10 | 0 | 10 | [5 empty] | Supply failure
|  | 15.07.24 | 15:57 | 15.07.24 | 16:50 | 0:53 | 0 | 53 | [5 empty] | At Bolangir end: E/F, O/C
|  | 07.09.24 | 18:55 | 07.09.24 | 19:52 | 0:57 | 0 | 8 | [5 empty] | At Bolangir New end: Earth Fault, Ic=8.88KA At Bolangir end: Ic=1.98KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
483 | 132kV Bolangir- ACME |  |  |  |  | 1899-12-31 15:48 | 15 | 38 | [7 empty] | 21.62 | 8760 | 99.82% | 337.9927 | 189391.2
|  | 04.04.24 | 20:02 | 04.04.24 | 20:54 | 20:54 | 0 | 49 | [5 empty] | Zone 2, Ir- 2.846kA, Iy- 0.217kA, Ib- 0.299kA
|  | 11.06.24 | 16:54 | 11.06.24 | 17:37 | 0:43 | 0 | 43 | [5 empty] | At Bolangir end:Distance Protection,Fault occured at zone2 at a distance of 18.9km with fault current 2.1KA
|  | 11.06.24 | 17:37 | 11.06.24 | 18:50 | 1:13 | 1 | 13 | [5 empty] | At Bolangir end: Distance Protection,Fault occured at zone2 with fault current 2.1KA
|  | 15.07.24 | 15:57 | 15.07.24 | 16:58 | 16:58 | 0 | 53 | [5 empty] | At Bolangir end: E/F, O/C
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
484 | 132 kV ACME - Tusura |  |  |  |  | 0.045139 | 1 | 5 | [7 empty] | 24.02 | 8760 | 99.99% | 26.0217 | 210415.2
|  | 11.06.24 | 16:55 | 11.06.24 | 18:00 | 1:05 | 1 | 5 | [5 empty] | At Tusura end: Earth Fault,tripped phase-AG, Distance protection operated upto-17.9 km
485 | 132 kV Tusura- Saintala |  |  |  |  | 0.63264 | 14 | 6 | [7 empty] | 22.38 | 8760 | 99.84% | 315.558 | 196048.8
|  | 02.05.24 | 12:55 | 02.05.24 | 13:05 | 13:05 | 0 | 10 | [5 empty] | At Saintala end: R-B Ph, Zone 1, Dist- 20.45km, Ir- 4.751kA, Ib- 5.03kA At Tusura end: E/F
|  | 07.05.24 | 07:15 | 07.05.24 | 07:38 | 0:23 | 0 | 22 | [5 empty] | At Saintala end: E/F
|  | 11.06.24 | 16:55 | 11.06.24 | 18:00 | 1:05 | 1 | 5 | [5 empty] | At Tusura end: Earth Fault,tripped phase-AG, Distance protection operated upto-17.9 km
|  | 07.09.24 | 18:43 | 07.09.24 | 19:03 | 0:20 | 0 | 13 | [5 empty] | At Saintala end: zone-1,distance-20.25km,Ia-4.66A,Ib-1.57kA,Ic-5.39A
|  | 30.09.24 | 14:19 | 30.09.24 | 14:37 | 0:18 | 0 | 16 | [5 empty] | At Saintala end: Distance Protection,ZONE-1,DISTANCE-20.63KM,IA-3.53A,IB-1.55KA,IC-5.32A,RESISTANCE-11.66 OHMS
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
486 | 132kV Tusura -RTSS Deogaon road |  |  |  |  | 0.24514 | 17 | 52 | [7 empty] | 9.991 | 8760 | 99.8% | 178.5059 | 87521.16
|  | 07.05.24 | 07:15 | 07.05.24 | 07:38 | 0:23 | 0 | 22 | [5 empty] | At Saintala end: E/F
|  | 14.07.24 | 16:08 | 14.07.24 | 20:20 | 4:12 | 4 | 12 | [5 empty] | Jumper snap at Loc. No. 35
|  | 26.08.24 | 17:36 | 26.08.24 | 18:08 | 0:32 | 0 | 32 | [5 empty] | At Tusura end: O/C,Tripped phase A&C, IA=0.25 kA, IC=0.25kA, master trip 86 operated.
|  | 2024-10-18 | 8:45 | 2024-10-18 | 8:55 | 0:10 | 0 | 10 | [5 empty] | O/C
|  | 2024-10-18 | 9:50 | 2024-10-18 | 10:01 | 0:11 | 0 | 11 | [5 empty] | O/C
|  | 2024-10-18 | 13:36 | 2024-10-18 | 13:40 | 0:04 | 0 | 4 | [5 empty] | O/C
|  | 2024-10-21 | 8:42 | 2024-10-21 | 8:50 | 0:08 | 0 | 8 | [5 empty] | O/C
|  | 6.12.24 | 14:55 | 6.12.24 | 15:04 | 0:09 | 0 | 9 | [5 empty] | E/F
|  | 2.03.25 | 11:38 | 2.03.25 | 11:42 | 0:04 | 0 | 4 | [5 empty] | At Tusura end: O/C, Ir- 0.25kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
487 | 132kV Saintala- ABREL |  |  |  |  | 0.015972 | 0 | 6 | [7 empty] | 3 | 8760 | 100% | 0.3 | 26280
|  | 07.05.24 | 07:15 | 07.05.24 | 07:38 | 0:23 | 0 | 22 | [5 empty] | At Saintala end: E/F
488 | 132kV ABREL- Kesinga |  |  |  |  | 0.015972 | 0 | 22 | [7 empty] | 33 | 8760 | 100% | 12.1 | 289080
|  | 07.05.24 | 07:15 | 07.05.24 | 07:38 | 0:23 | 0 | 22 | [5 empty] | At Saintala end: E/F
489 | 132kV Kesinga-Khariar |  |  |  |  | 0.25 | 17 | 50 | [7 empty] | 57.7 | 8760 | 99.8% | 1028.9833 | 505452
|  | 06.04.24 | 12:53 | 06.04.24 | 13:00 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Y-N, Dist- 25.27km, Iy- 1.58kA At Khariar end: Y-N, Dist- 45.3km, Iy- 0.77kA
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | O/C, Iy-0.44kA
|  | 07.05.24 | 07:15 | 07.05.24 | 07:52 | 0:37 | 0 | 37 | [5 empty] | Transformer Failed from Kesinga end
|  | 08.06.24 | 15:03 | 08.06.24 | 15:10 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Over Current,O/.C , D/P Zone-1, R= 0.42KA, Y = 0.38KA, B= 0.23KA
|  | 25.07.24 | 2:39 | 25.07.24 | 3:14 | 0:35 | 0 | 35 | [5 empty] | At Kesinga end: Ir- 1.004kA, Iy- 0.946kA, Ib- 0.912kA,Dist- 27.66km
|  | 28.07.24 | 22:53 | 28.07.24 | 23:12 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Zone 1, Dist- 13.43km, B-N, Ib- 3.8kA
|  | 07.08.24 | 18:18 | 07.08.24 | 18:27 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: B-N, Zone 1, Dist- 13.46km, Ib- 4kA
|  | 16.08.24 | 00:04 | 16.08.24 | 0:20 | 0:16 | 0 | 15 | [5 empty] | At Khariar end: R-Y, Zone 1, Dist- 12.65km, Ir- 3.6kA, Iy- 3.3kA
|  | 01.09.24 | 17:50 | 01.09.24 | 17:59 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: Zone 1, Dist- 14.4km, Ir- 0.178kA, Iy- 1.672kA, Ib- 1.669kA
|  | 03.09.24 | 21:06 | 03.09.24 | 21:21 | 0:15 | 0 | 9 | [5 empty] | At Khariar end: Dist- 76.6km, Ir- 0.327kA, Iy- 1.72kA, Ib- 1.66kA
|  | 12.09.24 | 02:38 | 12.09.24 | 2:57 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Distance Protection,Dist 40.65 KM, B-PHASE 3.766 KA
|  | 12.09.24 | 22:50 | 12.09.24 | 22:55 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: Earth Fault,Distance-14.09 kms,R ph-102A,Y ph-359.1A,B ph-3.766 KA
|  | 21.09.24 | 23:48 | 22.09.24 | 0:14 | 0:26 | 0 | 23 | [5 empty] | TRIP FROM SOURCE END GSS KHARIAR END
|  | 24.09.24 | 20:17 | 24.09.24 | 20:28 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Earth Fault,R ph-2.8 KA At Kesinga end: Distance Protection,Distance-22.7 kms,R ph-2.81 KA,Y ph-149 A,B ph-451 A
|  | 25.09.24 | 04:44 | 25.09.24 | 5:00 | 0:16 | 0 | 16 | [5 empty] | At Khariar end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A At Kesinga end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A
|  | 26.09.24 | 18:00 | 26.09.24 | 18:07 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Distance Protection,Distance-36.9 kms,R ph-2.07 KA,Y ph-168 A,B ph-338 A
|  | 29.09.24 | 01:58 | 29.09.24 | 2:16 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Distance Protection,Distance-14.9 kms, R ph-113.9 A,Y ph-381 A,B ph-3.7 KA
|  | 05.09.24 | 9:58 | 05.09.24 | 10:00 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 570A
|  | 07.09.24 | 16:35 | 07.09.24 | 16:38 | 0:03 | 0 | 3 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 600A
|  | 07.09.24 | 21:19 | 07.09.24 | 21:21 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 339A
|  | 17.09.24 | 11:16 | 17.09.24 | 11:18 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 566A
|  | 24.09.24 | 14:37 | 24.09.24 | 14:39 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 324A
|  | 2024-10-05 | 17:41 | 2024-10-05 | 17:52 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA At Kesinga end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA
|  | 2024-10-05 | 20:06 | 2024-10-05 | 20:19 | 0:13 | 0 | 13 | [5 empty] | At Khariar end: Distance Protection, Zone 1 Operated, Fault dist. 13.77KM, Fault current R-Ph 3.309KA
|  | 2024-10-07 | 05:31 | 2024-10-07 | 5:41 | 0:10 | 0 | 10 | [5 empty] | At Khariar end: Distance ProtectionZone 1, Fault dist. 40.6KM,R ph- 158A, Y ph- 514A, B ph- 2KA At Kesinga end: Earth Fault, R-158 A,Y-514 A,B-2 KA,DISTANCE-13.77 KM
|  | 2024-10-12 | 04:57 | 2024-10-12 | 5:08 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Earth FaultR-106.5 A,Y-363.1 A,B-3.763 KA,DISTANCE-14.03 KM
|  | 2024-10-12 | 19:56 | 2024-10-12 | 20:03 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 2.02KA, FAULT DISTANCE 40 KM
|  | 2024-10-19 | 01:15 | 2024-10-19 | 1:22 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance ProtectionR PH-3.606 KA, Y PH-158.8A, B PH-379.2A, FAULT DISTANCE-13 KM, Zone 1 OPERATED At Kesinga end: Earth Fault, R-3.606 KA,Y-158.8A,B-379.2A,DISTANCE-13 KM
|  | 2024-10-19 | 20:58 | 2024-10-19 | 21:06 | 0:08 | 0 | 8 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 3.8 KA, FAULT DISTANCE 14.4 KM
|  | 7.11.24 | 02:18 | 7.11.24 | 2:25 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection,fault dist. 23.54KM, Zone-1 Operated, Fault current R-Ph 104.7A, Y-Ph 399A, B-Ph 2.9KA
|  | 28.01.25 | 11:08 | 28.01.25 | 11:15 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Over Current, R-Ph 450A, Y-Ph 390A, B-Ph 350A At Kesinga end: Over Current,R-0.45 KA,Y-0.39 KA,B-0.35 KA
|  | 25.02.25 | 17:14 | 25.02.25 | 17:23 | 0:09 | 0 | 9 | [5 empty] | Over Current,R-0.46 KA,Y-0.44 KA,B-0.35 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
490 | 132 kV Khariar - Kantabanji |  |  |  |  | 0.27083 | 18 | 20 | [7 empty] | 32.6 | 8760 | 99.79% | 597.6667 | 285576
|  | 06.04.24 | 12:53 | 06.04.24 | 13:00 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Y-N, Dist- 25.27km, Iy- 1.58kA At Khariar end: Y-N, Dist- 45.3km, Iy- 0.77kA
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | O/C, Iy-0.44kA
|  | 07.05.24 | 07:15 | 07.05.24 | 07:52 | 0:37 | 0 | 37 | [5 empty] | Transformer Failed from Kesinga end
|  | 08.06.24 | 15:03 | 08.06.24 | 15:10 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Over Current,O/.C , D/P Zone-1, R= 0.42KA, Y = 0.38KA, B= 0.23KA
|  | 25.07.24 | 2:39 | 25.07.24 | 3:14 | 0:35 | 0 | 35 | [5 empty] | At Kesinga end: Ir- 1.004kA, Iy- 0.946kA, Ib- 0.912kA,Dist- 27.66km
|  | 28.07.24 | 22:53 | 28.07.24 | 23:12 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Zone 1, Dist- 13.43km, B-N, Ib- 3.8kA
|  | 07.08.24 | 18:18 | 07.08.24 | 18:27 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: B-N, Zone 1, Dist- 13.46km, Ib- 4kA
|  | 16.08.24 | 00:04 | 16.08.24 | 0:20 | 0:16 | 0 | 15 | [5 empty] | At Khariar end: R-Y, Zone 1, Dist- 12.65km, Ir- 3.6kA, Iy- 3.3kA
|  | 01.09.24 | 17:50 | 01.09.24 | 17:59 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: Zone 1, Dist- 14.4km, Ir- 0.178kA, Iy- 1.672kA, Ib- 1.669kA
|  | 03.09.24 | 21:06 | 03.09.24 | 21:21 | 0:15 | 0 | 9 | [5 empty] | At Khariar end: Dist- 76.6km, Ir- 0.327kA, Iy- 1.72kA, Ib- 1.66kA
|  | 12.09.24 | 02:38 | 12.09.24 | 2:57 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Distance Protection,Dist 40.65 KM, B-PHASE 3.766 KA
|  | 12.09.24 | 22:50 | 12.09.24 | 22:55 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: Earth Fault,Distance-14.09 kms,R ph-102A,Y ph-359.1A,B ph-3.766 KA
|  | 21.09.24 | 23:48 | 22.09.24 | 0:14 | 0:26 | 0 | 23 | [5 empty] | TRIP FROM SOURCE END GSS KHARIAR END
|  | 24.09.24 | 20:17 | 24.09.24 | 20:28 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Earth Fault,R ph-2.8 KA At Kesinga end: Distance Protection,Distance-22.7 kms,R ph-2.81 KA,Y ph-149 A,B ph-451 A
|  | 25.09.24 | 04:44 | 25.09.24 | 5:00 | 0:16 | 0 | 16 | [5 empty] | At Khariar end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A At Kesinga end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A
|  | 26.09.24 | 18:00 | 26.09.24 | 18:07 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Distance Protection,Distance-36.9 kms,R ph-2.07 KA,Y ph-168 A,B ph-338 A
|  | 29.09.24 | 01:58 | 29.09.24 | 2:16 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Distance Protection,Distance-14.9 kms, R ph-113.9 A,Y ph-381 A,B ph-3.7 KA
|  | 05.09.24 | 9:58 | 05.09.24 | 10:00 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 570A
|  | 07.09.24 | 16:35 | 07.09.24 | 16:38 | 0:03 | 0 | 3 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 600A
|  | 07.09.24 | 21:19 | 07.09.24 | 21:21 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 339A
|  | 17.09.24 | 11:16 | 17.09.24 | 11:18 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 566A
|  | 24.09.24 | 14:37 | 24.09.24 | 14:39 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 324A
|  | 2024-10-05 | 17:41 | 2024-10-05 | 17:52 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA At Kesinga end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA
|  | 2024-10-05 | 20:06 | 2024-10-05 | 20:19 | 0:13 | 0 | 13 | [5 empty] | At Khariar end: Distance Protection, Zone 1 Operated, Fault dist. 13.77KM, Fault current R-Ph 3.309KA
|  | 2024-10-07 | 05:31 | 2024-10-07 | 5:41 | 0:10 | 0 | 10 | [5 empty] | At Khariar end: Distance ProtectionZone 1, Fault dist. 40.6KM,R ph- 158A, Y ph- 514A, B ph- 2KA At Kesinga end: Earth Fault, R-158 A,Y-514 A,B-2 KA,DISTANCE-13.77 KM
|  | 2024-10-12 | 04:57 | 2024-10-12 | 5:08 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Earth FaultR-106.5 A,Y-363.1 A,B-3.763 KA,DISTANCE-14.03 KM
|  | 2024-10-12 | 19:56 | 2024-10-12 | 20:03 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 2.02KA, FAULT DISTANCE 40 KM
|  | 2024-10-19 | 01:15 | 2024-10-19 | 1:22 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance ProtectionR PH-3.606 KA, Y PH-158.8A, B PH-379.2A, FAULT DISTANCE-13 KM, Zone 1 OPERATED At Kesinga end: Earth Fault, R-3.606 KA,Y-158.8A,B-379.2A,DISTANCE-13 KM
|  | 2024-10-19 | 20:58 | 2024-10-19 | 21:06 | 0:08 | 0 | 8 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 3.8 KA, FAULT DISTANCE 14.4 KM
|  | 7.11.24 | 02:18 | 7.11.24 | 2:25 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection,fault dist. 23.54KM, Zone-1 Operated, Fault current R-Ph 104.7A, Y-Ph 399A, B-Ph 2.9KA
|  | 11.11.24 | 9:53 | 11.11.24 | 10:04 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Over Current,started phase=AB, Tripped Phase=A, Ia=300.9A, Ib=285.8A, Ic=182A
|  | 11.11.24 | 10:21 | 11.11.24 | 10:33 | 0:12 | 0 | 12 | [5 empty] | At Nuapada end: Over Current,started phase =AB, Tripped phase=A, Ia=300.5A, Ib=279.7A, Ic=158.7A
|  | 28.01.25 | 11:08 | 28.01.25 | 11:15 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Over Current, R-Ph 450A, Y-Ph 390A, B-Ph 350A At Kesinga end: Over Current,R-0.45 KA,Y-0.39 KA,B-0.35 KA
|  | 25.02.25 | 17:14 | 25.02.25 | 17:23 | 0:09 | 0 | 9 | [5 empty] | Over Current,R-0.46 KA,Y-0.44 KA,B-0.35 KA
|  | 21.03.25 | 14:30 | 21.03.25 | 14:32 | 0:02 | 0 | 2 | [5 empty] | Supply failure
|  | 25.03.25 | 7:08 | 25.03.25 | 7:13 | 0:05 | 0 | 5 | [5 empty] | Incomer failure at GSS Kantabanji on overcurrent 0.29kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
491 | 132kV Kantabanji- Kantabanji RTSS |  |  |  |  | 0.2875 | 18 | 44 | [7 empty] | 4 | 8760 | 99.79% | 74.9333 | 35040
|  | 06.04.24 | 12:53 | 06.04.24 | 13:00 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Y-N, Dist- 25.27km, Iy- 1.58kA At Khariar end: Y-N, Dist- 45.3km, Iy- 0.77kA
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | O/C, Iy-0.44kA
|  | 07.05.24 | 07:15 | 07.05.24 | 07:52 | 0:37 | 0 | 37 | [5 empty] | Transformer Failed from Kesinga end
|  | 08.06.24 | 15:03 | 08.06.24 | 15:10 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Over Current,O/.C , D/P Zone-1, R= 0.42KA, Y = 0.38KA, B= 0.23KA
|  | 03.07.24 | 15:14 | 03.07.24 | 15:16 | 0:02 | 0 | 2 | [5 empty] | If- 0.575kA
|  | 04.07.24 | 19:04 | 04.07.24 | 19:06 | 0:02 | 0 | 2 | [5 empty] | If- 0.575kA
|  | 13.07.24 | 17:50 | 13.07.24 | 17:53 | 0:03 | 0 | 3 | [5 empty] | L-L fault, If- 0.575kA
|  | 17.07.24 | 15:22 | 17.07.24 | 15:24 | 0:02 | 0 | 2 | [5 empty] | L-L fault, If- 0.574kA
|  | 29.07.24 | 16:06 | 29.07.24 | 16:10 | 0:04 | 0 | 4 | [5 empty] | L-L fault, If- 0.385kA
|  | 31.07.24 | 20:28 | 31.07.24 | 20:30 | 0:02 | 0 | 2 | [5 empty] | L-L fault, If- 0.584kA
|  | 25.07.24 | 2:39 | 25.07.24 | 3:14 | 0:35 | 0 | 35 | [5 empty] | At Kesinga end: Ir- 1.004kA, Iy- 0.946kA, Ib- 0.912kA,Dist- 27.66km
|  | 28.07.24 | 22:53 | 28.07.24 | 23:12 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Zone 1, Dist- 13.43km, B-N, Ib- 3.8kA
|  | 07.08.24 | 18:18 | 07.08.24 | 18:27 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: B-N, Zone 1, Dist- 13.46km, Ib- 4kA
|  | 16.08.24 | 00:04 | 16.08.24 | 0:20 | 0:16 | 0 | 15 | [5 empty] | At Khariar end: R-Y, Zone 1, Dist- 12.65km, Ir- 3.6kA, Iy- 3.3kA
|  | 01.09.24 | 17:50 | 01.09.24 | 17:59 | 0:09 | 0 | 9 | [5 empty] | At Khariar end: Zone 1, Dist- 14.4km, Ir- 0.178kA, Iy- 1.672kA, Ib- 1.669kA
|  | 03.09.24 | 21:06 | 03.09.24 | 21:21 | 0:15 | 0 | 9 | [5 empty] | At Khariar end: Dist- 76.6km, Ir- 0.327kA, Iy- 1.72kA, Ib- 1.66kA
|  | 12.09.24 | 02:38 | 12.09.24 | 2:57 | 0:19 | 0 | 19 | [5 empty] | At Khariar end: Distance Protection,Dist 40.65 KM, B-PHASE 3.766 KA
|  | 12.09.24 | 22:50 | 12.09.24 | 22:55 | 0:05 | 0 | 5 | [5 empty] | At Kesinga end: Earth Fault,Distance-14.09 kms,R ph-102A,Y ph-359.1A,B ph-3.766 KA
|  | 21.09.24 | 23:48 | 22.09.24 | 0:14 | 0:26 | 0 | 23 | [5 empty] | TRIP FROM SOURCE END GSS KHARIAR END
|  | 24.09.24 | 20:17 | 24.09.24 | 20:28 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Earth Fault,R ph-2.8 KA At Kesinga end: Distance Protection,Distance-22.7 kms,R ph-2.81 KA,Y ph-149 A,B ph-451 A
|  | 25.09.24 | 04:44 | 25.09.24 | 5:00 | 0:16 | 0 | 16 | [5 empty] | At Khariar end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A At Kesinga end: Distance Protection,Distance-22.06 kms, R ph-2.7 KA,Y ph-199 A,B ph-517 A
|  | 26.09.24 | 18:00 | 26.09.24 | 18:07 | 0:07 | 0 | 7 | [5 empty] | At Kesinga end: Distance Protection,Distance-36.9 kms,R ph-2.07 KA,Y ph-168 A,B ph-338 A
|  | 29.09.24 | 01:58 | 29.09.24 | 2:16 | 0:18 | 0 | 18 | [5 empty] | At Kesinga end: Distance Protection,Distance-14.9 kms, R ph-113.9 A,Y ph-381 A,B ph-3.7 KA
|  | 05.09.24 | 9:58 | 05.09.24 | 10:00 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 570A
|  | 07.09.24 | 16:35 | 07.09.24 | 16:38 | 0:03 | 0 | 3 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 600A
|  | 07.09.24 | 21:19 | 07.09.24 | 21:21 | 0:02 | 0 | 2 | [5 empty] | At Kantabanji end: L-L FAULT WITH FAULT CURRENT 339A
|  | 17.09.24 | 11:16 | 17.09.24 | 11:18 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 566A
|  | 24.09.24 | 14:37 | 24.09.24 | 14:39 | 0:02 | 0 | 2 | [5 empty] | L-L FAULT WITH FAULT CURRENT 324A
|  | 2024-10-05 | 17:41 | 2024-10-05 | 17:52 | 0:11 | 0 | 11 | [5 empty] | At Khariar end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA At Kesinga end: Over Current, R-0.46 KA,Y-0.44 KA,B-0.24 KA
|  | 2024-10-05 | 20:06 | 2024-10-05 | 20:19 | 0:13 | 0 | 13 | [5 empty] | At Khariar end: Distance Protection, Zone 1 Operated, Fault dist. 13.77KM, Fault current R-Ph 3.309KA
|  | 2024-10-07 | 05:31 | 2024-10-07 | 5:41 | 0:10 | 0 | 10 | [5 empty] | At Khariar end: Distance ProtectionZone 1, Fault dist. 40.6KM,R ph- 158A, Y ph- 514A, B ph- 2KA At Kesinga end: Earth Fault, R-158 A,Y-514 A,B-2 KA,DISTANCE-13.77 KM
|  | 2024-10-12 | 04:57 | 2024-10-12 | 5:08 | 0:11 | 0 | 11 | [5 empty] | At Kesinga end: Earth FaultR-106.5 A,Y-363.1 A,B-3.763 KA,DISTANCE-14.03 KM
|  | 2024-10-12 | 19:56 | 2024-10-12 | 20:03 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 2.02KA, FAULT DISTANCE 40 KM
|  | 2024-10-19 | 01:15 | 2024-10-19 | 1:22 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance ProtectionR PH-3.606 KA, Y PH-158.8A, B PH-379.2A, FAULT DISTANCE-13 KM, Zone 1 OPERATED At Kesinga end: Earth Fault, R-3.606 KA,Y-158.8A,B-379.2A,DISTANCE-13 KM
|  | 2024-10-19 | 20:58 | 2024-10-19 | 21:06 | 0:08 | 0 | 8 | [5 empty] | At Khariar end: Distance Protection, Zone 1, FAULT CURRENT B-PH 3.8 KA, FAULT DISTANCE 14.4 KM
|  | 7.11.24 | 02:18 | 7.11.24 | 2:25 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection,fault dist. 23.54KM, Zone-1 Operated, Fault current R-Ph 104.7A, Y-Ph 399A, B-Ph 2.9KA
|  | 11.11.24 | 9:53 | 11.11.24 | 10:04 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Over Current,started phase=AB, Tripped Phase=A, Ia=300.9A, Ib=285.8A, Ic=182A
|  | 11.11.24 | 10:21 | 11.11.24 | 10:33 | 0:12 | 0 | 12 | [5 empty] | At Nuapada end: Over Current,started phase =AB, Tripped phase=A, Ia=300.5A, Ib=279.7A, Ic=158.7A
|  | 28.01.25 | 11:08 | 28.01.25 | 11:15 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Over Current, R-Ph 450A, Y-Ph 390A, B-Ph 350A At Kesinga end: Over Current,R-0.45 KA,Y-0.39 KA,B-0.35 KA
|  | 25.02.25 | 17:14 | 25.02.25 | 17:23 | 0:09 | 0 | 9 | [5 empty] | Over Current,R-0.46 KA,Y-0.44 KA,B-0.35 KA
|  | 16.03.25 | 1:03 | 16.03.25 | 1:06 | 0:03 | 0 | 3 | [5 empty] | O/C, If- 0.57kA
|  | 19.03.25 | 20:00 | 19.03.25 | 20:02 | 0:02 | 0 | 2 | [5 empty] | L-L fault, If- 0.406kA
|  | 20.03.25 | 20:06 | 20.03.25 | 20:08 | 0:02 | 0 | 2 | [5 empty] | L-L fault, If- 0.404kA
|  | 22.03.25 | 3:34 | 22.03.25 | 3:36 | 0:02 | 0 | 2 | [5 empty] | L-L fault, If- 0.357kA
|  | 21.03.25 | 14:30 | 21.03.25 | 14:32 | 0:02 | 0 | 2 | [5 empty] | Supply failure
|  | 25.03.25 | 7:08 | 25.03.25 | 7:13 | 0:05 | 0 | 5 | [5 empty] | Incomer failure at GSS Kantabanji on overcurrent 0.29kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
492 | 132 kV Khariar - Nuapada |  |  |  |  | 0.038194 | 12 | 55 | [7 empty] | 76.43 | 8760 | 99.85% | 987.2208 | 669526.8
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | Tripped due to overloading from Kesinga
|  | 25.09.24 | 04:44 | 25.09.24 | 4:59 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,sousrece
|  | 7.11.24 | 02:18 | 7.11.24 | 2:25 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Distance Protection,fault dist. 23.54KM, Zone-1 Operated, Fault current R-Ph 104.7A, Y-Ph 399A, B-Ph 2.9KA
|  | 11.11.24 | 9:53 | 11.11.24 | 10:04 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Over Current,started phase=AB, Tripped Phase=A, Ia=300.9A, Ib=285.8A, Ic=182A
|  | 11.11.24 | 10:21 | 11.11.24 | 10:33 | 0:12 | 0 | 12 | [5 empty] | At Nuapada end: Over Current,started phase =AB, Tripped phase=A, Ia=300.5A, Ib=279.7A, Ic=158.7A
|  | 28.01.25 | 11:08 | 28.01.25 | 11:15 | 0:07 | 0 | 7 | [5 empty] | At Khariar end: Over Current, R-Ph 450A, Y-Ph 390A, B-Ph 350A At Kesinga end: Over Current,R-0.45 KA,Y-0.39 KA,B-0.35 KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
493 | 132kV Nuapada-Nuapada RTSS |  |  |  |  | 0.93403 | 17 | 2 | [7 empty] | 4.528 | 8760 | 99.81% | 77.1269 | 39665.28
|  | 25.04.24 | 10:44 | 25.04.24 | 10:47 | 0:03 | 0 | 3 | [5 empty] | Tripped due to overloading from Kesinga
|  | 19.04.24 | 16:27 | 19.04.24 | 16:51 | 0:24 | 0 | 24 | [5 empty] | Remote end Tripping
|  | 07.06.24 | 17:59 | 07.06.24 | 18:09 | 0:10 | 0 | 10 | [5 empty] | At Nuapada end: Distance Protection,Distance protection operated, zone-1,distance:50kM, Ia:1.192Amp, Ib:: 878 Amp, Ic: 953.5Amp,
|  | 26.06.24 | 20:44 | 26.06.24 | 20:58 | 0:14 | 0 | 14 | [5 empty] | At Padampur end: Distance Protection,Tripped due to Distance protection operated. Zone2, 77.53KM Ia=87.75A, Ib=60.42A, Ic=99.64A At Nuapada end: Earth Fault,tripped on E/F, Started phase:N, Tripped phase:N, Ia=94.09A, Ib=57.09A Ic=130.9A,In=231.5A
|  | 19.06.24 | 16:47 | 19.06.24 | 20:36 | 3:49 | 0 | 20 | [5 empty] | At Padampur end: Earth Fault,Tripped due to jumper snapped at loc 156
|  | 20.07.24 | 21:08 | 20.07.24 | 21:32 | 0:24 | 0 | 24 | [5 empty] | At Padampur end: R-N, Ir- 0.315kA, Iy- 0.192kA, Ib- 0.481kA, Zone 1, Dist- 32.39km
|  | 01.08.24 | 20:34 | 01.08.24 | 20:52 | 0:18 | 0 | 18 | [5 empty] | At Nuapada end: O/C, Ir- 0.528kA, Ib- 0.53kA
|  | 18.08.24 | 07:01 | 18.08.24 | 7:40 | 7:40 | 0 | 23 | [5 empty] | At Padampur end: R-N, Ir- 1.99kA, Zone 1 At Nuapada end: R-N, Zone 1, Dist- 51.38km, Ir- 0.118kA
|  | 19.08.24 | 11:27 | 19.08.24 | 11:42 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,SOURCE FAILURE
|  | 24.08.24 | 01:51 | 24.08.24 | 2:09 | 0:18 | 0 | 18 | [5 empty] | At Nuapada end: Remote End Tripping
|  | 27.08.24 | 19:19 | 27.08.24 | 19:55 | 0:36 | 0 | 10 | [5 empty] | At Padampur end: Dist Protection,PH-AN,Ia-257A,Ib-245A,Ic-504A,Zone 2
|  | 29.08.24 | 09:23 | 29.08.24 | 9:34 | 0:11 | 0 | 11 | [5 empty] | At Nuapada end: Dist Protection,Zone 1, Dist 47.24km, Started ph B,C tripped ph ABC Ia 149.7A, Ib 1.29kA Ic 1.61LA
|  | 25.09.24 | 04:44 | 25.09.24 | 4:59 | 0:15 | 0 | 15 | [5 empty] | At Nuapada end: Remote End Tripping,sousrece
|  | 13.01.25 | 09:43 | 13.01.25 | 9:50 | 0:07 | 0 | 7 | [5 empty] | At Nuapada end: O/C
|  | 21.01.25 | 06:01 | 21.01.25 | 6:03 | 0:02 | 0 | 2 | [5 empty] | At Nuapada end: Ir- 0.8kA, Ib- 0.45kA, Dist- 2.7km
|  | 25.01.25 | 03:13 | 25.01.25 | 3:15 | 0:02 | 0 | 2 | [5 empty] | At Nuapada end: O/C, Ir- 0.602kA, Ib- 0.499kA
|  | 15.01.25 | 7:03 | 15.01.25 | 13:50 | 6:47 | 0 | 35 | [5 empty] | At Padampur end: R-N, Ir- 0.44kA, Iy- 0.342kA, Ib- 0.627kA, Zone 1, Dist- 2.3km
|  | 17.01.25 | 10:43 | 17.01.25 | 10:51 | 0:08 | 0 | 8 | [5 empty] | At Padampur end: Tripped due to O/C. Tripped Phase:A, Ia=400.2A, Ib=372.2A, Ic=295.1A,In= 9.9A.
|  | 28.01.25 | 11:08 | 28.01.25 | 11:15 | 0:07 | 0 | 8 | [5 empty] | At Khariar end: Over Current, R-Ph 450A, Y-Ph 390A, B-Ph 350A At Kesinga end: Over Current,R-0.45 KA,Y-0.39 KA,B-0.35 KA
|  | 8.02.25 | 16:28 | 8.02.25 | 16:33 | 0:05 | 0 | 5 | [5 empty] | At Bolangir New end: Over CurrentIa=389A, Ib=400A, Ic=396A
|  | 22.02.25 | 17:50 | 22.02.25 | 18:02 | 0:12 | 0 | 12 | [5 empty] | Source failure
|  | 19.03.25 | 15:38 | 19.03.25 | 15:48 | 0:10 | 0 | 10 | [5 empty] | source failure
|  | 19.03.25 | 15:59 | 19.03.25 | 16:07 | 0:08 | 0 | 8 | [5 empty] | Tripped on Over current
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
494 | 132kV Salipur-Kendrapara |  |  |  |  | 0.36736 | 14 | 53 | [7 empty] | 34 | 8760 | 99.83% | 506.0333 | 297840
|  | 08.05.24 | 16:37 | 08.05.24 | 17:12 | 0:35 | 0 | 35 | [5 empty] | At Salipur end: Distance Protection,Tripped on DP, Zone-1, distance=17.05km, IR=72.9A, IY=2.96kA, IB=2.91kA, IN=26A At Kendrapara end: Distance Protection,Tripped on DP, Zone-1, distance=17.05km, IR=72.9A, IY=2.96kA, IB=2.91kA, IN=26A
|  | 12.08.24 | 15:56 | 12.08.24 | 18:11 | 2:15 | 0 | 47 | [5 empty] | Source failure at Paradeep end
|  | 19.08.24 | 17:50 | 19.08.24 | 18:54 | 1:04 | 1 | 4 | [5 empty] | At Kendrapara end: Dist Protection,Tripped on DP,Zone 1, Dist-27.58km, IR=3.2kA
|  | 29.09.24 | 22:43 | 29.09.24 | 22:46 | 0:03 | 0 | 3 | [5 empty] | At Salipur end: Relay Not Operated,No relay indication or tripping at Salipur end.
|  | 24.03.25 | 16:11 | 24.03.25 | 18:58 | 2:47 | 0 | 9 | [5 empty] | At Kendrapara end: Zone 1, Dist- 17.58km, Ir- 3.37kA, Iy- 3.34kA No tripping at Salipur end
|  | 25.03.25 | 10:32 | 25.03.25 | 12:37 | 2:05 | 0 | 15 | [5 empty] | At Kendrapara end:Tripped on DP with Zone-1. IR=206A, IY=431.2A IB=3.571kA IN=3.074kA Distance: 11.33 kms At Salipur end: Tripped on DP with Zone-1 Autorecloser Successful
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
495 | 132kV Samagara-Puri |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3.99 | 8760 | 100% | 0 | 34952.4
496 | 132kV Samagara-Malatipatpur RTSS |  |  |  |  | 0.39722 | 13 | 12 | [7 empty] | 5.535 | 8760 | 99.85% | 73.062 | 48486.6
|  | 06.04.24 | 11:09 | 06.04.24 | 13:21 | 2:12 | 0 | 28 | [5 empty] | At Nimapara end: B-N, Zone 1, Dist- 20.66km, Ib- 2.45kA At Samangara end: B-N, Zone 1, Dist- 12.4km, Ib- 0.5kA
|  | 26.04.24 | 07:26 | 26.04.24 | 07:45 | 0:19 | 0 | 18 | [5 empty] | Zone 1, Dist- 21.1km, Ir- 0.54kA
|  | 18.04.24 | 10:18 | 18.04.24 | 17:19 | 7:01 | 0 | 26 | [5 empty] | At Samangara end: Zone 1. Dist- 12.1km, Ib- 0.56kA At Nimapara end: B-N, Zone 1. Dist- 21.46km, Ib- 2.257kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
497 | 132kV Samagara-Satasankha Ckt-I |  |  |  |  | 0.030556 | 0 | 44 | [7 empty] | 28.07 | 8760 | 99.99% | 20.5847 | 245893.2
|  | 26.04.24 | 07:27 | 26.04.24 | 07:45 | 0:18 | 0 | 18 | [5 empty] | Remote end Tripping D/P, Zone 1, Ir- 0.54kA
|  | 18.04.24 | 10:18 | 18.04.24 | 10:44 | 0:26 | 0 | 26 | [5 empty] | At Samangara end: Zone 1. Dist- 12.1km, Ib- 0.56kA At Nimapara end: B-N, Zone 1. Dist- 21.46km, Ib- 2.257kA
498 | 132kV Samagara-Satasankha Ckt-II |  |  |  |  | 0.088194 | 14 | 7 | [7 empty] | 28.07 | 8760 | 99.84% | 396.2548 | 245893.2
|  | 26.04.24 | 07:27 | 26.04.24 | 07:45 | 0:18 | 0 | 18 | [5 empty] | Remote end Tripping D/P, Zone 1, Ir- 0.54kA
|  | 18.04.24 | 10:18 | 18.04.24 | 10:44 | 0:26 | 0 | 26 | [5 empty] | At Samangara end: Zone 1. Dist- 12.1km, Ib- 0.56kA At Nimapara end: B-N, Zone 1. Dist- 21.46km, Ib- 2.257kA
|  | 2024-10-19 | 17:53 | 2024-10-19 | 19:16 | 1:23 | 1 | 23 | [5 empty] | At Samangara end: Distance Protection, DP,ZONE-2,IL1=2.89 KA,IL2=0.01 KA,IL3=0.01 KA,DIST.=24.9 KM At Satasankha end: Distance Protection, TRIPPED ON R-PHASE, Zone 1(1.05KM), IL1-2.944KA, IL2-86.18A, IL3-86.43
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
499 | 132kV Sambalpur-Shyam DRI |  |  |  |  | 0.78958 | 14 | 29 | [7 empty] | 28.91 | 8760 | 99.83% | 418.7132 | 253251.6
|  | 01.06.24 | 21:01 | 01.06.24 | 21:16 | 0:15 | 0 | 15 | [5 empty] | At Sambalpur end: Tripped on Z1, Yph E/F, Ia=231A, Ib=254A,Ic=220A, Ig=2238A, Fault dist.=25.72KM, fault duration= 167.433ms No tripping at Shyam DRI end.
|  | 13.06.24 | 19:43 | 13.06.24 | 20:07 | 0:24 | 0 | 24 | [5 empty] | At Sambalpur end: Z1, Yph E/F, Ia=12A, Ib=2573A,Ic=9A, Ig=2579A, Fault dist.=24.17KM, fault duration=56.712ms At Shyam DRI end: DP, Yph E/F,Fault distance=24.17km
|  | 16.06.24 | 1:29 | 19.06.24 | 45462.7882 | 17:26 | 0 | 58 | [5 empty] | At Sambalpur end: Tripped on Z1, Yph E/F, Ia=7.4A, Ib=4427A,Ic=4424A, Ig=62A, Fault dist.=3.26KM, fault duration=56.64ms
|  | 2024-10-08 | 14:20 | 2024-10-08 | 14:36 | 0:16 | 0 | 16 | [5 empty] | At SambaIpur end: tripped on Y ph E/F, Z1, Fault dist.=24.31Km, Fault duration= 114.258ms, Ia=159A, Ib=2620A, Ic=190A, In=2604A At Shyam DRI end: No tripping
|  | 12.12.24 | 14:45 | 12.12.24 | 15:21 | 0:36 | 0 | 36 | [5 empty] | At Sambalpur end: E/F (R Ph), Zone 1, Dist- 24.62km, ir- 2.472kA At Shyam DRI end: CB didn't trip, R Ph, E/F
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
500 | 132kV Shamuka-Puri |  |  |  |  | 0.33819 | 0 | 15 | [7 empty] | 16.9 | 8760 | 100% | 4.225 | 148044
|  | 13.06.24 | 23:58 | 13.06.24 | 45457.3368 | 8:07 | 0 | 15 | [5 empty] | At Atri end: Distance Protection,R-Y-B phase-N, Zone- 1, IR =4.598 kA, IY=4.496 kA, IB=4.614 kA, Distance- 23.19 km At Shamuka end: Remote End Tripping,Ir-4.598kA,Iy-4.496KA,Ib-4.614KA,DISTANCE-23.19, FAULT TYPE: 3Phase to ground, Zone-I
501 | 132kV Shyam DRI-Aryan Ispat |  |  |  |  | 0.72639 | 0 | 58 | [7 empty] | 4.2 | 8760 | 99.99% | 4.06 | 36792
|  | 16.06.24 | 1:29 | 19.06.24 | 45462.7882 | 17:26 | 0 | 58 | [5 empty] | At Sambalpur end: Tripped on Z1, Yph E/F, Ia=7.4A, Ib=4427A,Ic=4424A, Ig=62A, Fault dist.=3.26KM, fault duration=56.64ms
502 | 132kV Aryan Ispat - Lapanga |  |  |  |  | 0.18056 | 15 | 48 | [7 empty] | 3.9 | 8760 | 99.82% | 61.62 | 34164
|  | 13.06.24 | 19:20 | 13.06.24 | 20:17 | 0:57 | 0 | 57 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.18KA IL2-0.13KA IL3-11.10KA DIST-1.9KM
|  | 01.06.24 | 20:53 | 01.06.24 | 22:46 | 1:53 | 1 | 53 | [5 empty] | At Lapanga end: Distance Protection, MAIN RELAY-1:- FAULT LOOP-L1-L2 ZONE-1 IL1-9.2KA IL2-9.2KA IL3-0.02KA DIST-6.2KM
|  | 16.06.24 | 00:14 | 16.06.24 | 1:44 | 1:30 | 0 | 58 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L3-E ZONE-1 IL1-0.5KA IL2-0.05KA IL3-13.94KA DIST-1.9KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
503 | 132kV Lapanga-SMC Power |  |  |  |  | 0.39236 | 17 | 17 | [7 empty] | 4.7 | 8760 | 99.8% | 81.2317 | 41172
|  | 13.06.24 | 19:20 | 13.06.24 | 21:02 | 1:42 | 0 | 27 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.07KA IL2-10.45KA IL3-0.06KA DIST-1.8KM
|  | 01.06.24 | 20:00 | 02.06.24 | 0:08 | 4:08 | 1 | 15 | [5 empty] | At Lapanga end: Distance Protection, MAIN RELAY-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.06KA IL2-15.64KA IL3-0.06KA DIST-1.6KM
|  | 18.06.24 | 10:21 | 18.06.24 | 13:56 | 3:35 | 3 | 35 | [5 empty] | At Lapanga end: Distance Protection,LAPANGA END DETAILS MAIN-1:- FAULT LOOP-L2-E ZONE-1 IL1-0.05KA IL2-14.26KA IL3-0.06KA DIST-1.9KM
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
504 | 132kV SMC Power-Kuchinda |  |  |  |  | 0.52708 | 22 | 2 | [7 empty] | 52.53 | 8760 | 99.75% | 1157.411 | 460162.8
|  | 25.05.24 | 10:16 | 25.05.24 | 18:01 | 7:45 | 7 | 40 | [5 empty] | At Kuchinda end: Distance Protection,Relay indication at KCD end : Zone 2 , tripped ph-Y , Fault loc = 52.75 km , Ir=91.8A ,Iy =660A, Ib=96.8A ,Fault res= 12.11 ohm
|  | 13.06.24 | 19:20 | 13.06.24 | 19:47 | 0:27 | 0 | 27 | [5 empty] | At Kuchinda end: Distance Protection, zone-2, location=47.07km Tripped phase Yph,Fault duration=130.3ms, Ir=59.59A,Iy=723A, Ib=45.87A, Fault resistnace=9.832 Ohm" At SMC end: zone-1, Tripped phase Yph,Fault duration=137ms, Ir=55.17A,Iy=392.3A, Ib=74.71A"
|  | 02.06.24 | 19:05 | 02.06.24 | 21:40 | 2:35 | 0 | 23 | [5 empty] | At Kuchinda end: Distance Protection,Zone-1, Tripped Y, Fault location=28.30km, Ir=190.4A. Iy=851.8A, Ib=55.81A At SMC end: Zone-1, tripped ph R Y B,Fault Location=14.21km,Ir=190.8A, Iy=4.699kA, Ib=45.25A
|  | 20.06.24 | 16:09 | 20.06.24 | 16:41 | 0:32 | 0 | 17 | [5 empty] | At Kuchinda end: Distance Protection,zone-1, location=36.07km Tripped phase Yph,Fault duration=81.63ms, Ir=11.93A,Iy=655.5A, Ib=15.48A, Fault resistnace=45.59 Ohm At SMC end: zone-1, location=12.20km Tripped phase Yph,Fault duration=79.96ms, Ir=112.7A,Iy=4.791kA, Ib=36.35A, fault resistance=4.746 Ohm
|  | 01.06.24 | 20:47 | 01.06.24 | 22:07 | 1:20 | 1 | 15 | [5 empty] | At Kuchinda end: Earth Fault,Lapanga end data:rnE/F,Tripped ph R,rnIr=3kA, Disntance=1.6km ,Zone-1
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
505 | 132kV Soro-Bhadrak |  |  |  |  | 0.24583 | 1 | 8 | [7 empty] | 45.62 | 8760 | 99.99% | 51.7027 | 399631.2
|  | 12.05.24 | 14:58 | 12.05.24 | 18:04 | 3:06 | 0 | 51 | [5 empty] | At Bhadrak end: Distance Protection,IL1-914.2A,IL2-279.8A,IL3-147.3A, Zone-4,Distance-765.3Mtr
|  | 6.11.24 | 11:40 | 6.11.24 | 14:28 | 2:48 | 0 | 17 | [5 empty] | At Soro end: Distance Protection, Distance Protection Relay: Zone-1, Distance-32.799Km, Event-B-G, IA=94.4A, IB=0.979KA, Ic=100.4A, IN=1.192KA, VA=73.632KV, VB=26.68KV, VC=76.95KV. At Bhadrak end: Distance Protection Relay, Zone-2, Started phase B to N, Tripped phase A,B,C. Distance=36.04Km, IA=156.7A, IB=1.85KA, IC=155.9A, VAN=69.03KV, VBN=47.97KV, VCN=69.53KV.
506 | 132kV Jayanagar-Sunabeda -I |  |  |  |  | 0.31667 | 18 | 7 | [7 empty] | 40 | 8760 | 99.79% | 724.6667 | 350400
|  | 08.07.24 | 15:37 | 08.07.24 | 16:55 | 1:18 | 1 | 1 | [5 empty] | At Jayanagar end: R-Y, Zone 1, Dist- 7.0km, Ir=4.06kA, Iy=4.28kA
|  | 04.09.24 | 22:27 | 04.09.24 | 23:10 | 0:43 | 0 | 43 | [5 empty] | At Jayanagar end: Distance Protection,R-G, zone-1, dist=N/A, Ir=2.1kA
|  | 20.09.24 | 18:54 | 20.09.24 | 19:12 | 0:18 | 0 | 18 | [5 empty] | At Jayanagar end: Distance Protection,R-G, zone-1,dist=17.2km, Ir=3.0kA
|  | 24.03.25 | 02:38 | 24.03.25 | 7:55 | 5:17 | 4 | 5 | [5 empty] | At Jayanagar end: R-N, Zone 1, Dist- 7.3km, Ir- 0.75kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
507 | 132kV Jayanagar-Sunabeda -II |  |  |  |  | 0.24792 | 4 | 23 | [7 empty] | 39.63 | 4020 | 99.89% | 173.7115 | 159312.6
|  | 20.09.24 | 18:54 | 20.09.24 | 19:33 | 0:39 | 0 | 18 | [5 empty] | At Jayanagar end: Distance Protection,R-B, zone-1,dist=8km, Ir=3kA,Ib=7kA
|  | 24.03.25 | 02:38 | 24.03.25 | 7:56 | 5:18 | 4 | 5 | [5 empty] | At Jayanagar end: O/C, B-N, If- 0.268kA
508 | 132kV Sunabeda-Damanjodi (NALCO) |  |  |  |  | 0 | 0 | 0 | [7 empty] | 12.6 | 8760 | 100% | 0 | 110376
509 | 132kV Sunabeda-HAL |  |  |  |  | 0.15 | 13 | 50 | [7 empty] | 0.7 | 8760 | 99.84% | 9.6833 | 6132
|  | 30.05.24 | 11:35 | 30.05.24 | 11:58 | 0:23 | 0 | 23 | [5 empty] | At Potangi end: Remote End Tripping,Source failure at Sunabeda end.
|  | 01.06.24 | 17:37 | 01.06.24 | 19:32 | 1:55 | 0 | 26 | [5 empty] | Incomer failed and Change Over P/S from 132kV Sunabeda-Potangi Feeder to 132kV Podagada-Potangi Feeder .
|  | 08.07.24 | 15:37 | 08.07.24 | 16:55 | 1:18 | 1 | 1 | [5 empty] | At Jayanagar end: R-Y, Zone 1, Dist- 7.0km, Ir=4.06kA, Iy=4.28kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
510 | 132kV Sunabeda-Pottangi |  |  |  |  | 0.33889 | 18 | 13 | [7 empty] | 33 | 8760 | 99.79% | 601.15 | 289080
|  | 30.05.24 | 11:35 | 30.05.24 | 11:58 | 0:23 | 0 | 23 | [5 empty] | At Potangi end: Remote End Tripping,Source failure at Sunabeda end.
|  | 01.06.24 | 17:37 | 01.06.24 | 19:32 | 1:55 | 1 | 55 | [5 empty] | Incomer failed and Change Over P/S from 132kV Sunabeda-Potangi Feeder to 132kV Podagada-Potangi Feeder .
|  | 15.06.24 | 15:29 | 15.06.24 | 16:05 | 0:36 | 0 | 36 | [5 empty] | I/C failed at Sunabeda end on O/C ,E/F on R,Y,B- ph, IL1=2.19kA IL2 =3.05kA, IL3=2.51 KA
|  | 30.06.24 | 6:37 | 30.06.24 | 7:05 | 0:28 | 0 | 28 | [5 empty] | Incomer failure
|  | 30.06.24 | 7:32 | 30.06.24 | 7:56 | 0:24 | 0 | 24 | [5 empty] | Incomer failure
|  | 20.09.24 | 18:54 | 20.09.24 | 19:13 | 0:19 | 0 | 19 | [5 empty] | At Potangi end: Source failure at Sunabeda end.
|  | 28.12.24 | 9:36 | 28.12.24 | 10:25 | 0:49 | 0 | 49 | [5 empty] | I/C Power supply failure at Sunabeda end.
|  | 15.03.25 | 18:14 | 15.03.25 | 18:31 | 0:17 | 0 | 17 | [5 empty] | Incoming p/s failed from Sunabeda end
|  | 24.03.25 | 02:38 | 24.03.25 | 2:57 | 2:57 | 1 | 2 | [5 empty] | Failure from Dabugaon end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
511 | 132kV Tarkera-Kalunga |  |  |  |  | 0 | 0 | 0 | [7 empty] | 15.48 | 8760 | 100% | 0 | 135604.8
512 | 132kV Tarkera-Budhipadar-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 109 | 8760 | 100% | 0 | 954840
513 | 132kV Tarkera-Chhend-I |  |  |  |  | 0.10278 | 0 | 58 | [7 empty] | 6.165 | 8760 | 99.99% | 5.9595 | 54005.4
|  | 03.05.24 | 12:54 | 03.05.24 | 13:36 | 0:42 | 0 | 42 | [5 empty] | At Tarkera end: B-N, Zone 2, Ib- 5.225kA
|  | 25.11.24 | 20:15 | 25.11.24 | 22:01 | 1:46 | 0 | 16 | [5 empty] | At Chend end: Distance Protection,Distance-10.8km,Zone-1,Ia-156A,Ib-61A,Ic-148A,Ig-279A
514 | 132kV Tarkera-Chhend-II |  |  |  |  | 0.10278 | 0 | 58 | [7 empty] | 6.165 | 8760 | 99.99% | 5.9595 | 54005.4
|  | 03.05.24 | 12:54 | 03.05.24 | 13:36 | 0:42 | 0 | 42 | [5 empty] | At Tarkera end: B-N, Zone 2, Ib- 5.225kA
|  | 25.11.24 | 20:15 | 25.11.24 | 22:01 | 1:46 | 0 | 16 | [5 empty] | At Chend end: Distance Protection,Distance-6.95 km,Zone-1,Ia-181A,Ib-67A, Ic-131A,Ig-256A
515 | 132kV Tarkera-Rajgangpur-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 24.1 | 8760 | 100% | 0 | 211116
516 | 132kV Tarkera-Rajgangpur-II |  |  |  |  | 0.015972 | 0 | 23 | [7 empty] | 24.1 | 8760 | 100% | 9.2383 | 211116
|  | 9.12.24 | 07:20 | 9.12.24 | 7:43 | 0:23 | 0 | 23 | [5 empty] | At Tarkera end: R-Y, Dist- 44.413kA, Ir- 0.236kA, Iy- 0.872kA
517 | 132kV Tarkera-RSP-I |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
518 | 132kV Tarkera-RSP-II |  |  |  |  | 0 | 0 | 0 | [7 empty] | 11.04 | 8760 | 100% | 0 | 96710.4
519 | 132kV Tarkera-Rourkela-I |  |  |  |  | 0.043056 | 0 | 55 | [7 empty] | 3 | 8760 | 99.99% | 2.75 | 26280
|  | 25.11.24 | 21:17 | 25.11.24 | 22:19 | 1:02 | 0 | 55 | [5 empty] | H/Ted while exstingushing fire of Auto TRF-II
520 | 132kV Tarkera-Rourkela-II |  |  |  |  | 0.097917 | 2 | 7 | [7 empty] | 3 | 8760 | 99.98% | 6.35 | 26280
|  | 25.11.24 | 21:17 | 25.11.24 | 22:26 | 1:09 | 0 | 55 | [5 empty] | H/Ted while exstingushing fire of Auto TRF-II
|  | 4.02.25 | 15:57 | 4.02.25 | 17:09 | 1:12 | 1 | 12 | [5 empty] | At Rourkela end: Y-N, Zone 1, Dist- 1.33km, Iy- 5.598kA
521 | 132kV Tarkera-Rourkela-III |  |  |  |  | 0.1125 | 0 | 55 | [7 empty] | 3 | 8760 | 99.99% | 2.75 | 26280
|  | 25.11.24 | 20:15 | 25.11.24 | 22:57 | 2:42 | 0 | 55 | [5 empty] | At Rourkela end: R-N, Dist- 5.09km, Ir- 0.573kA, Zone 1
522 | 132kV Jayapatna- Dabugaon |  |  |  |  | 0.01875 | 0 | 27 | [7 empty] | 65.59 | 8760 | 99.99% | 29.5155 | 574568.4
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 2:51 | 0:13 | 0 | 13 | [5 empty] | At Jayapatna end: O/C (R-Y), Zone 3, Dist-134.1km, Ir- 0.461kA, Iy- 0.773kA
523 | 132kV Dabugaon -Umerkote |  |  |  |  | 0.13264 | 1 | 16 | [7 empty] | 45.49 | 8760 | 99.99% | 57.6207 | 398492.4
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 2:57 | 2:57 | 1 | 2 | [5 empty] | Failure from Dabugaon end.
524 | 132kV Tentulikhunti-Dabugaon |  |  |  |  | 0.10139 | 13 | 31 | [7 empty] | 42.8 | 8760 | 99.85% | 578.5133 | 374928
|  | 09.05.24 | 05:46 | 09.05.24 | 06:12 | 0:26 | 0 | 20 | [5 empty] | At Tentulikhunti end: Zone 2, Ir- 1.053kA, Ib- 1.047kA
|  | 01.06.24 | 15:19 | 01.06.24 | 16:13 | 0:54 | 0 | 42 | [5 empty] | At Dabugaon End: Distance Protection, Operated on zone 2 distance 39.54 KM with fault current in R Phase 0.995kA. At Tentulikhunti end: DP relay Operated, Zone-1, Distance=4.023KM, Ir= 2.695kA, Iy=212A,Ib= 69A
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 15 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
525 | 132kV Tentulikhunti-Vento Solar |  |  |  |  | 0.045833 | 0 | 29 | [7 empty] | 4.192 | 8760 | 99.99% | 2.0261 | 36721.92
|  | 24.03.25 | 04:36 | 24.03.25 | 4:50 | 0:14 | 0 | 14 | [5 empty] | At Jayapatna end: O/C (R-Y Ph), Ir- 0.398kA, Iy- 0.402kA
|  | 24.03.25 | 02:38 | 24.03.25 | 3:30 | 0:52 | 0 | 15 | [5 empty] | At Jayanagar end: O/C, Reverse protection Zone 5 of 656A (Y ph)
526 | 132kV Therubali-IMFA |  |  |  |  | 0 | 0 | 0 | [7 empty] | 2 | 8760 | 100% | 0 | 17520
527 | 132kV Therubali-JK Pur |  |  |  |  | 0 | 0 | 0 | [7 empty] | 9.68 | 8760 | 100% | 0 | 84796.8
528 | 132kV Therubali-Rayagada |  |  |  |  | 1899-12-31 02:12 | 13 | 50 | [7 empty] | 19.6 | 8760 | 99.84% | 271.1333 | 171696
|  | 20.04.24 | 16:57 | 20.04.24 | 17:25 | 0:28 | 0 | 28 | [5 empty] | At Therubali end: E/F (B-N), Ib- 3.6kA
|  | 02.06.24 | 20:39 | 03.06.24 | 14:20 | 17:41 | 0 | 45 | [5 empty] | At Rayagada end: Earth Fault,B-Phase E/F, Ib=9.8KA, Ig=9.8KA At Therubali end: Earth Fault,B-Phase E/F, Ib=9.8KA, Ig=9.8KA
|  | 19.07.24 | 10:11 | 19.07.24 | 18:14 | 8:03 | 0 | 37 | [5 empty] | At Therubali end: Earth Fault, YG,Iy=5.645kA, At Rayagada end: Earth Fault,Snapping of jumper,No data recorded at Rayagada end.
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
529 | 132kV Therubali-RTSS Bhalumaska |  |  |  |  | 0.065278 | 13 | 34 | [7 empty] | 31.1 | 8760 | 99.85% | 421.9233 | 272436
|  | 07.05.24 | 6:09 | 07.05.24 | 7:06 | 0:57 | 0 | 57 | [5 empty] | At Therubali end: B-N, Zone 1, Ib- 5.571kA
|  | 25.05.24 | 16:46 | 25.05.24 | 17:00 | 0:14 | 0 | 14 | [5 empty] | At Therubali end: C-N, 4.318KM, Ic=7.21KA
|  | 26.05.24 | 14:37 | 26.05.24 | 14:45 | 0:08 | 0 | 8 | [5 empty] | At Therubali end: C-N, 7.96KM, Ic=4.8KA
|  | 30.05.24 | 16:25 | 30.05.24 | 16:40 | 0:15 | 0 | 15 | [5 empty] | A-N, Z-1, 24.34KM, Ia=2.79KA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
530 | 132kV TTPS-Angul |  |  |  |  | 0.063194 | 0 | 37 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 15.6 | 8760 | 100% | 9.62 | 136656
|  | 20.06.24 | 19:38 | 20.06.24 | 21:09 | 1:31 | 0 | 37 | [5 empty] | At Angul end: Remote End Tripping
531 | 132kV TTPS-Chainpal-I |  |  |  |  | 0.086111 | 0 | 44 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 3 | 8760 | 99.99% | 2.2 | 26280
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 44 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
532 | 132kV TTPS-Chainpal-II |  |  |  |  | 0.15069 | 1 | 21 | [5 empty] | As per OERC Regulation 2014, outage hour is multiplied by factor 2. |  | 3 | 8760 | 99.98% | 4.05 | 26280
|  | 05.05.24 | 12:01 | 05.05.24 | 14:05 | 2:04 | 0 | 44 | [5 empty] | At TTPS end: 160MVA AUTO TRF-I tripped on O/C
|  | 20.06.24 | 19:38 | 20.06.24 | 21:11 | 1:33 | 0 | 37 | [5 empty] | At Chainpal end: Remote End Tripping,DISTANCE PROTECTION, DISTANCE=19.68KM, L1-N, IA=1.88KA
533 | 132kV TTPS-Chainpal-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 3 | 8760 | 100% | 0 | 26280
534 | 132kV TTPS- Gondia |  |  |  |  | 0.041667 | 12 | 55 | [7 empty] | 85.383 | 8760 | 99.85% | 1102.8637 | 747955.08
|  | 05.05.24 | 12:00 | 05.05.24 | 12:22 | 0:22 | 0 | 17 | [5 empty] | At Gondia end: Remote End Tripping, O/C
|  | 3.11.24 | 05:40 | 3.11.24 | 5:50 | 0:10 | 0 | 10 | [5 empty] | At Gondia end: Distance Protection,Ir- 0.06 KA, Iy- 0.17 KA , Ib- 1.10 KA
|  | 5.11.24 | 18:19 | 5.11.24 | 18:37 | 0:18 | 0 | 18 | [5 empty] | At Gondia end: Distance Protection,Ir- 1.10 KA, Iy- 0.09 KA , Ib- 0.18 KA
|  | 5.11.24 | 23:51 | 5.11.24 | 23:55 | 0:04 | 0 | 4 | [5 empty] | At Gondia end: Distance Protection,Ir- 1.17 KA, Iy- 0.08 KA , Ib- 0.20 KA
|  | 18.12.24 | 03:27 | 18.12.24 | 3:33 | 0:06 | 0 | 6 | [5 empty] | At Gondia end: Ir- 0.08 kA, Iy- 0.12 kA , Ib- 1.18 kA
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
535 | 132kV Gondia-Jabamayee FAlloys |  |  |  |  | 1899-12-31 00:56 | 13 | 54 | [7 empty] | 39.178 | 8760 | 99.84% | 544.5742 | 343199.28
|  | 05.05.24 | 12:00 | 05.05.24 | 12:43 | 12:43 | 0 | 17 | [5 empty] | At Gondia end: Remote End Tripping, O/C
|  | 02.06.24 | 20:18 | 02.06.24 | 20:45 | 0:28 | 0 | 25 | [5 empty] | At Gondia end: Remote End Tripping,Adjacent line (132kV JFAL-Duburi) tripped at remote end (Duburi end).
|  | 3.11.24 | 05:40 | 3.11.24 | 6:03 | 0:23 | 0 | 23 | [5 empty] | At Gondia end: Distance Protection,Ir-0.14 KA , Iy-0.04 KA , Ib-1.29 KA Dist-1.7 Kms Remote end tripping details Ir-131.6 A , Iy- 21.15 A ,Ib-1.897 KA Dist-31.54 Kms
|  | 5.11.24 | 18:19 | 5.11.24 | 18:58 | 0:39 | 0 | 18 | [5 empty] | At Gondia end: Distance Protection,Ir-1.29 KA , Iy-0.12 KA , Ib-0.01 KA Dist-1.0 Kms Remote end tripping details Ir-1.778 KA ,Iy- 132.2 A ,Ib-17.74 A,Dist-33.34 Kms
|  | 5.11.24 | 22:38 | 5.11.24 | 22:59 | 0:21 | 0 | 21 | [5 empty] | At Gondia end: Distance Protection,Ir-1.45 KA , Iy-0.18 KA , Ib-0.04 KA Dist-1.7 Kms Remote end tripping details Ir-1.818 KA , Iy- 157.7 A , Ib-25.63 A,Dist-30.00 Kms
|  | 5.11.24 | 23:51 | 6.11.24 | 9:48 | 9:57 | 0 | 4 | [5 empty] | At Gondia end: Distance Protection,Ir-1.44 KA , Iy-0.15 KA , Ib-0.04 KA Dist-1.7 Kms Remote end tripping details Ir-1.822 KA , Iy- 139.2 A , Ib-23.08 A , Dist-33.24 Kms
|  | 18.12.24 | 03:27 | 18.12.24 | 3:52 | 0:25 | 0 | 6 | [5 empty] | At Gondia end: Ir-0.11 kA , Iy-0.06 kA , Ib-1.36 kA Dist-9.6 Kms At TTPS end: Ir-109.3 A , Iy- 58.71 A , Ib-2.427 kA , Dist-26.79 Kms
| Addl. outage duration as per OERC Regulation 2014 | [5 empty] | 12 | 0
536 | 132kV TTPS-OPCL |  |  |  |  | 0 | 0 | 0 | [7 empty] | 31 | 8760 | 100% | 0 | 271560
537 | 132kV Tusura-Vento Solar |  |  |  |  | 0 | 0 | 0 | [7 empty] | 14.8 | 8760 | 100% | 0 | 129648
(17): 8839.4591; (20): 102046.6919; (21): 157049849.904 | 0.00064977
ICTs / AUTOS
1 | New Duburi 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 472.5 | 6898500
2 | New Duburi 315MVA ICT – II |  |  |  |  | 0.025 | 0 | 36 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
|  | 18.08.24 | 14:45 | 18.08.24 | 15:21 | 0:36 | 0 | 36 | [5 empty] | Differenial,NO RECORD
3 | Lapanga 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
4 | Lapanga 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
5 | Meramundali 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
6 | Meramundali 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
7 | Mendhasal 315MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
8 | Mendhasal 315MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
9 | Mendhasal 315MVA ICT – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 315 |  | 8760 | 100% | 0 | 6898500
10 | Aska New 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
11 | Aska New 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
12 | Atri 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
13 | Atri 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
14 | Balasore 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
15 | Balasore 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
16 | Balasore 160MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
17 | Bamra 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
18 | Bamra 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
19 | Bargarh New 160MVA Auto – I |  |  |  |  | 0.31736 | 0 | 30 | [6 empty] | 160 |  | 8760 | 99.99% | 200 | 3504000
|  | 2.11.24 | 03:23 | 2.11.24 | 11:00 | 7:37 | 0 | 30 | [5 empty] | Buchholz relay tripped
20 | Bargarh New 100MVA Auto – II |  |  |  |  | 0.020833 | 0 | 30 | [6 empty] | 100 |  | 8760 | 99.99% | 125 | 2190000
|  | 2.11.24 | 03:23 | 2.11.24 | 3:53 | 0:30 | 0 | 30 | [5 empty] | Over loading of Transformer
21 | Bidanasi 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
22 | Bidanasi 100MVA Auto - II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
23 | Bidanasi 160MVA Auto - III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
24 | Bhadrak 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
25 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
26 | Bhadrak 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
27 | Bhadrak 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
28 | Bhanjanagar 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
29 | Bhanjanagar 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
30 | Budhipadar 160MVA Auto – I |  |  |  |  | 0.015278 | 0 | 22 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
|  | 05.06.24 | 4:41 | 05.06.24 | 4:57 | 0:16 | 0 | 16 | [5 empty] | H/T for restoration of power supply
|  | 18.03.25 | 12:54 | 18.03.25 | 13:00 | 0:06 | 0 | 6 | [5 empty] | Ir- 0.297kA, Iy- 4.24kA, Ib- 0.933kA
31 | Budhipadar 160MVA Auto – II |  |  |  |  | 0.098611 | 2 | 22 | [6 empty] | 160 |  | 8760 | 99.97% | 946.6667 | 3504000
|  | 13.06.24 | 19:11 | 13.06.24 | 20:02 | 0:51 | 0 | 51 | [5 empty] | Busbar Protection relay operated.
|  | 05.06.24 | 4:41 | 05.06.24 | 6:12 | 1:31 | 1 | 31 | [5 empty] | H/T for restoration of power supply
32 | Chandaka 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
33 | Chandaka 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
34 | Chandaka 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
35 | Chandaka 160MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
36 | Chandaka-B 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
37 | Chandaka-B 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
38 | Cuttack 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
39 | Cuttack 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
40 | Dhamara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
41 | Dhamara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
42 | Duburi 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
43 | Duburi 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
44 | Duburi 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
45 | Duburi 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
46 | Goda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
47 | Goda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
48 | Gunupur 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
49 | Gunupur 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
50 | Jayanagar 160MVA Auto – I |  |  |  |  | 0.18403 | 1 | 26 | [6 empty] | 160 |  | 8760 | 99.98% | 573.3333 | 3504000
|  | 24.03.25 | 02:38 | 24.03.25 | 7:03 | 4:25 | 1 | 26 | [5 empty] | At Jayanagar end: O/C, If- 4kA
51 | Jayanagar 160MVA Auto – II |  |  |  |  | 0.2625 | 1 | 26 | [6 empty] | 160 |  | 8760 | 99.98% | 573.3333 | 3504000
|  | 24.03.25 | 02:38 | 24.03.25 | 8:56 | 6:18 | 1 | 26 | [5 empty] | At Jayanagar end: O/C, If- 4kA
52 | Jayapatna 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
53 | Jayapatna 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
54 | Joda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
55 | Joda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
56 | Joda 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
57 | Katapalli 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
58 | Katapalli 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
59 | Katapalli 160MVA Auto – III |  |  |  |  | 0.038194 | 0 | 21 | [6 empty] | 160 |  | 8760 | 100% | 140 | 3504000
|  | 23.05.24 | 19:14 | 23.05.24 | 20:09 | 0:55 | 0 | 21 | [5 empty] | At Katapali end: Earth Fault,Tripped with differential pick up and back relay pick up , weather condition is windy and heavy lightning
60 | Kesinga 160MVA Auto – I |  |  |  |  | 0.015278 | 0 | 22 | [6 empty] | 160 |  | 8760 | 100% | 146.6667 | 3504000
|  | 21.09.24 | 23:48 | 22.09.24 | 0:10 | 0:22 | 0 | 22 | [5 empty] | Over Current,R ph-1.2 KA,Y ph-1.2 KA, B ph- 0.5 KA
61 | Kesinga 160MVA Auto – II |  |  |  |  | 0.039583 | 0 | 22 | [6 empty] | 160 |  | 8760 | 100% | 146.6667 | 3504000
|  | 21.09.24 | 23:48 | 22.09.24 | 0:45 | 0:57 | 0 | 22 | [5 empty] | Over Current,R ph-903.6 A,Y ph-235 A,B ph-503 A
62 | Kuarnmunda 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
62 | Kuarnmunda 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 6324 | 100% | 0 | 2529600
63 | Lapanga 160MVA Auto – I |  |  |  |  | 0.018056 | 0 | 26 | [6 empty] | 160 |  | 8760 | 100% | 173.3333 | 3504000
|  | 01.04.24 | 8:53 | 01.04.24 | 09:19 | 0:26 | 0 | 26 | [5 empty] | O/C, Ir- 2.18kA, Iy- 0.76kA, Ib- 0.23kA. R Ph insulator burst at Loc No 118 from Lapanga end.
64 | Lapanga 160MVA Auto – II |  |  |  |  | 0.052083 | 1 | 15 | [6 empty] | 160 |  | 8760 | 99.99% | 500 | 3504000
|  | 01.04.24 | 8:53 | 01.04.24 | 09:19 | 0:26 | 0 | 26 | [5 empty] | O/C, Ir- 2.18kA, Iy- 0.76kA, Ib- 0.23kA. R Ph insulator burst at Loc No 118 from Lapanga end.
|  | 05.06.24 | 04:11 | 05.06.24 | 5:00 | 0:49 | 0 | 49 | [5 empty] | At Lapanga end: Differenial
65 | Mendhasal 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
66 | Mendhasal 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
67 | Meramundali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
68 | Meramundali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
69 | Meramundali 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
70 | Meramundali-B 500MVA ICT – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 500 |  | 8760 | 100% | 0 | 10950000
71 | Meramundali-B 500MVA ICT – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 500 |  | 8760 | 100% | 0 | 10950000
72 | Narendrapur 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
73 | Narendrapur 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
74 | Narendrapur 100MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
75 | New Bolangir 160MVA Auto I |  |  |  |  | 0.0090278 | 0 | 13 | [6 empty] | 160 |  | 8760 | 100% | 86.6667 | 3504000
|  | 19.04.24 | 16:27 | 19.04.24 | 16:40 | 0:13 | 0 | 13 | [5 empty] | Remote end Tripping
76 | New Bolangir 160 MVA Auto II |  |  |  |  | 0.015972 | 0 | 23 | [6 empty] | 160 |  | 8760 | 100% | 153.3333 | 3504000
|  | 19.04.24 | 16:27 | 19.04.24 | 16:50 | 0:23 | 0 | 23 | [5 empty] | Remote end Tripping
77 | New Bolangir 160 MVA Auto III |  |  |  |  | 0.015972 | 0 | 23 | [6 empty] | 160 |  | 8760 | 100% | 153.3333 | 3504000
|  | 19.04.24 | 16:27 | 19.04.24 | 16:50 | 0:23 | 0 | 23 | [5 empty] | Remote end Tripping
78 | Paradeep 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
79 | Paradeep 160 MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
80 | Paradeep 160 MVA Auto – III |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
81 | Pratapsasan 160 MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
82 | Pratapsasan 160 MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
83 | Samagara 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
84 | Samagara 160MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 8760 | 100% | 0 | 3504000
85 | Tarkera 100MVA Auto – I |  |  |  |  | 0.067361 | 0 | 55 | [6 empty] | 100 |  | 8760 | 99.99% | 229.1667 | 2190000
|  | 25.11.24 | 20:37 | 25.11.24 | 22:14 | 1:37 | 0 | 55 | [5 empty] | H/Ted while exstingushing fire of Auto TRF-II
86 | Tarkera 100MVA Auto – II |  |  |  |  | 0.067361 | 0 | 55 | [6 empty] | 100 |  | 8760 | 99.99% | 229.1667 | 2190000
|  | 25.11.24 | 18:30 | 25.11.24 | 20:07 | 1:37 | 0 | 55 | [5 empty] | OSR,OSR TRIP, MASTER RELAY OPERATED
87 | Tarkera 100MVA Auto – III |  |  |  |  | 0.059028 | 0 | 55 | [6 empty] | 100 |  | 8760 | 99.99% | 229.1667 | 2190000
|  | 25.11.24 | 20:37 | 25.11.24 | 22:02 | 1:25 | 0 | 55 | [5 empty] | H/Ted while exstingushing fire of Auto TRF-II
88 | Tarkera 100MVA Auto – IV |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
89 | Therubali 100MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 41.6667 | 2190000
90 | Therubali 100MVA Auto – II |  |  |  |  | 0 | 0 | 0 | [6 empty] | 100 |  | 8760 | 100% | 0 | 2190000
91 | Therubali 160MVA Auto –III |  |  |  |  | 0.10694 | 0 | 10 | [6 empty] | 160 |  | 8760 | 100% | 66.6667 | 3504000
|  | 06.06.24 | 18:31 | 06.06.24 | 21:05 | 2:34 | 0 | 10 | [5 empty] | Tripped due to overfluxing.
92 | Turumunga 160MVA Auto – I |  |  |  |  | 0 | 0 | 0 | [6 empty] | 160 |  | 6060 | 100% | 0 | 2424000
15395
(16): Sub-total (ICTs / Autos); (20): 5186.6667; (21): 335096100 | 1.5478e-05 | 99.9985
[15 empty] | TOTAL (Lines, ICTs & Autos) |  |  |  | 107233.3586 | 492145949.904
[11 empty] | NAFY |  | [ Σ ( OH l x Cktkm l x NSC l ) + Σ ( OH t x MVA t x 2.5 )] [THY x { Σ (Cktkm l x NSC l ) +Σ (MVA t x 2.5 ) } ] | [5 empty] | 0.00021789
[13 empty] | 100 - (100 X NAFY) | [5 empty] | 99.9782

## ANNEXURE-III
Transmission Element Data as on 31/03/17 ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
a) Transmission Lines
SL. NO | Name of the Transmission line |  | Voltage Level(in KV) | S/C or D/C | Line Length (in Ckt KM) | Conductor Type & Characteristics | No. of Sub-Conductor (NSC) | Date of Comm. / Comm. Operation
| From | To
1 | Rengali-Kuchei PG | Kolaghat PG | 400 | S/C | 483 | Twin Moose | 2 | 1995
2 | Indravati PH | Indravati PG | 400 | S/C | 7.4 | Twin Moose | 2 | 03/09/09
3 | Meramundal I | Mendhasal I | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
4 | Meramundal I | Mendhasal II | 400 | D/C | 100.45 | Twin Moose | 2 | 31/01/10
3 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
4 | Meramundal I | New Duburi | 400 | D/C | 96.8 | Twin Moose | 2 | 19/10/15
5 | Meramundali | JSPL I | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
6 | Meramundali | JSPL II | 400 | D/C | 75.83 | Twin Moose | 2 | 16/09/2010
7 | Balimela | U. Seluru | 220 | S/C | 24.76 | Single Zebra | 1 | 1982
8 | Balimela | Jayanagar-I | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
9 | Balimela | Jayanagar-II | 220 | D/C | 92.072 | Single Zebra | 1 | 1974
10 | Balimela | Jayanagar-III | 220 | S/C | 93.46 | Single Zebra | 1 | 1982
11 | Balasore | Bhadrak | 220 | S/C | 80 | Single Zebra | 1 | 22.10.08
12 | Barkote | Tarkera | 220 | D/C | 97.48 | Single Zebra | 1 | 1979
13 | Bhanjanagar | Meramundali-I | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
14 | Bhanjanagar | Meramundali-II | 220 | D/C | 134.135 | Single Zebra | 1 | 1974
15 | Bhanjanagar | Mendhasal | 220 | D/C | 156 | Single Zebra | 1 | 1989
16 | Bhanjanagar | Nayagarh | 220 | D/C | 46.47 | Single Zebra | 1 | 1989
17 | Bidanasi | Mendhasal ckt II | 220 | D/C | 15 | Single Zebra | 1 | 2008
18 | Bidanasi | Mendhasal ckt III | 220 | D/C | 15 | Single Zebra | 1 | 2008
19 | Bisra | Tarkera-I | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
20 | Bisra | Tarkera-II | 220 | D/C | 15.335 | Single Zebra | 1 | 1993
21 | Budhipadar | IbTPS -I | 220 | D/C | 26 | Single Zebra | 1 | 1995
22 | Budhipadar | IbTPS -II | 220 | D/C | 26 | Single Zebra | 1 | 1995
23 | Budhipadar | IbTPS -III | 220 | D/C | 25.38 | Single Zebra | 1 | 1995
24 | Budhipadar | IbTPS -IV | 220 | D/C | 25.38 | Single Zebra | 1 | 07/01/08
25 | Budhipadar | Raigarh | 220 | D/C | 60 | Single Zebra | 1 | 1995
26 | Budhipadar | Korba-II | 220 | D/C | 60 | Single Zebra | 1 | 1995
27 | Budhipadar | Katapalli -I | 220 | D/C | 61.679 | Single Zebra | 1 | 20/04/07
28 | Budhipadar | Katapalli -II | 220 | D/C | 61.769 | Single Zebra | 1 | 20/04/07
29 | Budhipadar | SPS I | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
30 | Budhipadar | SPS II | 220 | D/C | 13.424 | Single Zebra | 1 | 07/11/07
31 | Budhipadar | Bhusan Steel-I | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
32 | Budhipadar | Bhusan Steel-II | 220 | D/C | 14.92 | Single Zebra | 1 | 06/08/05
33 | Chandaka | Mendhasal ckt I | 220 | D/C | 19 | Single Zebra | 1 | 2008
34 | Chandaka | Mendhasal ckt II | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
35 | Chandaka | Mendhasal ckt III | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
36 | Chandaka | Mendhasal ckt IV | 220 | D/C | 19.9 | Single Zebra | 1 | 2008
37 | Duburi | Duburi (New) ckt I | 220 | D/C | 11.056 | Single Zebra | 1 | 1996
38 | Duburi | Duburi (New) ckt II | 220 | D/C | 11.056 | Single Zebra | 1 | 1997
39 | Duburi | NINL | 220 | S/C | 6 | Single Zebra | 1 | 01/06/2000
40 | Duburi (New) | Balasore | 220 | D/C | 137.36 | Single Zebra | 1 | 1997
41 | Indravati PH | Therubali-I | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
42 | Indravati PH | Therubali-II | 220 | D/C | 86.2 | Single Zebra | 1 | 26/05/01
43 | Indravati PH | Therubali-III | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
44 | Indravati PH | Therubali-IV | 220 | D/C | 91 | Single Zebra | 1 | 22/07/05
45 | Jayanagar | Jeyapore PG-I | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
46 | Jayanagar | Jeyapore PG-II | 220 | D/C | 7.23 | Single Zebra | 1 | 1990
47 | Jayanagar | Laxmipur ckt I | 220 | D/C | 65 | Single Zebra | 1 | 1974
48 | Jayanagar | Laxmipur Ckt II | 220 | D/C | 65 | Single Zebra | 1 | 1974
49 | Jindal | Jamsedpur DVC | 220 | S/C | 20.8 | Single Zebra | 1 | 1985
50 | Joda | RCPur PG | 220 | S/C | 15.5 | Single Zebra | 1 | 1985
51 | Joda | Jindal | 220 | S/C | 21 | Single Zebra | 1 | 1985
52 | Joda | TSIL Ckt. | 220 | S/C | 7.3 | Single Zebra | 1 | 23/03/07
53 | Katapali | Bolangir-I | 220 | D/C | 117.85 | Single Zebra | 1 | 2010
54 | Katapali | Bolangir-II | 220 | D/C | 117.85 | Single Zebra | 1 | 2011
55 | Kuchei PG | Balasore Ckt I | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
56 | Kuchei PG | Balasore Ckt II | 220 | D/C | 76.859 | Single Zebra | 1 | 03/10/07
57 | Laxmipur | Therubali Ckt I | 220 | D/C | 56 | Single Zebra | 1 | 1974
58 | Laxmipur | Therubali Ckt II | 220 | D/C | 56 | Single Zebra | 1 | 1974
59 | Laxmipur | Utkal Alu,ina Ckt I | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
60 | Laxmipur | Utkal Alu,ina Ckt II | 220 | D/C | 31.04 | Single Zebra | 1 | 2014
61 | Mendhasal | Bidanasi-II | 220 | D/C | 32.99 | Single Zebra | 1 | 2003
62 | Meramundali | Bidanasi-II | 220 | D/C | 90.94 | Single Zebra | 1 | 2003
63 | Meramundali | Duburi-I | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
64 | Meramundali | Duburi-II | 220 | D/C | 95.556 | Single Zebra | 1 | 1995
65 | Meramundali | BSSL (Bhusan) I | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
66 | Meramundali | BSSL (Bhusan) II | 220 | D/C | 2.4 | Single Zebra | 1 | 22/08/06
67 | NALCO | Meramundali-I | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
68 | NALCO | Meramundali-II | 220 | D/C | 11.465 | Single Zebra | 1 | 27/08/04
69 | NALCO | Rengali PH | 220 | S/C | 71.337 | Single Zebra | 1 | 1984
70 | Nayagarh | Mendhasal | 220 | D/C | 90 | Single Zebra | 1 | 1989
71 | Narendrapur | Mendhasal I | 220 | D/C | 75 | Single Zebra | 1 | 02/07/2010
72 | New Duburi | Paradeep Ckt-I | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
73 | New Duburi | Paradeep Ckt-II | 220 | D/C | 113.433 | Single Zebra | 1 | 06/05/09
74 | Rengali GD | Rengali PG -I | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
75 | Rengali GD | Rengali PG -II | 220 | D/C | 0.4 | Single Zebra | 1 | 1997
76 | Rengali GD | Chandiposh (T) | 220 | D/C | 162.08 | Single Zebra | 1 | 26/03/2000
77 | Rengali GD | Barkote | 220 | D/C | 55 | Single Zebra | 1 | 1979
78 | Rengali PH | Rengali GD -I | 220 | D/C | 5 | Single Zebra | 1 | 1997
79 | Rengali PH | Rengali GD -II | 220 | D/C | 5 | Single Zebra | 1 | 1997
80 | Rengali PH | STPS | 220 | S/C | 29.5 | Single Zebra | 1 | 1984
81 | STPS (Kaniha) | TTPS | 220 | S/C | 34.5 | Single Zebra | 1 | 1984
82 | STPS | Meramundali-I | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
83 | STPS | Meramundali-II | 220 | D/C | 42.52 | Single Zebra | 1 | 1995
84 | Tarkera | Budhipadar-I | 220 | D/C | 109 | Single Zebra | 1 | 1995
85 | Tarkera | Budhipadar-II | 220 | D/C | 109 | Single Zebra | 1 | 1995
86 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 2008
87 | Tarkera | RSP I | 220 | D/C | 10 | Single Zebra | 1 | 1995
88 | Therubali | Narendrapur-I | 220 | D/C | 196 | Single Zebra | 1 | 2013
89 | Therubali | Narendrapur-II | 220 | D/C | 196 | Single Zebra | 1 | 20/08/2001
90 | Therubali | Bhanjanagar-I | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
91 | Therubali | Bhanjanagar-II | 220 | D/C | 171.46 | Single Zebra | 1 | 1974
92 | TTPS | Meramundali-I | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
93 | TTPS | Meramundali-II | 220 | D/C | 11.155 | Single Zebra | 1 | 1979
94 | TTPS | Joda-I | 220 | D/C | 154 | Single Zebra | 1 | 1967
95 | TTPS | Joda-II | 220 | D/C | 154 | Single Zebra | 1 | 1970
96 | U. Kolab | Jayanagar-I | 220 | D/C | 6 | Single Zebra | 1 | 1987
97 | U. Kolab | Jayanagar-II | 220 | D/C | 6 | Single Zebra | 1 | 1987
98 | U. Kolab | Therubali | 220 | S/C | 128 | Single Zebra | 1 | 1984
Transmission Element Data as on 31/03/17 | [6 empty] | ANNEXURE-III
Name of the Transmission licensee: ODISHA POWER TRANSMISSION CORPORATION LTD
b) Sub Stations
SL. NO | Name of the Sub-Station |  | Voltage Level(in KV) | NO. of ICTs/ AUTOs | MVA Capacity of ICTs / Autos | Date of Commissioning | Date of Comml. Operation
1 | MERAMUNDALI |  | 400/220/132 | 2 | 315 | 02/06/05
|  |  | 220/132 | 2 | 100 | 2002
|  |  |  | 1 | 100 | 2014 | 19.03.2014
2 | MENDHASAL |  | 400/220 | 2 | 315 | 2010
|  |  | 220/132 | 1 | 100 | 2006
|  |  | 220/132 | 1 | 100 | 2010
|  |  | 220/132 | 1 | 100 | 2014
3 | BIDANASI |  | 220/132 | 2 | 100 | 2004
|  |  |  | 1 | 100 | 2013 | 17.07.2013
5 | BHANJANAGAR |  | 220/132 | 2 | 160 | 1984,2014 | 05.01.2014
6 | BHADRAK |  | 220/132 | 2 | 100 | 2008,2009
7 | CHANDAKA |  | 220/132 | 2 | 160 | 2012
|  |  |  | 2 | 100 | 1989
8 | CUTTACK |  | 220/132 | 1 | 160 | 2017
9 | NARENDRAPUR |  | 220/132 | 2 | 160 | 1999
|  |  |  | 1 | 100 | 2012
10 | THERUBALI |  | 220/132 | 2 | 100 | 1981
11 | BALASORE |  | 220/132 | 2 | 160 | 2012
12 | JAYANAGAR |  | 220/132 | 2 | 100 | 1997
13 | DUBURI |  | 220/132 | 3 | 100 | 1989
14 | BUDHIPADAR |  | 220/132 | 2 | 160 | 1995
15 | TARKERA |  | 220/132 | 4 | 100 | 1981
16 | JODA |  | 220/132 | 2 | 100 | 1969
17 | KATAPALLI |  | 220/132 | 2 | 100 | 2007
18 | PARADEEP |  | 220/132 | 2 | 100,160,50 | 2009,2011,2009
19 | BOLANGIR NEW |  | 220/132 | 3 | 100 | 2011,2014 | 05.05.2014
20 | LAPANGA |  | 220/132 | 2 | 160 | 2014
21 | ATRI |  | 220/132 | 2 | 160 | 2016
22 | SAMANGARA |  | 220/132 | 2 | 160 | 2015,2016

## Lines not owned by OPTCL
PERIOD : 2019-20
Sl. No. | Name of the Transmission Element | OUTAGE |  | RESTORATION |  | OUTAGE PERIOD | DURATION OF OUTAGE ATTRIBUTABLE TO | [5 empty] | Deemed Availability | Reason of Outage | MVA capacity for ICTs / Autos | Ckm and number of Sub-Conductor for lines | Time considered for availability (hrs) (365 X 24) | Element wise availbility (C19 - C7 - C8/60) / C19 | ( OH l x Cktkm l x NSC l ) ( OH t x MVA t x 2.5 ) | (THY x Ckt KM X NSC) (THY X MVA x 2.5)
|  | DATE | TIME | DATE | TIME |  | UTILITY ITSELF |  | OTHERS |  | System Constraints/Natural Calamities
|  | dd/mm/yy | hh:mm | dd/mm/yy | hh:mm | hh:mm | Hrs | Min | Hrs | Min | Hrs | Min
(1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13) | (14) | (15) | (16) | (17) | (18) | (19) | (20) | (21)
44 | 220kV Budhipadar-Korba-III |  |  |  |  | 0 | 0 | 0 | [7 empty] | 60 | 8760 | 100% | 0 | 525600
34 | 220kV Budhipadar-Vedant Ckt.-I |  |  |  |  | 0.16389 | 15 | 27 | [7 empty] | 16.67 | 8760 | 99.82% | 257.5515 | 146029.2
|  | 30.06.19 | 1:06 | 30.06.19 | 1:22 | 0:16 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
|  | 2020-04-27 | 2:48 | 2020-04-27 | 4:40 | 0:23 | 0 | 23 | [5 empty] | At Budhipadar-D/P-I I) Dist Gen Trip, II) Relay Trip L1, III)Relay Trip L2 IV) Relay Trip L3, V) Zone-I, FL = AG, Ia=16.12 KA D/P-II(SIEMENS SIPROTEC 7SA52)-I) Dist Gen Trip II) Relay Trip L1, III)Relay Trip L2, IV) Relay Trip L3 V) Zone-I,FL = AG, Ia=16.21 KA
34 | 220kV Budhipadar-Vedant Ckt.-II |  |  |  |  | 0.16389 | 15 | 27 | [7 empty] | 16.67 | 8760 | 99.82% | 257.5515 | 146029.2
|  | 30.06.19 | 1:05 | 30.06.19 | 1:42 | 0:37 | 0 | 16
|  | 12.06.19 | 0:37 | 13.06.19 | 1:39 | 1:02 | 0 | 50 | [5 empty] | Y-Ph. LA failure and gantry jumper snapped at Budhipadar S/s lead to total blackout at Budhipadar S/s
345 | 132 kV Palasponga - Essar |  |  |  |  | 0.0055556 | 0 | 8 | [7 empty] | 19.093 | 8760 | 100% | 2.5457 | 167254.68
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 22.12.19 | 0:25 | 22.12.19 | 0:35 | 0.0069444 | 0 | 10 | [5 empty] | At Polasponga end-Tripped on; O/C & E/F, Ia=0.48KA, Ib=0.54KA, Ic=0.53KA
|  | 26.12.19 | 2:58 | 26.12.19 | 3:06 | 0.0055556 | 0 | 8 | [5 empty] | At Polasponga end-Tripped on;O/C & E/F, Ia=0.16KA, Ib=0.24KA, Ic=0.33KA
|  | 22.10.19 | 15:07 | 22.10.19 | 15:11 | 0.0027778 | 0 | 4 | [5 empty] | Tripped on Over current & Earth Fault at Polasponga end
|  | 06.10.19 | 15:25 | 06.10.19 | 16:00 | 0.024306 | 0 | 35 | [5 empty] | Tripped on E/F at Palasponga end.
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.
|  | 29.04.19 | 21:33 | 29.04.19 | 21:38 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 405A, Ib= 340A, Ic= 242.8A, In= 0.1A, Ig= 4.66A
|  | 28.04.19 | 15:06 | 28.04.19 | 15:09 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia= 423.4A, Ib= 355.9A, Ic= 309.8A, In= 0.09A, Ig= 2.4A
|  | 25.04.19 | 7:58 | 25.04.19 | 8:06 | 0.0055556 | 0 | 8 | [5 empty] | O/C,E/F (Y PH), Ia= 221.5A, Ib= 654.1A, Ic=161.2A, In= 0.1A, Ig= 686.26A
|  | 25.04.19 | 23:41 | 25.04.19 | 23:46 | 0.0034722 | 0 | 5 | [5 empty] | O/C (R PH), Ia= 421A, Ib= 361A, Ic=277.7A, In= 0.03A, Ig= 3.12A
|  | 21.04.19 | 15.35 | 21.04.19 | 16:15 | 0.027778 | 0 | 40 | [5 empty] | SOURCE FAILURE but Restricted P/S availed from Karanjia GSS end.
|  | 16.04.19 | 1:17 | 16.04.19 | 1:21 | 0.0027778 | 0 | 4 | [5 empty] | O/C(R,PH),IA=415.3,IB=381.2,IC=353 IN=0.05,IG2.56
|  | 15.04.19 | 1:18 | 15.04.19 | 1:20 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia= 396.4A, Ib=376.6KA, Ic=388.0KA IN=0.05
|  | 14.04.19 | 0:09 | 14.04.19 | 0:11 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R,Y PH), Ia=416, Ib=338.5KA, Ic=347.5KA,IN=0.05,IG=5.95
|  | 14.04.19 | 4:03 | 14.04.19 | 4:06 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA , IN=0.0A, IG=1.1
|  | 13.04.19 | 5:25 | 13.04.19 | 5:34 | 0.00625 | 0 | 9 | [5 empty] | O/C (B PH), Ia=1532A, Ib= 1037A, Ic=366.2, In= 0.00A, Ig= 4.9A
|  | 12.04.19 | 16:38 | 12.04.19 | 16:40 | 0.0013889 | 0 | 2 | [5 empty] | E/F WITH DP Z, Ia=80.81A, Ib=1.019KA, Ic=55.05, In=1.052KA, Ig= 1.05KA
|  | 07.04.19 | 16:01 | 07.04.19 | 16:03 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia=396.4A, Ib= 376.04A, Ic=388.84A Ig=51.8A
|  | 02.04.19 | 0.275 | 02.04.19 | 6:39 | 0.0020833 | 0 | 3 | [5 empty] | O/C (R PH), Ia=414.1A, Ib= 341.7A, Ic=285.9A, In= 0.09A, Ig= 5.73A
|  | 02.04.19 | 3:02 | 02.04.19 | 3:05 | 0.0020833 | 0 | 3 | [5 empty] | O/C (B PH), Ia= 435.38A, Ib= 355.4A, Ic=333.3A, In= 0.0A, Ig= 3.94A
|  | 01.04.19 | 20:53 | 01.04.19 | 20:55 | 0.0013889 | 0 | 2 | [5 empty] | O/C (R PH), Ia= 421.5A, Ib= 364.0A, Ic= 388.0A, In= 0.05A, Ig= 5.56A
345 | 132 kV Palasponga - MSP | [14 empty] | 7.5 | 8760 | 100% | 0 | 65700
|  | 19.03.20 | 17:06 | 19.03.20 | 17:34 | 0.019444 | 0 | 28 | [5 empty] | At Polasponga end: E/F ZONE1 , Ia=264A, Ib=240A, Ic=152A, IG= 451A
|  | 12.03.20 | 12:42 | 12.03.20 | 12:55 | 0.0090278 | 0 | 13 | [5 empty] | At Polasponga end: E/F ZONE1 LOC 32.85KM, Ia=202.1A, Ib=203A, Ic=79A, IG= 427A
|  | 29.10.19 | 14:05 | 29.10.19 | 14:11 | 0.0041667 | 0 | 6 | [5 empty] | At Palasponga-Tripped
|  | 28.10.19 | 10:17 | 28.10.19 | 10:27 | 0.0069444 | 0 | 10 | [5 empty] | Tripped From Karanjia Grid s/s
|  | 16.10.19 | 1:27 | 16.10.19 | 1:29 | 0.0013889 | 0 | 2 | [5 empty] | Tripped at Palasponga end; O/C & E/F, Ia=341.3A, Ib=844.1A, Ic=148.9A, In =0.09A, Ig = 386.63A
|  | 06.10.19 | 14:34 | 06.10.19 | 15:15 | 0.028472 | 0 | 41 | [5 empty] | Tripped at Joda end.
|  | 04.10.19 | 21:13 | 04.10.19 | 21:15 | 0.0013889 | 0 | 2 | [5 empty] | At Polasponga end: O/C R-ph, Ia=431.3A, Ib=363.6A, Ic=280.1A, In =0.04A
|  | 15.09.19 | 18:42 | 15.09.19 | 18:46 | 0.0027778 | 0 | 4 | [5 empty] | At Polasponga end;- O/C (R PH), Ia=423.0A, Ib=341.2A, Ic=288.2A, In =0.01A, Ig = 2.91A
|  | 19.07.19 | 19:25 | 19.07.19 | 21:06 | 0.070139 | 0 | 23 | [5 empty] | 132 kV main bus conductor snapped at Joda Grid S/s which led to complete 132 kV black out.Polasponga GSS availed P/S at 19:48 Hrs from Karanjia GSS.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 31.05.19 | 16:32 | 31.05.19 | 16:40 | 0.0055556 | 0 | 8 | [5 empty] | Tripped at Joda end; E/F (Y PH) WITH DP Z-1, Ia= 234A, Ib= 182A, Ic=133A, In= 0.1A, Ig= 339A
|  | 28.05.19 | 14.35 | 28.05.19 | 15.15 | 0.027778 | 0 | 40 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end.
|  | 09.05.19 | 14.15 | 09.05.19 | 14.18 | 0.0020833 | 0 | 3 | [5 empty] | Tripped at Joda end; O/C (R,Y PH), Ia=411.1KA, Ib=350.82KA, Ic=331.3KA ,IN=0.0A,IG=1.1
|  | 07.05.19 | 17:37 | 07.05.19 | 19.06 | 0.061806 | 1 | 29 | [5 empty] | fdr. made H/T for restoration of power at Joda grid as 220 KV incomer source failure at JODA end; 132KV PPG S/S availed P/S from Karanjia end till restoration of power at Joda end.