## CBA
COST BENEFIT ANALYSIS
A. BENEFITS DUE TO ADDITIONAL SALE OF ENERGY ON ACCOUNT OF CONSTRUCTION OF 220/33KV GSS Bhandaripokhari
1 | Transformation Capacity considered for revenue calculation | 80
2 | Power factor (PF) | 0.9
3 | Diversity factor (DF=1.3 due to industrial GSS) | 1.3
4 | Load factor (LF=0.7 due to industrial GSS) | 0.7
5 | Additional Avg. power available for sale on account of construction of 2X40 MVA, 220/33KV GIS Grid substation at Bhandaripokhari. (5 = 1 x 2 x 4 / 3) | 38.7692 | 750 | 0.9: power factor 1.3: Diversity factor
6 | Additional energy available for sale in LU | 3396.1846 |  | Due to industrial GSS 0.7 LF is considered
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 3294.2991 |  | TL of 3% is approved for FY 25-26
8 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 790.6318
B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES
1 | Total losses before implementation of the scheme in MW | 1191.6208
2 | Total losses after implementation of the scheme in MW | 1186.9017 |  | Loss reduction from Load flow study
3 | Total reduction in losses in MW | 4.7191
4 | Load factor | 0.7
5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.532
6 | The energy available for sale per year in LU | 219.9255
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 213.3278
8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/Unit | 51.1987
C. CALCULATION OF REVENUE RETURN
1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 51.1987
2 | Anticipated revenue due to sale of additional energy [Rs. Lakhs] | 790.6318
3 | Total anticipated annual revenue [Rs. Cr.] | 8.4183
4 | Estimated Cost [Rs. Cr.] | 88.5133
5 | Average Annual Rate of Return in (%) | 9.5108
6 | Internal Rate of Return (%) | 6.74%

## IRR Bhandaripokhari
Calculation of NPV and IRR : For 220/33KV GSS Bhandaripokhari and associated lines
CoC (%) = | 70% | x | 8.03 | + | 30% | x | 15.5 | Average | 6.58 |  |  | RoI on Loan P.a |  |  | = | 7.75 |  | IRR = | 6.74% | [16 empty] | (Rs. in Crores)
Particulars | Constuction Period |  |  | Benefits Period | [34 empty] | Total
Financial Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
Cash Inflow (CI)
Equity | 7.97 | 7.97 | 10.62 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26.56
Loan(Principal) | 18.59 | 18.59 | 24.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.96
Loan (Interest) | 1.49 | 2.99 | 4.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.46
Revenue | 0 | 0 | 0 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 294.6407
Salvage Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.798 | 9.798
Total (CI) - (A) | 28.05 | 29.55 | 40.38 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 8.4183 | 18.2163 | 402.4187
Cash Outflow (CO)
CWIP | 26.56 | 26.56 | 35.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.52
IDC | 1.49 | 2.99 | 4.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.46
Loan Repayment | 0 | 0 | 0 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71.42
Interest on Loan | 0 | 0 | 0 | 5.5 | 5.02 | 4.54 | 4.06 | 3.58 | 3.11 | 2.63 | 2.15 | 1.67 | 1.19 | 0.72 | 0.24 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.41
R&M exp. @ 3 % PC | 0 | 0 | 0 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 102.9
Total (CO) - (B) | 28.05 | 29.55 | 40.38 | 14.3917 | 13.9117 | 13.4317 | 12.9517 | 12.4717 | 12.0017 | 11.5217 | 11.0417 | 10.5617 | 10.0817 | 9.6117 | 9.1317 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 2.94 | 306.71 | IRR
Net Cash Inflow (A-B) | 0 | 0 | 0 | -5.9734 | -5.4934 | -5.0134 | -4.5334 | -4.0534 | -3.5834 | -3.1034 | -2.6234 | -2.1434 | -1.6634 | -1.1934 | -0.71336 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 5.4783 | 15.2763 | 95.7087 | 6.74%
DF @ CoC | 1 | 0.938 | 0.88 | 0.826 | 0.775 | 0.727 | 0.682 | 0.64 | 0.601 | 0.564 | 0.529 | 0.496 | 0.465 | 0.437 | 0.41 | 0.384 | 0.361 | 0.338 | 0.318 | 0.298 | 0.28 | 0.262 | 0.246 | 0.231 | 0.217 | 0.203 | 0.191 | 0.179 | 0.168 | 0.158 | 0.148 | 0.139 | 0.13 | 0.122 | 0.115 | 0.107 | 0.101 | 0.095
Net Present value(NPV) | 0 | 0 | 0 | -4.93 | -4.26 | -3.64 | -3.09 | -2.59 | -2.15 | -1.75 | -1.39 | -1.06 | -0.77 | -0.52 | -0.29 | 2.1 | 1.98 | 1.85 | 1.74 | 1.63 | 1.53 | 1.44 | 1.35 | 1.27 | 1.19 | 1.11 | 1.05 | 0.98 | 0.92 | 0.87 | 0.81 | 0.76 | 0.71 | 0.67 | 0.63 | 0.59 | 0.55 | 1.45 | 0.74
NPV at IRR | 0 | 0 | 0 | -4.91 | -4.23 | -3.62 | -3.06 | -2.57 | -2.12 | -1.73 | -1.37 | -1.05 | -0.76 | -0.51 | -0.29 | 2.06 | 1.93 | 1.81 | 1.69 | 1.59 | 1.48 | 1.39 | 1.3 | 1.22 | 1.14 | 1.07 | 1 | 0.94 | 0.88 | 0.83 | 0.77 | 0.72 | 0.68 | 0.64 | 0.6 | 0.56 | 0.53 | 1.37 | -0.02
**
CoC - Cost of Capital
IDC- Interest During Construction
CWIP- Capital Work in Progress
DF- Discounting Factor
IRR- Internal Rate of Return
ARR- Average Annual Rate of Return
Opening Balance |  |  |  | 71.42 | 65.4683 | 59.5167 | 53.565 | 47.6133 | 41.6617 | 35.71 | 29.7583 | 23.8067 | 17.855 | 11.9033 | 5.9517
Repayment |  |  |  | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517 | 5.9517
Closing Balance |  |  |  | 65.4683 | 59.5167 | 53.565 | 47.6133 | 41.6617 | 35.71 | 29.7583 | 23.8067 | 17.855 | 11.9033 | 5.9517 | -1.2434e-14
Agerage Loan |  |  |  | 68.4442 | 62.4925 | 56.5408 | 50.5892 | 44.6375 | 38.6858 | 32.7342 | 26.7825 | 20.8308 | 14.8792 | 8.9275 | 2.9758
Interest |  |  |  | 5.4961 | 5.0181 | 4.5402 | 4.0623 | 3.5844 | 3.1065 | 2.6286 | 2.1506 | 1.6727 | 1.1948 | 0.71688 | 0.23896
|  |  |  | -0.0039334 | -0.0018522 | 0.00022892 | 0.0023101 | 0.0043912 | -0.0035276 | -0.0014464 | 0.00063475 | 0.0027159 | 0.0047971 | -0.0031218 | -0.0010406

## Data sheet
| Expenditure in Cr.: | 88.5133
| Year: | 2025-26 | 2026-27 | 2027-28
| % of Expenditure: | 30% | 30% | 40%
| Year wise expenditure: | 26.554 | 26.554 | 35.4053
Loan | 70% | 18.59 | 18.59 | 24.78
Equity | 30% | 7.97 | 7.97 | 10.62
Total | 100% | 26.56 | 26.56 | 35.4