## VIIA SS PALASPANGA SUPPLY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
SUPPLY OF EQUIPMENT / MATERIALS,
PART -A, SCHEDULE-VIIA-SUPPLY (FOR 132 KV SUB-STATION WORK)
SLNO | DESCRIPTION OF ITEMS SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT | Qty | Unit Price IN INR | OGST@9% | CGST@9% | Total Unit Price with GST | Total Amount | PRICE REF: COST DATA/ OPTCL'S LATEST PO PRICE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4x8 | 10
ELECTRICAL EQUIPMENTS
1 | 145 KV,(800-400-200 Ratio),40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 6 | 232701.42 | 20943.1278 | 20943.1278 | 274587.6756 | 1647526.0536 | CD 24-25-SS-24
2 | S/I WITH OUT EARTH SWITCH | NOS | 2 | 231941.65 | 20874.7485 | 20874.7485 | 273691.147 | 547382.294 | CD 24-25-SS-11
3 | D/I WITH SINGLE EARTH SWITCH | NOS | 2 | 534828.58 | 48134.5722 | 48134.5722 | 631097.7244 | 1262195.4488 | CD 24-25-SS-12
4 | Beam Mounted Isolator W/O E/S (S/I) | NOS | 1 | 267414.29 | 24067.2861 | 24067.2861 | 315548.8622 | 315548.8622 | CD 24-25-SS-55
5 | 145 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 163753.99 | 14737.8591 | 14737.8591 | 193229.7082 | 1159378.2492 | CD 24-25-SS-35
6 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS | 6 | 29179.14 | 2626.1226 | 2626.1226 | 34431.3852 | 206588.3112 | CD 24-25-SS-31
7 | 132 KV Bus Post Insulators | NOS | 20 | 17491.3202 | 1574.2188 | 1574.2188 | 20639.7578 | 412795.1557 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
8 | 145KV, 3150A, 40KA, SF6 CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | SET | 2 | 571890.4 | 51470.136 | 51470.136 | 674830.672 | 1349661.344 | CD 24-25-SS-03
9 | BUS BAR AND CIRCUIT MATERIALS
9.1.1 | 120 KN Antifog Porcelain Disc Insulator | NOS | 504 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 428222.1888 | CD 24-254-TL-54
9.1.2 | 90 KN Antifog Porcelain Disc insulator | NOS | 170.1 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 134186.0045 | CD 24-25-TL ACCE.-53
10 | ACSR MOOSE CONDUCTOR | KM | 1 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 527374.6742 | CD24-25-TL -19
10.1 | Single Tension H/W fitting suitable for single ACSR Moose (1 x 120kN) | NOS | 24 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 79958.1216 | CD24-25-TL ACCE.-9
10.2 | Double Tension H/W fitting suitable for twin ACSR Moose (2 x 120kN) | NOS | 12 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 71606.1288 | CD24-25-TL ACCE.-10
10.3 | Single suspension H/W fitting suitable for single ACSR Moose (1 x 90kN) | NOS | 12 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 49069.0728 | CD24-25-TL ACCE.-07
10.4 | Single suspension H/W fitting suitable for twin ACSR Moose (1 x 90kN) | NOS | 6 | 5275.69 | 474.8121 | 474.8121 | 6225.3142 | 37351.8852 | CD24-25-TL ACCE.-08
10.5 | 132 KV Switchyard Clamp & Connectors (compression type) | Lot | 2 | 200000 | 18000 | 18000 | 236000 | 472000 | Tentative
11 | EARTHING MATERIALS
11.1 | EARTHING CONDUCTOR FOR BURRIAL : 75x10 mm GI Earth Flat for laying (Spacing maximum 5m both ways) | MT | 10 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1102732.302 | CD 24-25-Line-4
11.2 | EARTHING CONDUCTOR : 50 X 6 mm GI Earth Flat for raiser from the burrial earthmat to equipment, structure etc. | MT | 6 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 661639.3812
11.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) (3 CTU+3 LA+ 3CVT+1 CT+1 SI+1 CB+ 1DI+3 COLUMN) | NOS | 32 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 86129.8048 | CD 24-25-TL-8
11.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 20 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 53831.128 | CD 24-25-TL-8
11.5 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:2-2,3-3 & 4-4 along with its accessories as per TS. | Lot | 2 | 349826.4958 | 31484.3846 | 31484.3846 | 412795.265 | 825590.53 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
12 | SUB STATION SWITCYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES
12.1 | BAY MARSHALLING KIOSK | NOS | 2 | 174062.8566 | 15665.6571 | 15665.6571 | 205394.1707 | 410788.3415 | CD 24-25-SS-76
12.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
12.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659
12.4 | Consol box for CTs(1nos) & IVTs(1nos) | NOS | 4 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 144478.3318
13 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132KV CLASS DIFFERENT TYPES OF COLUMNS WITH DETAILS
13.1 | T1S - 132 KV(NOMINAL UNIT WT- 1.092 MT) | NOS | 4 |  | 0 | 0 | 0 | 0
13.2 | T4S - 132KV (NOMINAL UNIT WT- 0.849 MT) | NOS | 2 |  | 0 | 0 | 0 | 0
13.3 | DIFFERENT TYPE OF BEAMS WITH DETAILS |  |  |  | 0 | 0 | 0 | 0
13.4 | G1 - 132 KV(NOMINAL UNIT WT- 0.576 MT) | NOS | 4 |  | 0 | 0 | 0 | 0
13.5 | G1X - 132 KV (NOMINAL UNIT WT- 0.641 MT) | NOS | 0 |  | 0 | 0 | 0 | 0
13.6 | G2 - 132 KV(NOMINAL UNIT WT- 0.851 MT) | NOS | 4 |  | 0 | 0 | 0 | 0
13.7 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132KV CLASS (column & Beam) | MT | 11.774 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1298357.0124 | CD 24-25-Line-4
13.8 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 1.1774 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 164720.1189 | CD 24-25-Line-5
14 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 132KV EQUIPMENTS
14.1 | SINGLE ISOLATORS with out ES-132KV ( 0.621 MT) | SET | 2 |  | 0 | 0 | 0 | 0
14.2 | Double isolator with ES- 132 KV (1.105MT) | SET | 2 |  | 0 | 0 | 0 | 0
14.3 | CTS-132 KV (0.207 MT)) | SET | 6 |  | 0 | 0 | 0 | 0
14.4 | IVTS-132 KV (0.206MT) | SET | 6 |  | 0 | 0 | 0 | 0
14.5 | Surge Arrester-132 kV (0.172MT) | SET | 6 |  | 0 | 0 | 0 | 0
14.6 | BPI-132 KV (0.296MT) | SET | 20 |  | 0 | 0 | 0 | 0
14.7 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 132KV EQUIPMENTS | MT | 12.882 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1420539.7514 | CD 24-25-Line-4
14.8 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 1.2882 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 180221.2138 | CD 24-25-Line-5
15 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
15.1 | PVC 3.5 CX70 mm2 | KM | 1.2 | 265690.44 | 23912.1396 | 23912.1396 | 313514.7192 | 376217.663 | CD 24-25-SS-129
15.2 | PVC 3.5 CX35 mm2 | KM | 1.2 | 147505.32 | 13275.4788 | 13275.4788 | 174056.2776 | 208867.5331 | CD 24-25-SS-127
15.3 | PVC 4 CX 16 mm2 | KM | 0.8 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 109301.4459 | CD 24-25-SS-125
15.4 | PVC 4 CX 6 mm2 | MTRS | 600 | 131.1821 | 11.8064 | 11.8064 | 154.7948 | 92876.902 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23)
15.5 | PVC 4CX 4 mm2 | MTRS | 900 | 104.9503 | 9.4455 | 9.4455 | 123.8413 | 111457.2
16 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
16.1 | 2 CX 2.5 mm2 | KM | 2.4 | 78413.59 | 7057.2231 | 7057.2231 | 92528.0362 | 222067.2869 | CD 24-25-SS-107
16.2 | 4 CX 2.5 mm2 | KM | 5 | 123673.44 | 11130.6096 | 11130.6096 | 145934.6592 | 729673.296 | CD 24-25-SS-109
16.3 | 7CX 2.5 mm2 | KM | 4 | 187201.82 | 16848.1638 | 16848.1638 | 220898.1476 | 883592.5904 | CD 24-25-SS-110
16.4 | 10 CX 2.5 mm2 | KM | 3 | 254413.65 | 22897.2285 | 22897.2285 | 300208.107 | 900624.321 | CD 24-25-SS-111
16.5 | 12 CX 2.5 mm2 | KM | 3 | 393557.7713 | 35420.1994 | 35420.1994 | 464398.1701 | 1393194.5102 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23)
16.6 | 16 CX 2.5 mm2 | KM | 3 | 387033.75 | 34833.0375 | 34833.0375 | 456699.825 | 1370099.475 | CD 24-25-SS-112
16.7 | 19 CX 2.5 mm2 | KM | 4 | 448832.3 | 40394.907 | 40394.907 | 529622.114 | 2118488.456 | CD 24-25-SS-113
17 | 132 KV CONTROL RELAY PANEL
17.1 | 132 KV FEEDER PROTECTION PANEL: 1 feeder in one panel Numerical Distance Protection relay, BAckup relay, BCU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power supply 220V DC.TNC for CB and PBs for Isolators shall be provided additionally. | Nos | 2 | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 2877294.7484 | CD 24-25-SS-42
18 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).(150 watt each) | No. | 30 | 17085.7578 | 1537.7182 | 1537.7182 | 20161.1942 | 604835.8267 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
19 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS).
19.1 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | Nos. | 20 | 11105.3513 | 999.4816 | 999.4816 | 13104.3145 | 262086.2907 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
19.2 | GI Tubular Pole:(410-sp-24:IS 2713-part-II-1980 or latest) length of poles 8.5 mtrs (Minimun weight 158 Kgs) (all the street light pole shall be of GI tubular pole & provision of a GI junction box with suitable covers at a height of 1 mtr from the ground. The junction box shall have provision of fuses, buses, connectors for cable IN & OUT) | Nos. | 20 | 21356.2133 | 1922.0592 | 1922.0592 | 25200.3317 | 504006.6336
19.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB, XLPE cables (305 C*120sqmm) from main ACDB CR to the out door KIOSK. XLPE cable of 4CX16sqmm from outdoor KIOSK to the street light poles & 4CX6sqmm from pole to pole & 2CX6sqmm from pole to lighting fixtures | Nos. | 1 | 74748.2398 | 6727.3416 | 6727.3416 | 88202.923 | 88202.923
20 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | NOS | 6 | 64080.054 | 5767.2049 | 5767.2049 | 75614.4638 | 453686.7826
21 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC
21.1 | SODA ACID TYPE-9 LTRS | LOT | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | Tentative
21.2 | FOAM TYPE-9 LTRS
21.3 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS
21.4 | DRY POWDER TYPE - 5 KGS
21.5 | CO2 - 4.5 KGS
21.6 | CO2 - 9 KGS
21.7 | CO2 (TROLLY MOUNTED)- 22.5 KGS
21.8 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND
22 | BEST QUALITY &APPROVED MAKE INSULATING MAT for suitable voltage (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos | 20 | 4555.9374 | 410.0344 | 410.0344 | 5376.0061 | 107520.122 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
23 | Mereting Panel | Nos | 1 | 85000 | 7650 | 7650 | 100300 | 100300 | Tentative
24 | Meter(Main & Check) | Nos | 4 | 106000 | 9540 | 9540 | 125080 | 500320
25 | SUBSTATION AUTOMATION SYSTEM: Supply of the following 132KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of Industrial computer with accessories, PC with accessories, laser printer, UPS, GPS system & numerical Bay Control unit etc.
25.1 | 132KV Level
25.1.1 | Yard AC Kiosk: 4500mm (L)X4000mm(W)X3500mm(H) with AC,as per specification | Nos. | 1 | 1167498.1678 | 105074.8351 | 105074.8351 | 1377647.838 | 1377647.838 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
25.1.2 | BCU for 132KV side: Numerical Bay Control unit:32 Digital Input & 28Nos. Digital output with 4 CT Input,4 VT inputs, IEC 61850 protocol with PRP,power supply 220V DC | Nos. | 1 | 207326.82 | 18659.4138 | 18659.4138 | 244645.6476 | 244645.6476 | CD 24-25-SAS-14
25.1.3 | Numerical Distance protection with PRP,IEC 61850 protocol.Digital input & output to be provided as per the scheme. | Nos. | 2 | 165861.46 | 14927.5314 | 14927.5314 | 195716.5228 | 391433.0456 | CD 24-25-SAS-15
25.1.4 | Numerical O/C & E/F relays: IEC 61850protocol with PRP Digital input & outpot to be provided as per the scheme | Nos. | 2 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 251635.5192 | CD 24-25-SAS-17
25.1.5 | High impedance REF relay. Digital input & output to be provided as per scheme | Nos. | 2 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 251635.5192 | CD 24-25-SAS-18
25.1.6 | Auxiliary Relay for DC supervision | Nos. | 8 | 5331.28 | 479.8152 | 479.8152 | 6290.9104 | 50327.2832 | CD 24-25-SAS-19
25.1.7 | MPG-TEST BLOCK | Nos. | 16 | 2402.62 | 216.2358 | 216.2358 | 2835.0916 | 45361.4656 | CD 24-25-SAS-21
25.1.8 | High speed Trip relay (Electrical Reset) 86A,86B,96 | Nos. | 8 | 7700.71 | 693.0639 | 693.0639 | 9086.8378 | 72694.7024 | CD 24-25-SAS-22
26 | Supply & installation of Office Furniture: Godrej make (As per details below). | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | tentative
26.1 | For Control Room, conference room, office rooms, Library, testing room etc
26.1.1 | 5ftX3ft executive table with drawer on both sides | Nos | 4
26.1.2 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7
26.1.3 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 1
26.1.4 | Executive revolving, adjustable (height) chairs with arm | Nos | 4
26.1.5 | Cushion fixed “S” type steel chairs with arm | Nos | 16
26.1.6 | 6ftX3ft conference table | Nos | 1
26.1.7 | Cushion arm steel chairs for conference table purpose. | Nos | 6
26.1.8 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3
26.1.9 | 6ft height steel almirah with glass doors for library purpose | Nos | 2
26.1.10 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2
26.1.11 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8
26.2 | For Communication Room
26.2.1 | 5ftX3ft executive table with drawer both sides | Nos | 1
26.2.2 | Executive revolving, adjustable (height) chairs with arm | Nos | 1
26.2.3 | Cushion fixed “S” type steel chairs with arm | Nos | 2
26.2.4 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1
27 | ACCESSORIES FOR PLCC SYSTEM
27.1 | FODP (48 Fibre), Indoor type, rack mounted with FCPC coupling and pig tails (5 mtrs each) | NO. | 1 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 64023.201 | CD24-25-TEL-29
27.2 | Optical Line Terminal Equipment (OLTE)- STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of speech & data which should be compatible with existing OPTCL system. | NO. | 1 | 1910690 | 171962.1 | 171962.1 | 2254614.2 | 2254614.2 | LoA No.221,Dt.01.02.25 (Neulpoi)
27.3 | 48 Fibre Optic approach cable (DWSM) | Km | 1 | 127089.72 | 11438.0748 | 11438.0748 | 149965.8696 | 149965.8696 | CD24-25-TEL-33
27.4 | Installation hardware set (HDPE duct, HDPE coupling, etc) for 48 Fibre FOAC | Km | 1 | 93762.74 | 8438.6466 | 8438.6466 | 110640.0332 | 110640.0332 | CD24-25-TEL-34
27.5 | 48 V,300 AH,maintenance free VRLA Battery set | Set | 1 | 119332.12 | 10739.8908 | 10739.8908 | 140811.9016 | 140811.9016 | CD24-25-TEL-02
27.6 | SMPS based Battery Charger of 48V/75A suitable for 48V VRLA Battery | NO. | 1 | 110881.51 | 9979.3359 | 9979.3359 | 130840.1818 | 130840.1818 | CD24-25-TEL-18
27.7 | 2.5sqmm 3 core control cable for AC supply | MTRS | 200 | 61.71 | 5.5539 | 5.5539 | 72.8178 | 14563.56 | CD24-25-TEL-61
27.8 | 2.5sqmm 2 core control cable for DC supply | MTRS | 200 | 44.08 | 3.9672 | 3.9672 | 52.0144 | 10402.88 | CD24-25-TEL-62
27.9 | Earth flat, Cable tray, telephone Cable,ACDB,DCDB,Foundation rail,Junction Box. | LS | 1 | 174913.2479 | 15742.1923 | 15742.1923 | 206397.6325 | 206397.6325 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23)
TOTAL: PART -A, SCHEDULE-VIIA-SUPPLY (FOR 132 KV SUB-STATION WORK) | [7 empty] | 36746704.5294
| Estimator |  |  | Deputy General Manager (Elect.),
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## Supply (hidden)
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 132KV S/C line from existing 132/33KV Grid Sub-Station, Barbil to proposed MRSS of TATA STEEL LTD at Kalmang and 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil.
SUPPLY OF EQUIPMENT / MATERIALS,
SUPPLY PART
SLNO | DESCRIPTION OF ITEMS SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT | Quantity for Construction of 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil. | Unit Price IN INR | Escalation (UNIT PO PRICE/ COST DATA RATE + 5% ESCALATION PER YEAR) (Including F & I ) | Total Price IN INR | PRICE REF: COST DATA/ OPTCL'S LATEST PO PRICE
1 | 2 | 3 | 4 | 5 | 6 | 7=4x6
ELECTRICAL EQUIPMENTS
1 | 145 KV,(800-400-200 Ratio),40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 3 | 113534.48 | 119211.204 | 357633.612 | CD 23-24-SS-22
2 | S/I WITH OUT EARTH SWITCH | NOS | 1 | 219068.84 | 230022.282 | 230022.282 | CD 23-24-SS-09
3 | D/I WITH SINGLE EARTH SWITCH | NOS | 1 | 531843.89 | 558436.0845 | 558436.0845 | CD 23-24-SS-11
4 | Beam Mounted Isolator W/O E/S (S/I) | NOS | 2 | 205238.43 | 215500.3515 | 431000.703 | CD 23-24-SS-13
5 | 145 KV, 4400pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS | 3 | 119967.8 | 125966.19 | 377898.57 | CD 23-24-SS-32
6 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS | 3 | 28807.29 | 30247.6545 | 90742.9635 | CD 23-24-SS-28
7 | 132 KV Bus Post Insulators | NOS | 2 | 15109.66 | 16658.4002 | 33316.8003 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
8 | 145KV, 3150A, 40KA, SF6 CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | SET | 1 | 564602.44 | 592832.562 | 592832.562 | CD 23-24-SS-03
| BUS BAR AND CIRCUIT MATERIALS |  |  |  |  | 0
9 | 120 KN Antifog Disc Insulator for Twin Moose (Main Bus) & Single Moose(Transfer Bus) Conductor (Tension) for 132 KV side (20*6+10*6+10*6=240*1.05=252) | NOS | 252 | 710.86 | 746.403 | 188093.556 | CD 23-24-TL-52
10 | 90 KN Antifog Disc insulator for single conductor (suspension) for 132 KV side | NOS | 113.4 | 660.01 | 693.0105 | 78587.3907 | CD 23-24-TL ACCE.-51
11 | ACSR MOOSE CONDUCTOR | KM | 0.6 | 409923 | 430419.15 | 258251.49 | CD23-24-TL ACCE.-18
12 | 132 KV Single Tension H/W fitting suitable for single ACSR Moose | NOS | 12 | 2787.4 | 2926.77 | 35121.24 | CD23-24-TL ACCE.-9
13 | 132 KV Double Tension H/W fitting suitable for twin ACSR Moose | NOS | 6 | 4992.49 | 5242.1145 | 31452.687 | CD23-24-TL ACCE.-10
14 | 132 KV Single suspension H/W fitting suitable for single ACSR Moose | NOS | 6 | 3421.17 | 3592.2285 | 21553.371 | CD23-24-TL ACCE.-07
15 | 132 KV Single suspension H/W fitting suitable for twin ACSR Moose | NOS | 3 | 5208.46 | 5468.883 | 16406.649 | CD23-24-TL ACCE.-08
16 | 132 KV SIDE CLAMP & CONNECTOR | Lot | 1 | 200000 | 200000 | 200000 | Tentative
| EARTH SPIKE & IT'S HARDWARES & FITTING |  |  |  |  | 0
17 | Earthing Spikes of 7 mtr long each and Its Fittings in all respect. (132 KV Side) | NOS | 3 | 6149.15 | 6779.4379 | 20338.3136 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
| EARTHING MATERIALS |  |  |  |  | 0
18 | EARTHING CONDUCTOR FOR BURRIAL : 75x10 mm GI Earth Flat for laying (Spacing maximum 5m both ways) | MT | 3 | 90657.98 | 99950.4229 | 299851.2688 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
19 | EARTHING CONDUCTOR : 50 X 6 mm GI Earth Flat for raiser from the burrial earthmat to equipment, structure etc. | MT | 2 | 90657.98 | 99950.4229 | 199900.8459
20 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 18 | 2251.91 | 2364.5055 | 42561.099 | CD 23-24-TL-8
21 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 10 | 2251.91 | 2364.5055 | 23645.055 | CD 23-24-TL-8
22 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:2-2,3-3 & 4-4 along with its accessories as per TS. | Lot | 1 | 302193.28 | 333168.0912 | 333168.0912 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
| SUB STATION SWITCYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES |  |  |  |  | 0
23 | BAY MARSHALLING KIOSK | NOS | 1 | 148445.88 | 155868.174 | 155868.174 | CD 23-24-SS-81
24 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 1 | 26441.91 | 29152.2058 | 29152.2058 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
25 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 1 | 26441.91 | 29152.2058 | 29152.2058
26 | Consol box for CTs(1nos) & CVTs(1nos) | NOS | 2 | 26441.91 | 29152.2058 | 58304.4116
| SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132KV CLASS |  |  |  |  | 0
| DIFFERENT TYPES OF COLUMNS WITH DETAILS |  |  |  |  | 0
13.3 | T1S - 132 KV(NOMINAL UNIT WT- 1.092 MT) | NOS | 2
14 | T4S - 132KV (NOMINAL UNIT WT- 0.849 MT) | NOS | 1
14.1 | DIFFERENT TYPE OF BEAMS WITH DETAILS
14.2 | G1 - 132 KV(NOMINAL UNIT WT- 0.576 MT) | NOS | 2
14.3 | G1X - 132 KV (NOMINAL UNIT WT- 0.641 MT) | NOS | 0
14.4 | G2 - 132 KV(NOMINAL UNIT WT- 0.851 MT) | NOS | 2
27 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132KV CLASS (column & Beam) | MT | 5.887 | 91000 | 100327.5 | 590627.9925 | CPC Order on Tower Str.-170(2)/28.2.23
28 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 0.5887 | 115450 | 127283.625 | 74931.87
SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 132KV EQUIPMENTS ALONG WITH 33 KV EQUIPMENT
15.2 | SINGLE ISOLATORS with out ES-132KV ( 0.621 MT) | SET | 1
15.3 | Double isolator with ES- 132 KV (1.105MT) | SET | 1
15.4 | Double isolator with out ES 132 KV | SET | 0
15.5 | CTS-132 KV (0.207 MT)) | SET | 3
15.6 | CVTS-132 KV (0.206 MT) | SET | 3
15.7 | IVTS-132 KV (0.206MT) | SET | 0
15.8 | Surge Arrester-132 kV (0.172MT) | SET | 3
15.9 | BPI-132 KV (0.296MT) | SET | 2
15.1 | SF6 Circuit Breaker | SET | 0
15.11 | Wave Trap | SET | 0
15.12 | Strutcure for Cable termination (0.296MT) | SET | 0
29 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 132KV EQUIPMENTS ALONG WITH 33 KV EQUIPMENT | MT | 4.073 | 91000 | 100327.5 | 408633.9075 | CPC Order on Tower Str.-170(2)/28.2.23
30 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 0.4073 | 115450 | 127283.625 | 51842.6205
GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
132 KV CONTROL RELAY PANEL
31 | 132 KV FEEDER PROTECTION PANEL: Feeder 1 & 2 in one Panel. Numerical Distance Protection relay, BCPU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power supply 220V DC. | Nos | 1 | 2400000 | 2520000 | 2520000 | CD 23-24-SS-39
32 | Other requirement materials like ethernat switch, FO patch cord,cable, LIU etc. complete in all respect to integrate this bay to the existing system of SAS. | Lot | 1 | 226644.96 | 249876.0684 | 249876.0684 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
33 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).(150 watt each) | No. | 20 | 14759.32 | 16272.1503 | 325443.006 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
21 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS).
21.1 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | Nos. | 20 | 9593.22 | 10576.5251 | 211530.501 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
21.2 | GI Tubular Pole:(410-sp-24:IS 2713-part-II-1980 or latest) length of poles 8.5 mtrs (Minimun weight 158 Kgs) (all the street light pole shall be of GI tubular pole & provision of a GI junction box with suitable covers at a height of 1 mtr from the ground. The junction box shall have provision of fuses, buses, connectors for cable IN & OUT) | Nos. | 20 | 18448.3 | 20339.2507 | 406785.015
21.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB, XLPE cables (305 C*120sqmm) from main ACDB CR to the out door KIOSK. XLPE cable of 4CX16sqmm from outdoor KIOSK to the street light poles & 4CX6sqmm from pole to pole & 2CX6sqmm from pole to lighting fixtures | Nos. | 1 | 64570.34 | 71188.7998 | 71188.7998
22 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | NOS | 10 | 55354.76 | 61028.6229 | 610286.229
| FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC |  |  |  |  | 0
| SODA ACID TYPE-9 LTRS | LOT | 1 | 500000 | 500000 | 500000 | Tentative
FOAM TYPE-9 LTRS
DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS
DRY POWDER TYPE - 5 KGS
CO2 - 4.5 KGS
CO2 - 9 KGS
CO2 (TROLLY MOUNTED)- 22.5 KGS
FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND
| BEST QUALITY &APPROVED MAKE INSULATING MAT for suitable voltage (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos | 10 | 3935.59 | 4338.988 | 43389.8798 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
| Panel for secure meter | Nos | 1 | 85000 | 85000 | 85000 | Tentative
| Meter(Main & Check) | Nos | 2 | 106000 | 106000 | 212000
| POWER CABLES, 1.1KV, XLPE/ PVC, ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  |  | 0
| PVC 3.5 CX70 mm2 | KM | 0.45 | 262304.58 | 275419.809 | 123938.9141 | CD 23-24-SS-133
| PVC 3.5 CX35 mm2 | KM | 0.45 | 145625.56 | 152906.838 | 68808.0771 | CD 23-24-SS-131
| PVC 4 CX 16 mm2 | KM | 0.3 | 114309.9 | 120025.395 | 36007.6185 | CD 23-24-SS-129
| PVC 4 CX 6 mm2 | MTRS | 300 | 113.32 | 124.9353 | 37480.59 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
| PVC 4CX 4 mm2 | MTRS | 450 | 90.66 | 99.9527 | 44978.6925
| CONTROL CABLES, 1.1 KV, PVC, STRANDED COPPER(As per specification) |  |  |  |  | 0
1 | 2 CX 2.5 mm2 | KM | 0.8 | 77414.31 | 81285.0255 | 65028.0204 | CD 23-24-SS-112
2 | 4 CX 2.5 mm2 | KM | 4 | 122097.4 | 128202.27 | 512809.08 | CD 23-24-SS-114
3 | 7CX 2.5 mm2 | KM | 2.5 | 184816.18 | 194056.989 | 485142.4725 | CD 23-24-SS-115
4 | 10 CX 2.5 mm2 | KM | 1 | 251171.49 | 389649.4195 | 389649.4195 | CD 23-24-SS-116
5 | 12 CX 2.5 mm2 | KM | 1 | 339970 | 374816.925 | 374816.925 | TURUMUNGA-DHENKIKOTE LOA (1377/16.02.23)
6 | 16 CX 2.5 mm2 | KM | 1 | 382101.53 | 401206.6065 | 401206.6065 | CD 23-24-SS-117
7 | 19 CX 2.5 mm2 | KM | 2 | 443112.55 | 465268.1775 | 930536.355 | CD 23-24-SS-118
23 | SUBSTATION AUTOMATION SYSTEM: Supply of the following 132KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of Industrial computer with accessories, PC with accessories, laser printer, UPS, GPS system & numerical Bay Control unit etc.
23.1 | 132KV Level
23.1.1 | Yard AC Kiosk: 4500mm (L)X4000mm(W)X3500mm(H) with AC,as per specification | Nos. | 1 | 1039277.12 | 1145803.0248 | 1145803.0248 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
23.1.2 | BCU for 132KV side: Numerical Bay Control unit:32 Digital Input & 28Nos. Digital output with 4 CT Input,4 VT inputs,8 insulated transducer input(-20mA to +20mA) values on 8 independent galvanic isolated channels for TRF bay application, IEC 61850 protocol with PRP,power supply 220V DC | Nos. | 1 | 228077 | 239480.85 | 239480.85 | CD 23-24-TEL-13
23.1.3 | BCU for 132KV side: Numerical Bay Control unit:32 Digital Input & 28Nos. Digital output with 4 CT Input,4 VT inputs, IEC 61850 protocol with PRP,power supply 220V DC | Nos. | 1 | 204685 | 214919.25 | 214919.25 | CD 23-24-TEL-14
23.1.4 | Numerical Distance protection with PRP,IEC 61850 protocol.Digital input & output to be provided as per the scheme. | Nos. | 1 | 163748 | 171935.4 | 171935.4 | CD 23-24-TEL-15
23.1.5 | Numerical Transformer Differential/ REF protection with the following functionc: over flux, Over Volt etc. IEC 61850 protocol with PRP. Digital input & output to be provided as per the scheme. | Nos. | 1 | 210533 | 221059.65 | 221059.65 | CD 23-24-TEL-16
23.1.6 | Numerical O/C & E/F relays: IEC 61850protocol with PRP Digital input & outpot to be provided as per the scheme | Nos. | 1 | 105266 | 110529.3 | 110529.3 | CD 23-24-TEL-17
23.1.7 | High impedance REF relay. Digital input & output to be provided as per scheme | Nos. | 1 | 105266 | 110529.3 | 110529.3 | CD 23-24-TEL-18
23.1.8 | Auxiliary Relay for DC supervision | Nos. | 4 | 5263 | 5526.15 | 22104.6 | CD 23-24-TEL-19
23.1.9 | Auxiliary Relay for Transformer with three element each | Nos. | 1 | 7603 | 7983.15 | 7983.15 | CD 23-24-TEL-20
23.1.10 | MPG-TEST BLOCK | Nos. | 8 | 2372 | 2490.6 | 19924.8 | CD 23-24-TEL-21
23.1.11 | High speed Trip relay (Electrical Reset) 86A,86B,96 | Nos. | 4 | 7603 | 7983.15 | 31932.6 | CD 23-24-TEL-22
23.1.12 | Line interface unit | Set | 2 | 3743 | 3930.15 | 7860.3 | CD 23-24-TEL-23
23.1.13 | Ethernet switch IEEE802.3,IEEE1588,IEC 61850-3, PRP protocol,20% spare to be provided | Lot | 1 | 467851 | 491243.55 | 491243.55 | CD 23-24-TEL-24
23.1.14 | Simplex cubicle type for BCU & protection equipment, swing frame front access (VSG), Dimension 2300mm(H) X 1000mm (D) X 1000mm (W). Earth bar 25X6 sqmm, Copper & panel illumination. Complete wiring of protection & control components,all relay & equipment fitted . One panel for control & protection of two bays, with provision of TCS relay, DC changeover relay & suitable voltage slection relay. | Set | 1 | 116963 | 122811.15 | 122811.15 | CD 23-24-TEL-25
23.1.15 | DCDB panel : with Bus Bar switches,with dual source facility of Double Bus system for independent DC supply to each Bay, should have the facility of VTD & CTD for voltage & current montoring. Each MCB/MCCBs should also be given wth Aux contacts. | No. | 2 | 49124 | 51580.2 | 103160.4 | CD 23-24-TEL-35
23.1.16 | Windows based Industrial computer with standard accessories- Keyboard, mouse, monitor & dot Matrix printer with operating software window 10 or 8 or 7, IED configuration, Substation automation, Main & Back up, with automation software & license key. | Set | 1 | 134507 | 141232.35 | 141232.35 | CD 23-24-TEL-36
23.1.17 | Windows based PC with standard accessories- Keyboard, mouse, monitor with operating software window 10 or 8 or 7, IED configuaration, Substation automation, disturbance recorder software, DR & work station PC & license key. | Set | 1 | 134507 | 141232.35 | 141232.35 | CD 23-24-TEL-37
23.1.18 | Redundant Box: IEC 61850-3,IEEE 1613 (Power substations) compliant,IEC 62439-3,clause 4 (PRP) & clause 5 (HSR) compliant | No. | 1 | 88482 | 92906.1 | 92906.1 | CD 23-24-TEL-38
23.1.19 | Video display unit, LED,139cm,1920X1080 | No. | 1 | 111115 | 116670.75 | 116670.75 | CD 23-24-TEL-39
23.1.20 | Colour laser printer | No. | 1 | 59651 | 62633.55 | 62633.55 | CD 23-24-TEL-40
23.1.21 | Inverter,3KVA | No. | 1 | 181292 | 190356.6 | 190356.6 | CD 23-24-TEL-41
23.1.22 | GPS system with IRIG-B/SNTP/PTP with clock Distance Visual unit | Set | 1 | 122811 | 128951.55 | 128951.55 | CD 23-24-TEL-42
23.1.23 | Substation Gateway for communication with SLDC /Network control centre over IEC60870-5-104 with redudant facility | Set | 1 | 122811 | 128951.55 | 128951.55 | CD 23-24-TEL-44
23.1.24 | Operator desk (computer table large type) | No. | 1 | 17544 | 18421.2 | 18421.2 | CD 23-24-TEL-48
23.1.25 | Operator Chair | No. | 6 | 5263 | 5526.15 | 33156.9 | CD 23-24-TEL-49
23.1.26 | Rack for placing Inverter & UPS | No. | 1 | 2924 | 3070.2 | 3070.2 | CD 23-24-TEL-50
| ACDB PANEL: With Bus Bar Switches,(33KV, 132KV & 220KV KIOSKs) with provision of indicative Meters and LEDs and main MCCB of 63Amp and output of 05Nos. Of 32Amp MCB for 2Nos. Of AC unit, 01No. For testing facility & 02Nos. Spare, 15Nos. Of DP MCB of 16Amp each, should have the facility of VTD & CTD for Voltage and Current monitoring. Each MCB/MCCBs should also be given with aux contact. | No. | 1 | 49124 | 51580.2 | 51580.2 | CD 23-24-TEL-34
| DCDB PANEL: With Bus Bar Switches,(33KV, 132KV & 220KV KIOSKs) with dual Source facility of Double BUS system for independent DC supply to each Bay. Should have the facility of VTD & CTD for Voltage and Current monitoring. Each MCB/MCCBs should also be given with aux contacts. | No. | 1 | 49124 | 51580.2 | 51580.2 | CD 23-24-TEL-35
24 | AC & DC SYSTEM
24.1 | AC SYSTEM
24.1.1 | ACDB (HAVING 800A MCCB) AS PER SPECIFICATION (AC DB-1.AC DB-2 WITH B/C) | SET | 1 | 371115.33 | 389671.0965 | 389671.0965 | CD 23-24-SS-83
24.1.2 | MAIN LIGHTING DISTRIBUTION BOARD (HAVING 250A MCCB AS INCOMER)AS PER SPECIFICATION (WITH DB-1.DB-2 & B/C) | SET | 1 | 150000 | 201014.3461 | 201014.3461 | LOA NO.118/22.02.19 GODISAHI GIS
24.1.3 | INDOOR LIGHTING DISTRIBUTION BOARD AS PER SPECIFICATION (WITH DB-I.DB-2& B/C) | SET | 1 | 19000 | 25461.8172 | 25461.8172
24.1.4 | EMERGENCY LIGHTING DISTRIBUTION BOARD | SET | 1 | 16500 | 22111.5781 | 22111.5781
24.1.5 | INDOOR RECEPTACLE BOARD | SET | 1 | 6000 | 8040.5738 | 8040.5738
24.2 | DC SYSTEM
24.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). Consider separate source(DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered.Facilities for integration with SAS as per the site requirement. | SET | 1 | 371115.33 | 389671.0965 | 389671.0965 | CD 23-24-SS-84
24.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 1 | 12000 | 16081.1477 | 16081.1477 | LOA NO.118/22.02.19 GODISAHI GIS
25 | 350 AH PLANTE TYPE 220 V BATTERY SET | SET | 1 | 2025000 | 2126250 | 2126250 | CD 23-24-SS-74
26 | 220V BATTERY CHARGER 35/60A FOR 350AH PLANTE BATTERY WITH MANDATORY SPARE | SET | 1 | 395293.68 | 415058.364 | 415058.364 | CD 23-24-SS-77
27 | DE MINERALISED PLANT of 30 L/Hr FOR MAKING DISTLED WATER FOR BATTERY BANKS. | SET | 1 | 60000 | 80405.7384 | 80405.7384 | LOA NO.118/22.02.19 GODISAHI GIS
28 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO 19) | NOS | 2 | 32000 | 42883.0605 | 85766.121
29 | CARTWHEEL MOUNTED ALUMINIUM LADDER OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT | Nos | 1 | 15000 | 20101.4346 | 20101.4346
30 | WATER COOLER WITH WATER PURIFIER (with R.O & ultra violet purification system of ISI mark) SYSTEM minimum 20 ltrs capacity. | NOS | 1 | 49000 | 65664.6864 | 65664.6864
CCTV Surveilance system
32 | Outdoor PTZ Camera (with PTZ camera housing, gooseneck stand-wall mount bracket, power supply/ adaptor, camera holder and other accessories) (Range: 100Mtrs) | Nos. | 1 | 91758.2 | 96346.11 | 96346.11 | CD 23-24-SS-177
| Indoor Dome Camera (With power injector for dome camera) (Range: 30Mtrs) | Nos. | 3 | 21590.16 | 22669.668 | 68009.004 | CD 23-24-SS-179
| Fish Eye Camera with accessories | Nos. | 2 | 53975.41 | 56674.1805 | 113348.361 | CD 23-24-SS-180
| Supply, installation, commissioning, testing for IP based CCTV system with accessories: 16 Channel NVR with 2 SATA for 02Nos. Of HDD (with additional mouse and keyboard), 4TB surveillance HDD, 16Port Managed Network switch, 32inch LED Display, media convertor (Box type), 600VA interactive UPS, surge protector for outdoor cameras, Fibre Patch cords, 6Core Armoured Fibre Optic Cable, CAT6 STP Cable (outdoor), CAT6 STP cable (Indoor), 1.1KV Armoured Cu-Power Cable, 6U Network Rack, HDPE Conduit pipe for FO with necessary accessories, PVC conduit pipe for CAT6 with necessary accessories, Outdoor Junction Box, Pole with pole mount brackets and other accessories, LIU-Box with accessories (Adapter plate, pigtail, etc), Computer Desk, Installation & commissioning cost (Including casing-capping for UTP & power cables etc and Electrical Cabling & other Miscellaneous work as per site requirement) | LOT | 1 | 393218.42 | 412879.341 | 412879.341 | CD 23-24-SS-181
33 | Supply of Smoke & Heat detection system: Addressable optical Smoke & Heat Multi detector (quantity as per approved design calculation) for cum control room building including all accessories, the Main control panel (Microprocessor based 2 loop fire alarm control panel expandable upto 18 loops fully networkable with each loop capable of taking 99 devices, 8 line x 40 character alpha- numeric liquid crystal display .The panel shall be soft addressable type . The panel shall be able to give pin point location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have in built rectifier, Loop cards,provision for externel & internal printer(if required), L C D unit to indicate Fire/Fault Signal with address and analog output, built in printer to log all fire or fault events complete in all respects, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with BMS & PA system ,wall mounting loop powered addressable type hooter with all accessories , addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection etc. Should have facility for integration with SAS. | Set | 1 | 636000 | 852300.8274 | 852300.8274 | LOA NO.118/22.02.19 GODISAHI GIS
34 | INDOOR LIGHTING OF CR BUILDING ,SECURITY SHED CUM VISITORS ROOM, PUMP HOUSE, STORE SHED, STORE ROOM, PARKING SHED, DG SHED BUILDING: IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj/Havels) with switch gear for succesful illumination of the area/rooms. (No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | Lot | 1 | 400000 | 400000 | 400000 | Tentative
31 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO 18 ANNEXURE - IV INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) for PLACING IN CONTROL ROOM .CONFERENCE ROOM.OFFICE ROOMS. LIBRARY.TESTING LAB. etc. | SET | 1 | 500000 | 500000 | 500000 | tentative
| TOTAL_SUPPLY |  |  |  |  | 24995432.7608
| GST 18% on PART -A, SCHEDULE-2A-SUPPLY (FOR 132KV 1no. Bay Extension) |  |  |  |  | 4499177.8969
| PART -A, SCHEDULE-2A-SUPPLY (FOR 132KV 1no. Bay Extension) including GST 18% |  |  |  |  | 29494610.6577
| Estimator MT (Fin.) |  |  | Deputy General Manager (Elect.),
| E.H.T (Const.) Division, E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## VIIB VIIC SS ERECTION_CIVIL
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Polaspanga.
ERECTION OF EQUIPMENTS/ MATERIALS AND CIVIL WORKS
PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 132KV SUB-STATION WORK)
SLNO | DESCRIPTION OF ITEMS(SCHEDULE-VIIB ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS) (As per Technical Specification) | Unit | Qty
|  |  |  | Unit Price IN INR | OGST@9% | CGST@9% | Total Unit Price with GST | Total Amount | PRICE REF: COST DATA/ OPTCL'S LATEST PO PRICE
1 | ELECTRICAL WORKS
1.1 | 145 KV,(800-400-200 Ratio), 40KA, 5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 6 | 7925.99 | 713.3391 | 713.3391 | 9352.6682 | 56116.0092 | RC25-26-SS-E.1.12g(i)
1.2 | S/I WITH OUT EARTH SWITCH | NOS | 2 | 13829.2 | 1244.628 | 1244.628 | 16318.456 | 32636.912 | RC25-26-SS-E.1.12g(i)
1.3 | D/I WITH SINGLE EARTH SWITCH | NOS | 2 | 22291.86 | 2006.2674 | 2006.2674 | 26304.3948 | 52608.7896 | RC25-26-SS-E.1.12g(i)
1.4 | Beam Mounted Isolator W/O E/S (S/I) | NOS | 1 | 12384.36 | 1114.5924 | 1114.5924 | 14613.5448 | 14613.5448 | RC25-26-SS-E.1.12g(i)
1.5 | 145 KV, 3CORE,SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 7925.99 | 713.3391 | 713.3391 | 9352.6682 | 56116.0092 | RC25-26-SS-E.1.12g(i)
1.6 | 120 KV METAL OXIDE SURGE ARRESTOR, 10 KA, Class III | NOS | 6 | 4458.37 | 401.2533 | 401.2533 | 5260.8766 | 31565.2596 | RC25-26-SS-E.1.12g(i)
1.7 | 132 KV Bus Post Insulators | NOS | 20 | 1816.37 | 163.4733 | 163.4733 | 2143.3166 | 42866.332 | RC25-26-SS-E.1.12g(i)
1.8 | 145KV, 3150A, 40KA, SF6 CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | SET | 2 | 24355.92 | 2192.0328 | 2192.0328 | 28739.9856 | 57479.9712 | RC25-26-SS-E.1.12g(i)
BUS BAR & CIRCUIT MATERIALS
2 | ACSR MOOSE CONDUCTOR STRINGING
2.1 | Busbar stringing (for single moose) wirth fixing of insulator | Mtrs | 200 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 42867.04 | RC25-26-SS-F.1.e(i)
2.2 | Busbar stringing (for twin moose) wirth fixing of insulator | Mtrs | 70 | 247.93 | 22.3137 | 22.3137 | 292.5574 | 20479.018 | RC25-26-SS-F.1.f(i)
3 | ACSR MOOSE CONDUCTOR JUMPERING
3.1 | Jumpering to equipments with fixing of clamps and connectors (for single moose) | Mtrs | 200 | 132.1 | 11.889 | 11.889 | 155.878 | 31175.6 | RC25-26-SS-F.1.f(i)
3.2 | Jumpering to equipments with fixing of clamps and connectors (for twin moose) | Mtrs | 60 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 12860.112 | RC25-26-SS-F.1.f(i)
4 | EARTHING MATERIALS
4.1 | EARTHING CONDUCTOR FOR BURRIAL : 75x10 mm GI Earth Flat for laying (Spacing maximum 5m both ways) | Mtrs | 1695 | 108.47 | 9.7623 | 9.7623 | 127.9946 | 216950.847 | RC25-26-SS-I.1.1.vi(b)
4.2 | EARTHING CONDUCTOR : 50 X 6 mm GI Earth Flat for raiser from the burrial earthmat to equipment, structure etc. | Mtrs | 2512 | 108.47 | 9.7623 | 9.7623 | 127.9946 | 321522.4352 | RC25-26-SS-I.1.1.vi(b)
4.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 32 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 111169.5936 | RC25-26-SS-I.1.1.vi(b)
4.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 20 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 69480.996 | RC25-26-SS-I.1.1.vi(b)
4.5 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:2-2,3-3 & 4-4 along with its accessories as per TS. | Lot | 2 | 70000 | 6300 | 6300 | 82600 | 165200 | Tentative
5 | SUB STATION SWITCYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES
5.1 | BAY MARSHALLING KIOSK | NOS | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC23-24-SS-18.4
5.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC23-24-SS-18.4
5.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC23-24-SS-18.4
5.4 | Consol box for CTs(1nos) & CVTs(1nos) | NOS | 4 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 14184.8744 | RC23-24-SS-18.6
6 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 132KV CLASS (column & Beam) | MT | 11.774 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 79654.1548 | RC25-26-SS-F.3.2
7 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 1.1774 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 7965.4155 | RC23-24-SS-16.1
8 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 132KV EQUIPMENTS | MT | 12.882 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 87150.0613 | RC23-24-SS-16.1
9 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 1.2882 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 8715.0061 | RC23-24-SS-16.1
10 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
10.1 | PVC 3.5 CX70 mm2 | MTRS | 1200 | 674.0484 | 60.6644 | 60.6644 | 795.3771 | 954452.4642 | RC23-24-SS-17.2-viii
10.2 | PVC 3.5 CX35 mm2 | MTRS | 1200 | 511.3413 | 46.0207 | 46.0207 | 603.3828 | 724059.3455 | RC23-24-SS-17.2-vi
10.3 | PVC 4 CX 16 mm2 | MTRS | 800 | 271.1646 | 24.4048 | 24.4048 | 319.9742 | 255979.399 | RC23-24-SS-17.2-iv
10.4 | PVC 4 CX 6 mm2 | MTRS | 600 | 154.9532 | 13.9458 | 13.9458 | 182.8447 | 109706.8447 | RC23-24-SS-17.2-ii
10.5 | PVC 4CX 4 mm2 | MTRS | 900 | 123.97 | 11.1573 | 11.1573 | 146.2846 | 131656.14 | RC23-24-SS-17.2-i
11 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
11.1 | 2 CX 2.5 mm2 | MTRS | 2400 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 153595.4124 | RC23-24-SS-17.1-i
11.2 | 4 CX 2.5 mm2 | MTRS | 5000 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 319990.4426 | RC23-24-SS-17.1-iii
11.3 | 7CX 2.5 mm2 | MTRS | 4000 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 255992.354 | RC23-24-SS-17.1-iv
11.4 | 10 CX 2.5 mm2 | MTRS | 3000 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 219394.2569 | RC23-24-SS-17.1-vi
11.5 | 12 CX 2.5 mm2 | MTRS | 3000 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 219394.2569 | RC23-24-SS-17.1-vii
11.6 | 16 CX 2.5 mm2 | MTRS | 3000 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 219394.2569 | RC23-24-SS-17.1-viii
11.7 | 19 CX 2.5 mm2 | MTRS | 4000 | 77.4834 | 6.9735 | 6.9735 | 91.4305 | 365721.8702 | RC23-24-SS-17.1-ix
12 | 132 KV CONTROL RELAY PANEL
12.1 | 132 KV FEEDER PROTECTION PANEL: 1 feeder in one panel Numerical Distance Protection relay, Backup relay, BCU and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power supply 220V DC. TNC for CB and PBs for Isolators shall be provided additionally. | Nos | 2 | 28484.05 | 2563.5645 | 2563.5645 | 33611.179 | 67222.358 | RC25-26-SS-H.1.1(iv)
13 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).(150 watt each) | LOT | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Tentative
14 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos. | 20 | 413.56 | 37.2204 | 37.2204 | 488.0008 | 9760.016 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
14.1 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | Nos. | 20 | 4138.98 | 372.5082 | 372.5082 | 4883.9964 | 97679.928
14.2 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB. | Nos. | 1 | 5912.71 | 532.1439 | 532.1439 | 6976.9978 | 6976.9978
15 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | NOS | 6 | 5912.71 | 532.1439 | 532.1439 | 6976.9978 | 41861.9868
16 | FIRE FIGHTING SYSTEM (ONE EACH TYPE AS PER LIST BELOW)
16.1 | SODA ACID TYPE-9 LTRS | LOT | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | Tentative
16.2 | FOAM TYPE-9 LTRS
16.3 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS
16.4 | DRY POWDER TYPE - 5 KGS
16.5 | CO2 - 4.5 KGS
16.6 | CO2 - 9 KGS
16.7 | CO2 (TROLLY MOUNTED)- 22.5 KGS
16.8 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND
17 | BEST QUALITY &APPROVED MAKE INSULATING MAT for suitable voltage (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos | 20 | 500 | 45 | 45 | 590 | 11800 | Tentative
18 | Mereting Panel | Nos | 1 | 5000 | 450 | 450 | 5900 | 5900 | Tentative
19 | Meter(Main & Check) | Nos | 4 | 5000 | 450 | 450 | 5900 | 23600 | Tentative
20 | SUBSTATION AUTOMATION SYSTEM: Erection of the following 132KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of Industrial computer with accessories, PC with accessories, laser printer, UPS, GPS system & numerical Bay Control unit etc.
20.1 | 132KV Level
20.1.1 | Yard AC Kiosk: 4500mm (L)X4000mm(W)X3500mm(H) with AC,as per specification | Nos. | 1 | 2259.3308 | 203.3398 | 203.3398 | 2666.0104 | 2666.0104 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
20.1.2 | BCU for 132KV side: Numerical Bay Control unit:32 Digital Input & 28Nos. Digital output with 4 CT Input,4 VT inputs,8 insulated transducer input(-20mA to +20mA) values on 8 independent galvanic isolated channels for TRF bay application, IEC 61850 protocol with PRP,power supply 220V DC | Nos. | 1 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 2826.9203
20.1.3 | Numerical Distance protection with PRP,IEC 61850 protocol.Digital input & output to be provided as per the scheme. | Nos. | 2 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 5653.8405
20.1.4 | Numerical O/C & E/F relays: IEC 61850protocol with PRP Digital input & outpot to be provided as per the scheme | Nos. | 2 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 5653.8405
20.1.5 | High impedance REF relay. Digital input & output to be provided as per scheme | Nos. | 2 | 2669.4048 | 240.2464 | 240.2464 | 3149.8976 | 6299.7953
20.1.6 | Auxiliary Relay for DC supervision | Nos. | 2 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 5653.8405
20.1.7 | MPG-TEST BLOCK | Nos. | 8 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 22615.362
20.1.8 | High speed Trip relay (Electrical Reset) 86A,86B,96 | Nos. | 8 | 2395.6951 | 215.6126 | 215.6126 | 2826.9203 | 22615.362
15 | ERECTION FOR OPGW SYSTEM |  |  |  | 0 | 0 | 0 | 0
15.1 | 48 Fibre Optic approach cable (DWSM) | KM | 1 | 45000 | 4050 | 4050 | 53100 | 53100 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
15.2 | Erection / commissioning of SDH/MUX along with termination with FODP | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
15.3 | Erection / commissioning of digital teleprotection coupler | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986
15.4 | Earth flat, Cable tray, telephone Cable,ACDB,DCDB,Foundation rail,Junction Box. | Set | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
15.5 | DCDB | NO. | 1 | 3547.46 | 319.2714 | 319.2714 | 4186.0028 | 4186.0028
15.6 | 2.5sqmm 2C/3C control cable laying | Mtr | 400 | 23.73 | 2.1357 | 2.1357 | 28.0014 | 11200.56
| TOTAL OF ELECTRICAL WORKS | [6 empty] | 6067403.6744
CIVIL WORKS
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 1000 | 5.78 | 0.5202 | 0.5202 | 6.8204 | 6820.4 | RC SS 1.10
1.2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge upto 15 m depth. | PER POINT | 2 | 37978.72 | 3418.0848 | 3418.0848 | 44814.8896 | 89629.7792 | RC24-25-SS-1.1.5(b)
2 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
2.1 | CUTTING of substation area and utilising the usable soil for filling and compaction and disposing the unsuable soil from site
2.1.1 | [iii]Soft/Disintegrated rock soil (400sqm*0.3m) | CUM | 250 | 594.8 | 53.532 | 53.532 | 701.864 | 175466 | RC24-25-SS-B.1.iii
2.2 | FILLING of substation area with borrowed earth with supply of all labour,T & P.
2.2.1 | (iii) beyond 100mtr lead (550sqm*0.4) | CUM | 450 | 1144.94 | 103.0446 | 103.0446 | 1351.0292 | 607963.14 | RC24-25-SS-B.2.iii
3 | Foundations for capping,tie beam & pedestal etc. : Design, engineering, supply of all labour, material and constructionof PCC, RCC footings of any depth, pedestal including concreting, cement, excluding reinforcement steel, shuttering, grouting, underpinning and back filling of foundations etc complete for the switchyard gantry/ portal /column structures and equipment support as per the technical specification and approved drawings & disposal of excess earth as per the direction of Engineer In charge.
3.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge.
3.1.1 | Soft Soil/Loose Soil. | CUM | 360 | 183.0214 | 16.4719 | 16.4719 | 215.9653 | 77747.4959 | RC24-25-SS-B.1.i
3.1.2 | Dense Soil. | CUM | 700 | 289.78 | 26.0802 | 26.0802 | 341.9404 | 239358.28 | RC24-25-SS-B.1.ii
3.1.4 | Soft/Disintegrated Rock( not Requiring Blasting) | CUM | 300 | 648.18 | 58.3362 | 58.3362 | 764.8524 | 229455.72 | RC24-25-SS-B.1.iv
3.1.5 | Hard Rock (Requiring Blasting/Using Rock Breaker Machinery) | CUM | 100 | 1067.58 | 96.0822 | 96.0822 | 1259.7444 | 125974.44 | RC24-25-SS-B.1.iv
4 | Plain cement concrete (PCC 1:3:6) of grade M10: Supply of all materials, good quality planks, ballas, shuttering plates for centering, shuttering, supply of good quality 20mm machine broken granite chips, good quality river sand and concreting, curing for foundation of columns, equipment structure, transformer etc. as per IS:4156 including cost of taxes, royalties, lead lift, labour and T&P as per Technical specification and instruction of Engineer In charge. (With cost of cement & without steel) | CUM | 40 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 278843.912 | RC24-25-SS-B.1.2(i)
5 | RCC: 1:1.5:3 (Grade M-20) Supply of all materials, good quality planks, ballas, shuttering plates for centering, shuttering, supply of good quality 20mm machine broken granite chips, good quality river sand and concreting, curing for foundation of columns, equipment structure, transformer and cable trench slab etc. as per IS:4156 including cost of taxes, royalties, lead lift, labour and T&P as per Technical specification and instruction of Engineer In charge. (With cost of cement & without steel) | CUM | 400 | 8533.36 | 768.0024 | 768.0024 | 10069.3648 | 4027745.92 | RC24-25-SS-B.1.4(i)
6 | Supply of steel different sizes(TATA/RINL/SAIL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 12 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 927639.8664 | RC24-25-SS-1.1(i)
7 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge including supply of all labour, T&P, materials. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod(FE 500),Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash brickwork with Fly ash brick ,plastering (!:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc.
(5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}.
7.1 | Cable trench with covers
7.1.1 | Section 1- 1 | Lot | 1 | 1500000 | 135000 | 135000 | 1770000 | 1770000 | Tentative
7.1.2 | Section 3-3
7.1.3 | Section 4-4
8 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper levelling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area .After proper levelling of the switch yard area (after anti-weed treatment), spreading of plain cement concret with mixing ratio 1:3:6 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area . As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge.This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge and approved drawing. (950 sqm * 0.075m = 71.25 or say 71 ) | CUM | 150 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 1045664.67 | RC24-25-SS-B.1.2(i)
9 | Metal Spreading:Providing supplying and laying two layers of machine crushedmetals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8).The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. ( 950* 0.1=95) | CUM | 190 | 3233.69 | 291.0321 | 291.0321 | 3815.7542 | 724993.298 | RC24-25-SS-3.1
10 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. All the switcyard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification.
10.1 | Storm water drain | mtr | 100 | 3870 | 348.3 | 348.3 | 4566.6 | 456660 | Tentative
10.2 | Road side drain | mtr | 270 | 3317 | 298.53 | 298.53 | 3914.06 | 1056796.2
10.3 | Road-culverts, drain crossings | Lot | 1 | 400000 | 36000 | 36000 | 472000 | 472000
10.4 | Cable trench crossing | Lot | 1 | 400000 | 36000 | 36000 | 472000 | 472000
11 | Switchyard fencing: Providing and fixing of G.I chain link(2.5mm dia) fencing( the posts and links shall be of HD Galvanised ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central governemet bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous RR masonary work withratio 1:5 and cement pointing of the joints, for the fencing upto a height of 350mm from the finished ground level) .This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge. The earthing of the fencing as per specification. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Tentative
12 | COLOUR CODING, BAY MARKING : Design, engineering, procurement of labour, materials including all associated works for the followings. This should be as per direction of site in-charge, a) colour coding (red, yellow, blue) for equipments, bus guntry and column of entire switchyard. b) Identified with the help of bay marker sign board, suitable grouted, MS sign board with stand to be installed. Proper painting and lettering to be done of the entired switchyard. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | Tentative
13.1 | 3.75 mtrs Concrete road with shoulder at both the side as per technical specification indicated in the civil section, approved drawing and instruction of Engineer in charge. | Mtr | 25 | 20516 | 1846.44 | 1846.44 | 24208.88 | 605222 | Tentative
13.2 | 7 mtrs wide Concrete roads with shoulder as per specification indicated in the civil sectionapproved drawing and instruction of Engineer in charge. | Mtr | 80 | 12494 | 1124.46 | 1124.46 | 14742.92 | 1179433.6 | Tentative
| TOTAL OF CIVIL WORKS | [6 empty] | 15277414.7215
| PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 132KV SUB-STATION WORK) | [6 empty] | 21344818.396
| Estimator |  |  | Deputy General Manager (Elect.),
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## VIIA LINE SUPPLY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
Conductor:- Turumunga-Palaspanga: HTLS Panther, Palaspanga-Dhenkikote:Panther |  | Total length of over head line- 26.839 Km.
Earth wire- OPGW |  | Total towers- 108 Nos.
No. of Ciruit- DC line on DC tower |  | Angle towers- 68 Nos.
PART-B (132KV SC line)
COST OF EQUIPMENTS/MATERIALS
SCHEDULE-VII A (FOR LINE)
Sl. No. | DESCRIPTION OF ITEMS | Unit |  | IN INR
| SUPPLY OF FOLLOWING EQUIPMENTS/MATERIALS ALONG WITH CIVIL WORKS (As per Technical Specification) |  |  | Unit Price | SGST @ 9% | CGST @ 9% | Total unit cost including GST, Rs. | Total Price | Price Reference
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=8 x 4
1 | SUPPLY of following type tested Lattice type Galvanized steel Tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1 | PA TYPE (SUSPENSION ) TOWERS ( 2.993MT) 40 Nos. | MT | 119.72
1.1 | +3 EXTENSION ( 0.609 MT) -15 NOS. | MT | 9.135
1.2 | +6 EXTENSION ( 1.291 MT) - 10 NOS. | MT | 12.91
2 | PB TYPE (30 deg ANGLE ) TOWERS ( 4.517MT) - 30 NO. | MT | 135.51
2.1 | +3 EXTENSION ( 0.975MT) -10 NO. | MT | 9.75
2.2 | +6 EXTENSION ( 2.020 MT) - 5 NO. | MT | 10.1
3 | PC TYPE (60 deg ANGLE ) TOWERS ( 5.317MT)- 30 NOS. | MT | 159.51
3.1 | +3 EXTENSION ( 1.069 MT) - 8 NOS. | MT | 8.552
3.1 | +6 EXTENSION ( 2.246 MT) - 7 NOS. | MT | 15.722
4 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 8 NOS. | MT | 99.504
4.1 | +6 EXTENSION ( 4.161MT) - 8 NOS. | MT | 33.288
5 | STUBS & CLEATS
5.1 | PA TYPE( 0.252 MT)- 40Nos. | MT | 10.08
5.2 | PB TYPE ( 0.432 MT)-30Nos. | MT | 12.96
5.3 | PC TYPE ( 0.609 MT)-30Nos. | MT | 18.27
5.4 | UR TYPE ( 0.697 MT)- 8No. | MT | 5.576
6 | TEMPLATES
6.1 | PA TYPE( 0.252 MT)- 4Nos. | MT | 1.008
6.2 | PB TYPE ( 0.432 MT)-2Nos. | MT | 0.864
6.3 | PC TYPE ( 0.609 MT)-2Nos. | MT | 1.218
6.4 | UR TYPE ( 1.476 MT)- 1No. | MT | 1.476
7 | WEIGHT OF THE STRUCTURES (excluding templates) |  | 660.587 | 94889.6025 | 8540.06 | 8540.06 | 111969.7225 | 73965743.0771 | CD 24-25 Line sl.2
8 | MS enamel painted templates | MT | 4.566 | 73323.789 | 6599.14 | 6599.14 | 86522.069 | 395059.7671 | CD 24-25 Line sl.6
9 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 49.886 | 124488.693 | 11203.98 | 11203.98 | 146896.653 | 7328086.4316 | CD 24-25 Line sl.5
10 | Supply of the following tower accessories as per technical specification.
10.1 | EARTHING DEVICE | Nos. | 216 | 2395.029 | 215.55 | 215.55 | 2826.129 | 610443.864 | CD 24-25 Line sl.8
10.2 | DANGER BOARD | Nos. | 216 | 248.6085 | 22.37 | 22.37 | 293.3485 | 63363.276 | CD 24-25 Line sl.9
10.3 | NUMBER PLATE | Nos. | 216 | 135.849 | 12.23 | 12.23 | 160.309 | 34626.744 | CD 24-25 Line sl.10
10.4 | PHASE PLATE | Nos. | 648 | 105.966 | 9.54 | 9.54 | 125.046 | 81029.808 | CD 24-25 Line sl.11
10.5 | BIRD GUARD | Nos. | 240 | 524.7398 | 47.23 | 47.23 | 619.1998 | 148607.9607 | LOA NO.137,Dt.16.02.23 (Turumunga -Dhenkikote), Line 2.5
10.6 | ANTICLIMBING DEVICE | Nos. | 108 | 4620.2415 | 415.82 | 415.82 | 5451.8815 | 588803.202 | CD 24-25 Line sl.13
10.7 | CIRCUIT PLATE | Nos. | 216 | 105.966 | 9.54 | 9.54 | 125.046 | 27009.936 | CD 24-25 Line sl.12
10.8 | FLEXIBLE COPPER EARTH BOND | Nos. | 108 | 292.0785 | 26.29 | 26.29 | 344.6585 | 37223.118 | CD 24-25 Line sl.46
10.9 | 75X10 MM GI FLAT | MT | 9 | 98124.4845 | 8831.2 | 8831.2 | 115786.8845 | 1042081.9605 | CD 24-25-Line-4
11 | Supply of following POWER CONDUCTORS as per the technical specification.
11.1 | HTLS Conductor, ACSR Panther equivalent (solid Carbon Core) (From Turumunga GSS to Palaspanga GSS) | KM | 91.35 | 1263250.8 | 113692.57 | 113692.57 | 1490635.94 | 136169593.119 | CD 24-25 Line sl.21
11.2 | ACSR Panther (30+7/3.0 mm) (from Palaspanga to LILO point) | Kms. | 81.7248 | 201893.013 | 18170.37 | 18170.37 | 238233.753 | 19469595.0967 | CD 24-25 Line sl.17
12 | POWER CONDUCTOR ACESSORIES
12.1 | For HTLS Conductor equivalent to ACSR PANTHER
12.1.1 | VIBRATION DAMPER | Nos. | 648 | 2340.45 | 210.64 | 210.64 | 2761.73 | 1789601.04 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
12.1.2 | MID SPAN JOINT | Nos. | 50 | 43038.45 | 3873.46 | 3873.46 | 50785.37 | 2539268.5 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
12.1.3 | Repair Sleeve | Nos. | 25 | 2626.05 | 236.34 | 236.34 | 3098.73 | 77468.25 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
12.2 | For ACSR PANTHER
12.2.1 | VIBRATION DAMPER | Nos. | 648 | 489.4365 | 44.05 | 44.05 | 577.5365 | 374243.652 | CD 24-25 Line sl.31
12.2.2 | MID SPAN JOINT | Nos. | 50 | 562.422 | 50.62 | 50.62 | 663.662 | 33183.1 | CD 24-25 Line sl.36
12.2.3 | Repair Sleeve | Nos. | 25 | 231.84 | 20.87 | 20.87 | 273.58 | 6839.5 | CD 24-25 Line sl.42
12.2.4 | Performed Armoured Rod | Set | 40 | 563.8395 | 50.75 | 50.75 | 665.3395 | 26613.58 | CD 24-25 Line sl.27
13.1 | Supply of the following Anti fog type Porceain Disc Insulators as per the technical specification for ACSR Panther Equivalent
13.1.1 | 120 KN Porcelain Antifog Disc Insulators | Nos. | 135 | 14172.9 | 1275.56 | 1275.56 | 16724.02 | 2257742.7 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.1.2 | 90 KN Porcelain Antifog Disc Insulators | Nos. | 456 | 16024.05 | 1442.16 | 1442.16 | 18908.37 | 8622216.72 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.2 | Supply of the following Anti fog type Porceain Disc Insulators as per the technical specification for ACSR Panther
13.2.1 | 120 KN Porcelain Antifog Disc Insulators | Nos. | 135 | 6620.18 | 595.82 | 595.82 | 7811.82 | 1054595.7 | CD 24-25 Line sl.61
13.2.2 | 90 KN Porcelain Antifog Disc Insulators | Nos. | 456 | 7826.07 | 704.35 | 704.35 | 9234.77 | 4211055.12 | CD 24-25 Line sl.62
14 | Supply of the following hardware fittings suitable for HTLS conductor (ACSR Panther equivalent) as per the technical specification.
14.1 | Single Suspension Hardware fittings (1 x 90kN) | Nos. | 210 | 8104.95 | 729.45 | 729.45 | 9563.85 | 2008408.5 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
14.2 | Double suspension Hardware fittings (2 x 90kN) | Nos. | 30 | 14370.3 | 1293.33 | 1293.33 | 16956.96 | 508708.8 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.3 | Single Tension Hardware fittings (1 x 120kN) | Nos. | 600 | 40936.35 | 3684.27 | 3684.27 | 48304.89 | 28982934 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.4 | Double tension Hardware fittings (2 x 120kN) | Nos. | 216 | 47260.5 | 4253.45 | 4253.45 | 55767.4 | 12045758.4 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.5 | Single Suspension Hardware fittings for pilot (1 x 90kN) | No. | 15 | 7700.7 | 693.06 | 693.06 | 9086.82 | 136302.3
13.6 | T-Clamp (HTLS run-Moose drop) | Nos. | 12 | 6578.6175 | 592.08 | 592.08 | 7762.7775 | 93153.33 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
13.7 | Compression Die suitable for the HTLS conductor | Sets | 2 | 32691.33 | 2942.22 | 2942.22 | 38575.77 | 77151.54 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
16 | Supply of the following hardware fittings suitable for ACSR Panther conductors as per the technical specification.
16.1 | For ACSR PANTHER
16.1.1 | Single Suspension Hard wares fittings (AGS Type, Including Armoured Rod) (1x90kN) | Nos. | 210 | 2084.418 | 187.6 | 187.6 | 2459.618 | 516519.78 | CD 24-25 Line sl.25
16.1.2 | Double suspension Hard wares fittings (2x90kN) | Nos. | 30 | 2084.418 | 187.6 | 187.6 | 2459.618 | 73788.54 | CD 24-25 Line sl.21
16.1.3 | Single Tension Hardware fittings (1 x120kN) | Nos. | 600 | 1847.202 | 166.25 | 166.25 | 2179.702 | 1307821.2 | CD 24-25 Line sl.22
16.1.4 | Double tension Hardware fittings (2x120kN) | Nos. | 216 | 4125.891 | 371.33 | 371.33 | 4868.551 | 1051607.016 | CD 24-25 Line sl.23
| Single Suspension Hardware fittings for pilot (1x90kN) | Nos. | 10 | 2084.418 | 187.6 | 187.6 | 2459.618 | 24596.18
16.1.5 | D' shackle | Nos. | 816 | 416.4583 | 37.48 | 37.48 | 491.4183 | 400997.3736 | LOA NO.137,Dt.16.02.23 (Turumunga -Dhenkikote)
16.1.6 | U' Bolt | Nos. | 40 | 111.2643 | 10.01 | 10.01 | 131.2843 | 5251.372 | CD 24-25 Line sl.49
16.1.7 | Hanger | Nos. | 240 | 499.7522 | 44.98 | 44.98 | 589.7122 | 141530.934 | LOA NO.137,Dt.16.02.23 (Turumunga -Dhenkikote)
17 | Supply of OPGW Cable & Hardware fittings
17.1 | Supply of OPGW(DWSM) Fibre Optic Cable 48F | KM | 26.839 | 215500 | 19395 | 19395 | 254290 | 6824889.31 | CD24-25-TEL-25
17.2 | Hardware set for 48F OPGW such as suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper, Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Earth bond,Link plates | KM | 26.839 | 22597.72 | 2033.79 | 2033.79 | 26665.3 | 715669.9867 | CD 24-25-TEL-26
17.3 | Joint Box (splice enclosure),48F | Nos. | 12 | 6491 | 584.19 | 584.19 | 7659.38 | 91912.56 | CD 24-25-TEL-28
18 | Supply of Dynamic Bird Flight Diverter
18.1 | Supply of dynamic bird flight diverter LED type for conductor(for top conductor) | Nos. | 300 | 2205 | 198.45 | 198.45 | 2601.9 | 780570 | Order no.517(3), Dt.13.12.2023 of GM(El), EHT(C) Circle, Sambalpur
18.2 | Supply of dynamic bird flight diverter LED type for OPGW wire | Nos. | 300 | 5533.5 | 498.02 | 498.02 | 6529.54 | 1958862
19 | Intensity Aviation Light | Nos. | 5 | 50000 | 4500 | 4500 | 59000 | 295000 | Tentative
| TOTAL PART-B, SCHEDULE-VII A (FOR LINE) | [6 empty] | 318995528.3449
Note on B86: OPTCL: The description shall be as per the description in 400KV UOM shall be per KM

## VIIB VIIC LINE ERECTION_CIVIL
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
Conductor:- Turumunga-Palaspanga: HTLS Panther, Palaspanga-Dhenkikote:Panther |  | Total length of over head line- 26.839 Km.
Earth wire- OPGW |  | Total towers- 108 Nos.
No. of Ciruit- DC line on DC tower |  | Angle towers- 68 Nos.
132KV DC line
SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (132KV DC LINE )
Sl. No. | DESCRIPTION OF ITEMS | Unit | QTY | IN INR
| DESCRIPTION OF ITEMS (SCHEDULE-2C) ERECTION, TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) |  |  | Unit Price |  |  |  | Total Price | Rate contract Ref
1 | 2 |  | 4 | 5 |  |  |  | 6=4X5
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. This includes supply of all labourers, T&P, head loading of all type of structures, & other materials required for erection. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1 | PA TYPE (SUSPENSION ) TOWERS ( 2.993MT) 40 Nos. | MT | 119.72
1.1 | +3 EXTENSION ( 0.609 MT) -15 NOS. | MT | 9.135
1.2 | +6 EXTENSION ( 1.291 MT) - 10 NOS. | MT | 12.91
2 | PB TYPE (30 deg ANGLE ) TOWERS ( 4.517MT) - 30 NO. | MT | 135.51
2.1 | +3 EXTENSION ( 0.975MT) -10 NO. | MT | 9.75
2.2 | +6 EXTENSION ( 2.020 MT) - 5 NO. | MT | 10.1
3 | PC TYPE (60 deg ANGLE ) TOWERS ( 5.317MT)- 30 NOS. | MT | 159.51
3.1 | +3 EXTENSION ( 1.069 MT) - 8 NOS. | MT | 8.552
3.1 | +6 EXTENSION ( 2.246 MT) - 7 NOS. | MT | 15.722
4 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 8 NOS. | MT | 99.504
4.1 | +6 EXTENSION ( 4.161MT) - 8 NOS. | MT | 33.288
5 | STUBS & CLEATS
5.1 | PA TYPE( 0.252 MT)- 40Nos. | MT | 10.08
5.2 | PB TYPE ( 0.432 MT)-30Nos. | MT | 12.96
5.3 | PC TYPE ( 0.609 MT)-30Nos. | MT | 18.27
5.4 | UR TYPE ( 0.697 MT)- 8No. | MT | 5.576
6 | TEMPLATES
6.1 | PA TYPE( 0.252 MT)- 40Nos. | MT | 10.08
6.2 | PB TYPE ( 0.432 MT)-30Nos. | MT | 12.96
6.3 | PC TYPE ( 0.609 MT)-30Nos. | MT | 18.27
6.4 | UR TYPE ( 1.476 MT)- 8No. | MT | 11.808
7 | WEIGHT OF THE STRUCTURES (excluding templates) | MT | 613.701 | 7265.49 | 653.89 | 653.89 | 8573.27 | 5261424.3723
8 | MS enamel painted templates | MT | 100.004 | 5596.02 | 503.64 | 503.64 | 6603.3 | 660356.4132
9 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 49.886 | 7265.49 | 653.89 | 653.89 | 8573.27 | 427686.1472
10 | Erection of the following tower accessories as per technical specification.
10.1 | EARTHING OF TOWER: Pipe type earthing including cost of bentonate compound and good borrowed earth where necessary in accordance with IS:3043-1966 and with supply of all T&P and Labour, with excavation of Morrum and laterite layer and back filling with good borrowed earth.- i)With cost of earthing pipe (50mm Dia 3050mm length medium gauge and 50X6mm GI flat | Nos. | 216 | 7841.39 | 705.73 | 705.73 | 9252.85 | 1998615.6 | RC23-24 line 8.2.i
10.2 | DANGER BOARD | Nos. | 216 | 124.03 | 11.16 | 11.16 | 146.35 | 31611.6 | RC23-24 line 11.ii
10.3 | NUMBER PLATE | Nos. | 216 | 124.03 | 11.16 | 11.16 | 146.35 | 31611.6 | RC23-24 line 11.i
10.4 | PHASE PLATE | Nos. | 648 | 124.03 | 11.16 | 11.16 | 146.35 | 94834.8 | RC23-24 line 11.iii
10.5 | BIRD GUARD | Nos. | 240 | 124.03 | 11.16 | 11.16 | 146.35 | 35124 | RC23-24 line 11.iv
10.6 | ANTICLIMBING DEVICE | Nos. | 108 | 2676.58 | 240.89 | 240.89 | 3158.36 | 341102.88 | RC23-24 line 11.v
10.7 | CIRCUIT PLATE | Nos. | 216 | 124.03 | 11.16 | 11.16 | 146.35 | 31611.6 | RC23-24 line 11.i
11 | Hoisting & fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & jumperingetc. of POWER CONDUCTORS (Three Phase Conductor with out earth wire) as per the technical specification.
11.1 | HTLS Conductor (ACSR Panther equivalent) | km | 30 | 520223 | 46820.07 | 46820.07 | 613863.14 | 18415894.2 | LOA No.1353,Dt31.12.2024 (CTC-Jagantsingpur)
11.2 | ACSR Panther | km | 26.839 | 56142.45 | 5052.82 | 5052.82 | 66248.09 | 1778032.4875 | RC 25-26-TL-10.10.III.a
12 | ERECTION OF OPGW CABLE
12.1 | 24F/48F OPGW stringing without supply of required HWF, tension assembly set, suspension assembly set, vibration damper set etc.(Under offline condition) | KM | 26.839 | 45000 | 4050 | 4050 | 53100 | 1425150.9 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
13 | Installation of dynamic bird flight diverter LED type in ACSR PANTHER/OPGW wire conductor | No. | 600 | 600 | 54 | 54 | 708 | 424800 | Order no.517(3), Dt.13.12.2023 of GM(El), EHT(C) Circle, Sambalpur
| TOTAL OF ELECTRICAL WORKS (PART-A) | [6 empty] | 30957856.6002
CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey - Making walkover survey ascertaining feasibile route and marking on TOposheet, preparation of route alignment | KM. | 26.839 | 4953.75 | 445.84 | 445.84 | 5845.43 | 156885.4958 | RC25-26 TL-Survey-1.1
1.2 | Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 26.839 | 14035.61 | 1263.2 | 1263.2 | 16562.01 | 444507.7864 | RC25-26 TL-Survey-1.2
1.3 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 26.839 | 6604.99 | 594.45 | 594.45 | 7793.89 | 209180.2137 | RC25-26 TL-Survey-1.4
1.4 | Preparation of land schedule on revenue (if required)maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval.Detail GIS (Geographical Information System) of towers to be included. | KM. | 26.839 | 10733.12 | 965.98 | 965.98 | 12665.08 | 339918.0821 | RC25-26 TL-Survey-1.3
1.5 | Soil Testing in complete shape along with submission of report etc.
1.5.1 | Boring up to 3.0m, 5.0m, 7.0m depth | Per Loc. | 10 | 28071.23 | 2526.41 | 2526.41 | 33124.05 | 331240.5 | RC25-26 TL-Survey-1.5(a)
1.5.2 | Boirng up to 15.0m depth | Per Loc. | 15 | 37978.72 | 3418.08 | 3418.08 | 44814.88 | 672223.2 | RC25-26 TL-Survey-1.5(b)
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposal of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge ( Total 47000 CUM) | [7 empty] | RC23-24 line 2
2.1.1 | Soft/Loose soil | CUM | 1380 | 228.78 | 20.59 | 20.59 | 269.96 | 372544.8 | RC23-24 line 2i
2.1.2 | Dense / compact soil | CUM | 414 | 358.41 | 32.26 | 32.26 | 422.93 | 175093.02 | RC23-24 line 2ii
2.1.3 | Partially submerged soil | CUM | 1380 | 411.79 | 37.06 | 37.06 | 485.91 | 670555.8 | RC23-24 line 2vi
2.1.3 | Fully submerged soil | CUM | 690 | 411.79 | 37.06 | 37.06 | 485.91 | 335277.9 | RC23-24 line 2vi
2.1.4 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 2070 | 686.31 | 61.77 | 61.77 | 809.85 | 1676389.5 | RC23-24 line 2iii
2.1.5 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 4140 | 1372.61 | 123.53 | 123.53 | 1619.67 | 6705433.8 | RC23-24 line 2iv
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 250 | 6218.65 | 559.68 | 559.68 | 7338.01 | 1834502.5 | RC25-26 TL-FDN-1.2(iii)
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation, 500mm under ream piles, pile caps, chimney, risers (if any) with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 2500 | 8877.05 | 798.93 | 798.93 | 10474.91 | 26187275 | RC25-26 TL-FDN-1.4(i)
3.3 | Cutting bending hooking, fixing and binding in poisition of MS bars for rainforcement of all foundations (open or pile types) concrete of towers including supply of wire for binding With supply of steel rod(TATA/RINL/SAIL Make) and head loading. No other make of steel shall be allowed. | MT | 40 | 65511.29 | 5896.02 | 5896.02 | 77303.33 | 3092133.2 | RC25-26 TL-FDN-1.1
4 | WELDING OF TOWER MEMBERS
4.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 150000 | 10.01 | 0.9009 | 0.9009 | 11.8118 | 1771770 | RC25-26 TL-Fabrication-1.1(i)
5 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge.
5.1 | Excavation and Back filling (as per approved drawing)
5.1.1 | Soft/loose soil | CUM | 2000 | 228.78 | 20.59 | 20.59 | 269.96 | 539920 | RC25-26 TL-EXC-1(i)
5.1.2 | Dense/compact soil | CUM | 200 | 358.41 | 32.26 | 32.26 | 422.93 | 84586 | RC25-26 TL-EXC-1(ii)
5.1.3 | Soft/Dis intigrated rock (not required blasting) | CUM | 250 | 686.31 | 61.77 | 61.77 | 809.85 | 202462.5 | RC25-26 TL-EXC-1(iii)
5.2 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply of sand chips etc. | CUM | 250 | 6218.65 | 559.68 | 559.68 | 7338.01 | 1834502.5 | RC25-26 TL-FDN-1.2(iii)
5.3 | PCC in the ratio 1:2:4(Grade M-15) as above. | CUM | 320 | 8877.05 | 798.93 | 798.93 | 10474.91 | 3351971.2 | RC25-26 TL-FDN-1.4(i)
5.4 | RR Massonary work in the ratio 1:5.with cement | CUM | 2000 | 3721.06 | 334.9 | 334.9 | 4390.86 | 8781720 | RC25-26 TL-D-1.1(i)
6 | PTCC approval, railway crossing has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 226644.96 | 20398.05 | 20398.05 | 267441.06 | 267441.06 | LOA NO.137,Dt.16.02.2023 (Turumunga -Dhenkikote)
12 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hector | 15 | 302193.28 | 27197.3952 | 27197.3952 | 356588.0704 | 5348821.056
13 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line. | [7 empty] | Average bench mark value of concerned area
13.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per Loc. | 60 | 180000 | 16200 | 16200 | 212400 | 12744000
13.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | Per Km | 10 | 150000 | 13500 | 13500 | 177000 | 1770000
14 | Barbed wire fencing with spike to avoid wild animals, elephants from electrocution in Reserve Forest area including supply of barbed wire and all other materials as per approved TS and drawings ans as per recommendation of site Engineer-In -Charge | Per Loc. | 25 | 115000 | 10350 | 10350 | 135700 | 3392500 | Tentative
TOTAL CIVIL WORKS | [7 empty] | 83292855.114
TOTAL OF PART - B, SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (132KV SC LINE ) | [7 empty] | 114250711.7142

## SS Summery
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
SUMMARY (PART-A)
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (PART-I SCHEDULE-VIIA (For 132KV 1no. Bay Extension) including GST | 36746704.5294
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 1102401.1359
3 | Sub-Total (sl no. 1+2) | 37849105.6653
4 | Contigency 3% on Sl.No.3 | 1135473.17
5 | T&P cost @ 2% on Sl.No. 3 | 756982.1133
6 | Transportation @5% on Sl.No.3 | 1892455.2833
7 | Total erection Chages (PART-I, SCHEDULE-VIIB & VIIC (FOR 132KV 1no. Bay Extension) including GST | 21344818.396
8 | Total cost of 132KV 1no. Bay Extension (SL. No. 3 to 7) | 62978834.6278
9 | Or Say | 62978835

## Abstract (hidden)
| R0 | R1 | R2
Supply | 24995432.7608 | #REF! | #REF!
Service | 15277414.7215 | #REF! | #REF!
TOTAL | 40272847.4823 | #REF! | #REF!

## Sheet2 (hidden)
Tata Steel Jamshedpur | Across TSL | TGS Electrical
Tata Steel Kalinganagar | BLAST FURNACE | TGS Import
Tata Growth Shop | BF GAS HOLDER | TGS Logistics
Raw Material Projects | BOD | TGS Mechanical
Goplapur | BPRS | TGS Services
Others | CDQ | TGS Steel
| CETP | TGS Technological Packages
CIVIL & INFRA
COBP
Coke Plant
CPP
CRM
Central Ware House
Diesel Locomotive Works
DM Plant
Environment Project
Electrical (T&D)
Expediting
Ferro Alloy Metals Division
General Office
Hooghly Met Coke Ltd
HR
HSM
IBMD
IMS
Joda
Khondbond
LD#1
LD 1 & 2
LD#2
LD-3
LD GAS HOLDER
Logistics
Lime Plant
MRP
MRSS
Noamundi
OHYP
PCI
PDS
PH#3
Power House
PELLET PLANT
R&D
RAIL LOGISTICS
RMHS
RMP
RWTP
Slag Granulation
SMS
SINTER PLANT
Sinter Plant 1 & 2
Tinplate
TGS
TSJ RMGP
UGYP
UTILITY
West Bokaro
Wire and Rod Mill

## LINE CALCULATION
CALCULATION SHEET
SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
1 | PA+0 | 15 | 63.36 | 950.4 | 0.968 | 14.52 | 8.76 | 131.4 | 0.201 | 3.015
2 | PA+3 | 15 | 70 | 1050 | 0.968 | 14.52 | 9.72 | 145.8 | 0.201 | 3.015
3 | PA+6 | 10 | 70 | 700 | 0.968 | 9.68 | 9.72 | 97.2 | 0.201 | 2.01
4 | PB+0 | 15 | 104.43 | 1566.45 | 1.5125 | 22.6875 | 15.49 | 232.35 | 0.272 | 4.08
5 | PB+3 | 10 | 113.49 | 1134.9 | 1.5125 | 15.125 | 17 | 170 | 0.272 | 2.72
6 | PB+6 | 5 | 113.49 | 567.45 | 1.5125 | 7.5625 | 17 | 85 | 0.272 | 1.36
7 | PC+0 | 15 | 141.54 | 2123.1 | 1.74 | 26.1 | 20.64 | 309.6 | 0.309 | 4.635
8 | PC+3 | 8 | 141.54 | 1132.32 | 1.74 | 13.92 | 20.64 | 165.12 | 0.309 | 2.472
9 | PC+6 | 7 | 141.54 | 990.78 | 1.74 | 12.18 | 20.64 | 144.48 | 0.309 | 2.163
10 | UR+0 | 0 | 216.75 | 0 | 7.225 | 0 | 52.04 | 0 | 0.534 | 0
11 | UR+6 | 8 | 216.75 | 1734 | 7.225 | 57.8 | 52.04 | 416.32 | 0.534 | 4.272
12 | DD+0 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
13 | DD+3 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
14 | MB+0 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
15 | MB+6 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
16 | MB+9 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
17 | MC+0 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
18 | MC+6 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
19 | MC+9 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
20 | MC+15 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
21 | QD+9 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
22 | QD+15 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
|  | 108 |  | 11949.4 |  | 194.095 |  | 1897.27 |  | 29.742
[7 empty] | M20 | 1897.27
[7 empty] | M25 | 0
|  |  |  | 13741.81 |  | 223.2092 |  | 2181.8605 |  | 34.2033

## ABSTRACT
ODISHA POWER TRANSMISSION CORPORATION LIMITED
ABSTRACT
Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
Sl. No. | DESCRIPTION | AMOUNT IN INR
1 | PART- A : Construction of 2Nos 220KV Bays Extension at Palaspanga aG rid S/s | 62978835
2 | PART-B : Construction of 132 KV TURUMUNGA-PALASPANGA D/C LINE . | 475972645.3289
| Total Cost of Project (Sl. No. 1+2) | 538951480.3289
Or say |  | 538951480

## LINE SUMMERY
Name of of Works: Construction of 132KV LILO on one circuit of line from one circuit of 132KV Turumunga-Dhenkikote D/C line to 132/33KV Grid S/s, Palaspanga along with 02Nos. 132KV Bays at 132/33KV Grid S/s, Palaspanga.
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (SCHEDULE-VIIA (FOR 132 KV TURUMUNGA-PALASPANGA D/C LINE)) | 318995528.3449
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 9569865.8503
3 | Sub-Total (sl no. 1+2) | 328565394.1952
4 | Contigency 3% on Sl.No.3 | 9856961.8259
5 | T&P cost @ 2% on Sl.No. 3 | 6571307.8839
6 | Transportation @5% on Sl.No.3 | 16428269.7098
7 | Total erection Chages (SCHEDULE-VIIB & VIIC (FOR 132 KV TURUMUNGA-PALASPANGA D/C LINE | 114250711.7142
8 | Tree cutting @20000/- per Kms | 300000
9 | PTCC approval, railway crossing has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | 350000
10 | Grand Total (3+4+5+6+7+8) | 475972645.3289