## CALCULATION SHEET (hidden)
0 |  | CALCULATION SHEET
SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
1 | PA+0 | 4 | 63.36 | 253.44 | 0.968 | 3.872 | 8.76 | 35.04 | 0.201 | 0.804
2 | PA+3 | 1 | 70 | 70 | 0.968 | 0.968 | 9.72 | 9.72 | 0.201 | 0.201
3 | PA+6 | 1 | 70 | 70 | 0.968 | 0.968 | 9.72 | 9.72 | 0.201 | 0.201
4 | PB+0 | 1 | 104.43 | 104.43 | 1.5125 | 1.5125 | 15.49 | 15.49 | 0.272 | 0.272
5 | PB+3 | 1 | 113.49 | 113.49 | 1.5125 | 1.5125 | 17 | 17 | 0.272 | 0.272
6 | PB+6 | 1 | 113.49 | 113.49 | 1.5125 | 1.5125 | 17 | 17 | 0.272 | 0.272
7 | PC+0 | 2 | 141.54 | 283.08 | 1.74 | 3.48 | 20.64 | 41.28 | 0.309 | 0.618
8 | PC+3 | 1 | 141.54 | 141.54 | 1.74 | 1.74 | 20.64 | 20.64 | 0.309 | 0.309
9 | PC+6 |  | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
10 | OB+3 |  | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
11 | OB+6 |  | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
12 | OC+0 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
13 | OC+3 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
14 | OC+6 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
15 | OC+15 |  | 360 | 0 | 10 | 0 | 59 | 0 | 5.6 | 0
16 | OC+24 |  | 390 | 0 | 11 | 0 | 65 | 0 | 5.9 | 0
17 | UR+0 |  | 216.75 | 0 | 7.225 | 0 | 52.04 | 0 | 0.534 | 0
18 | UR+6 |  | 216.75 | 0 | 7.225 | 0 | 52.04 | 0 | 0.534 | 0
19 | DD+0 |  | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
20 | DD+3 |  | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
|  | 12 |  | 1149.47 |  | 15.5655 |  | 165.89 |  | 2.949
SL NO | AP | TOWER | ST FITTING | DT FITTING | SS FITTINg | DS FITTING | VIBRATION DAMPER | EARTHING DEVICE
1 | GANTRY | GANTRY | 3 | 0 | 0 | 0 | 3 | 0
2 | AP 01 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
3 | AP 02 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
4 | AP 03 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
5 | AP 04 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
6 | AP 05 | OC+24 | 0 | 6 | 0 | 0 | 6 | 2
7 | AP 06 | OC+15 | 3 | 3 | 0 | 0 | 6 | 2
8 | AP 07 | OC+15 | 6 | 0 | 0 | 0 | 6 | 1
9 | AP 08 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
10 | AP 09 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
11 | AP 10 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
12 | AP 11 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
13 | AP 12 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
14 | AP12/1 | PA+6 | 0 | 0 | 3 | 0 | 6 | 1
15 | AP 13 | PB+3 | 3 | 3 | 0 | 0 | 6 | 1
16 | AP 14 | PC+3 | 3 | 3 | 0 | 0 | 6 | 1
17 | AP 15 | PB+03 | 3 | 3 | 0 | 0 | 6 | 1
18 | AP 16 | PB+0 | 3 | 3 | 0 | 0 | 6 | 1
19 | AP 17 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
20 | AP 18 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
21 | AP 19 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
22 | AP 20 | PB+03 | 3 | 3 | 0 | 0 | 6 | 1
23 | AP 21 | PC+0 | 3 | 3 | 0 | 0 | 6 | 1
24 | AP 22 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
25 | AP 23 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
26 | AP 23/1 | PA+0 | 0 | 0 | 3 | 0 | 6 | 1
27 | AP 24 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
28 | AP 25 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
29 | AP 26 | DD+0 | 0 | 3 | 0 | 0 | 3 | 9
30 | AP 27 | DD+3 | 3 | 0 | 0 | 0 | 3 | 9
31 | AP 28 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
32 | AP 29 | OC+6 | 6 | 0 | 0 | 0 | 6 | 1
33 | AP 30 | OC+3 | 6 | 0 | 0 | 0 | 6 | 1
34 | AP 31 | OC+0 | 6 | 0 | 0 | 0 | 6 | 1
35 | AP 32 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
36 | AP 33 | OC+3 | 6 | 0 | 0 | 0 | 6 | 1
37 | AP 34 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
38 | AP34/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
39 | AP 35 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
40 | AP 36 | OC+15 | 6 | 0 | 0 | 0 | 6 | 1
41 | AP 37 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
42 | AP 38 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
43 | AP 39 | OC+6 | 6 | 0 | 0 | 0 | 6 | 1
44 | AP 40 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
45 | AP 41 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
46 | AP 42 | OC+6 | 3 | 3 | 0 | 0 | 6 | 2
47 | AP 43 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
48 | AP43/1 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
49 | AP 44 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
50 | AP 45 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
51 | AP 45/1 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
52 | AP 45/2 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
53 | AP 46 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
54 | AP 47 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
55 | AP 48 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
56 | AP 49 | OC+24 | 0 | 6 | 0 | 0 | 6 | 2
57 | AP 50 | OC+15 | 3 | 3 | 0 | 0 | 6 | 2
58 | AP 51 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
59 | AP 51/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
60 | AP 52 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
61 | AP 53 | OB+3 | 6 | 0 | 0 | 0 | 6 | 1
62 | AP 54 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
63 | AP 54/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
64 | AP 55 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
65 | AP 55/1 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
66 | AP 56 | OC+24 | 6 | 0 | 0 | 0 | 6 | 1
67 | AP 57 | UR+0 | 6 | 0 | 0 | 0 | 6 | 1
68 | AP 57/1 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
69 | AP 57/2 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
70 | AP 57/3 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
71 | AP 57/4 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
72 | AP 58 | OC+3 | 3 | 3 | 0 | 0 | 6 | 1
73 | AP 58/1 | OB+3 | 3 | 3 | 0 | 0 | 6 | 1
74 | AP 58/2 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
75 | AP 59 | PC+0 | 3 | 3 | 0 | 0 | 6 | 1
76 | AP 60 | PC+3 | 0 | 6 | 0 | 0 | 6 | 1
77 | AP 60/1 | PA+3 | 0 | 0 | 0 | 3 | 6 | 1
78 | AP 61 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
79 | AP 62 | DD+0 | 3 | 0 | 0 | 0 | 3 | 9
80 | GANTRY | GANTRY | 3 | 0 | 0 | 0 | 3 | 0
|  |  | 381 | 66 | 6 | 3 | 465 | 110

## CABLE SUPPLY (hidden)
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 132KV S/C line from existing 132/33KV Grid Sub-Station, Barbil to proposed MRSS of AM/NS INDIA LTD at Sagasahi and 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil.
PART-C, SCHEDULE-2A (SUPPLY PART FOR LAYING OF 132 KV UG CABLE 8.276 RKM & OFC cable 9 RKM)
| DESCRIPTION OF ITEMS | UNITS | Total Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | Escalation (UNIT PO PRICE/ COST DATA RATE + 5% ESCALATION PER YEAR) | TOTAL PRICE OF QUANTITY in Rs | Ref
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification)
1 | 2 | 3 | 4 | 5 | 6 | 7=4X6 | 8
1 | Type tested EHV XLPE Power Copper conductor cable as per IEC60840 & IS7098 for the (145 KV class) as per TS
1.1 | Supply of 132 KV, 1 Core, 4 run 630 mm² Copper, XLPE insulation (Extruded semi-conducting screen and extruded or seam welded corrugated Aluminium Sheath type) UG Cable inchuding loop, rise etc.. (Composite tower 1 to Composite tower 2=1.507 KM, Composite tower 3 to Composite Tower 4=6.769 KM), (6.769*4)+(1.507*4)=33.104 Kms extra 2 KM for Spare and termination at Tower and loop in cable joint chamber | Km. | 35 | 6300000 | 6615000 | 231525000 | Rungta Kamanda | 33.104
1.2 | Supply of Outdoor terminating kit Heat shrinkable type suitable for 132 kV class, 1Core, 630 mm², copper UG Cable connection of 300sqmm bonding cable (OET) | No | 12 | 400436.4 | 420458.22 | 5045498.64 | Rungta Kamanda
| Supply of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 16 | 102900 | 108045 | 1728720 | Rungta Kamanda
1.4 | Supply of 6.6 KV,Single core, 300 sqmm XLPE bonding cable | mtr | 8500 | 1995 | 2094.75 | 17805375 | Rungta Kamanda
1.6 | Straight through joint kit for 630 sq. mm UG cable | No. | 66 | 157500 | 165375 | 10914750 | Rungta Kamanda
1.8 | Supply of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 21000 | 22050 | 22050 | Rungta Kamanda
1.9 | Supply of HDPE PLB duct of size 160 mm for laying of 630mm2 UG Cables for NH, road crossing & inside AM/NS premises . (8.276-1.5)*4=27.104 or say 27.5 Kms | Km. | 27.5 | 945000 | 992250 | 27286875 | Rungta Kamanda
2 | Supply of 24 OFC cable,3 | Km. | 9 | 157500 | 165375 | 1488375 | Rungta Kamanda
2.1 | Supply of end Connectors and acessories for OFC connection at GRID subststions | No. | 4 | 15750 | 16537.5 | 66150 | Rungta Kamanda
2.2 | Supply of HDPE PLB duct of size 40 mm for laying of 24 OFC cable .(Composite tower 1 to Composite tower 2=3.550 KM, Composite tower 3 to Kamanda MRSS=6.200 KM), 6.15+3.55=9.70 kms. | Km. | 7 | 64050 | 67252.5 | 470767.5 | Rungta Kamanda
3 | Supply of 120 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No | 12 | 25000 | 38783.2054 | 465398.4648 | Cost data -ss-24
| TOTAL OF SUPPLY PART-E, SCHEDULE 2-A(FOR LINE) ,SUPPLY COMPONENT OF THE WORKS FOR 132KV UG CABLE |  |  |  |  | 296818959.6048
| GST @ 18% on TOTAL OF PART-E |  |  |  |  | 53427412.7289
| TOTAL SUPPLY PART-E, SCHEDULE-2A(LAYING OF 132 KV UG CABLE) including GST |  |  |  |  | 350246372.3337
| Manager (Fin.) |  |  | Deputy General Manager (El)
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## CABLE SERVICE (hidden)
0
NAME OF THE WORK:- Construction of 132KV S/C line from existing 132/33KV Grid Sub-Station, Barbil to proposed MRSS of AM/NS INDIA LTD at Sagasahi and 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil.
PART-C, SCHEDULE-2A (ERECTION PART FOR LAYING OF 132 KV UG CABLE 8.276 RKM & OFC cable 9 RKM)
| DESCRIPTION OF ITEMS | unit | Total Qty | Price per unit in Rs | Total price | Remarks
SL. No. | ERECTION,TESTING & COMMISSIONING INCLUDING CIVIL WORKS OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | [5 empty] | RC Ref
1 | 2 | 3 | 4 | 5 | 6=4X5 | 7
ELECTRICAL WORKS
1 | Erection, Comissioning & Testing of 132 kV, 1 Core,6-Runs, 630 mm² Copper, XLPE insulation UG Cable
1.1 | Laying , Comissioning & Testing of 132 kV, 1 Core,1X4-Runs, 630 mm² Copper, XLPE insulation UG Cable by RCC trench method in trefoil formation inside precast RCC trench. | Km. | 35 | 531300 | 18595500 | Rungta Kamanda price with 5% escalation
1.1 | Erection, Comissioning & Testing of Outdoor terminating kit Heat shrinkablre type uitable for 132 kV class, 1Core, 630 mm², copper UG Cable connection of 300sqmm bonding cable (OET) | Nos. | 12 | 51975 | 623700 | Rungta Kamanda
1.3 | Erection, Comissioning & Testing of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 16 | 3465 | 55440 | Rungta Kamanda
1.4 | Erection, Comissioning & Testing of Single core, 300 sqmm XLPE bonding cable | Mtr | 8500 | 75.075 | 638137.5 | Rungta Kamanda
1.5 | UG Cable straight jointing through jointing kits Pre Mould type suitable for 132 kV, 1 Core, 630 mm², copper UG Cable | No. | 66 | 210000 | 13860000 | Rungta Kamanda
1.6 | Erection of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 21000 | 21000 | Rungta Kamanda
2.2 | Erection of end Connectors and acessories for OFC connection at GRID subststions | No. | 4 | 5250 | 21000 | Rungta Kamanda
3 | Erection, Comissioning & Testing of 120 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No | 12 | 3525.24 | 42302.88 | RC 3121 Dt.03.12.2020 | 10.2.g.i
6 | Erection and supply of Earthing materials 3050 mm ,50mm ID Heavy gauge type pipe with GI clamp fixtures welded all around the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories)with 75mmX10mm GI flat as per approved drawing & specifications. | Nos. | 20 | 6003.56 | 120071.2 | RC 3121 Dt.03.12.2020 | 21.3.i
7 | laying of Earth Flat (75mmX 10mm) for laying of earth mat at cable termination end(composite tower)as per approved drawing & specifications. | Mtr | 800 | 612.61 | 490088 | RC 3121 Dt.03.12.2020 | 21.1.vi.a
| TOTAL ELECTRICAL WORKS |  |  |  | 34467239.58
CIVIL WORKS
2 | Cable joint chamber: for laying of 132 kV cables Width : 2000mm, Depth : 1500mm, Length: 14000mm, 18 location | CUM
2.1 | Earth work excavation of Hard Soil Trench Dimension : (2.2mtr w x 1.5mtr x14 mtr.X18) | Cum | 831.6 | 293.78 | 244307.448 | RC 3121 Dt.03.12.2020 | 2.2.ii
2.2 | Dispose of excavated soil(after back filling)at site. | per Cum/Mtr | 20790 | 1.31 | 27234.9 |  | 2.3
2.3 | Supply & Filling with fine river sand after/before laying of Cable inside the trench | Cum | 207.9 | 796.4 | 165571.56 |  | 5.2
2.4 | PCC for construction of kiln brick cable joint chamber for Width : 2200mm, Depth : 100mm, Length: 14000mm (M-10 grade/1:3:6 ration PCC) | Cum | 41.58 | 5237.8 | 217787.724 |  | 3.2.i
2.5 | Construction of prefabricated RCC partition slab for kiln brick cable joint chamber. Width :2000mm, Depth : 1500mm, Length: 14000mm (M-20 grade/1:1.5:3 ration RCC) | Cum | 50.4 | 7565.71 | 381311.784 |  | 3.4.i
2.6 | Supply and erection of kiln brick masonary with supply of cement for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Cum | 163.8 | 4093.64 | 670538.232 |  | 6.2.i
2.7 | Supply and erection of plastering the brick wall for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Sqm | 1310.4 | 116.39 | 152517.456 |  | 6.5.i
2.8 | Supply and erection of punning the brick wall for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Sqm | 1310.4 | 98.02 | 128445.408 |  | 6.6.i
2.9 | Supply of rod(TATA/RINL/SAIL), bending ,cutting and binding for prefabricated RCC slabs for cable joint chamber. | MT | 5 | 68623.36 | 343116.8 |  | 3.5.1
3 | Laying of HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS.
3.1 | Laying of 160mm Dia. HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS. | Kms. | 27.5 | 2850000 | 78375000
3.2 | Laying of 40mm Dia. HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS. | Kms. | 7.5 | 50000 | 375000
4 | UG cable Trench: RCC Trench fo laying of 132 kV Cables Width: 950 mm, Depth; 1400 mm, Length : 1500 mtr
4.1 | Earth work excavation of Hard Soil Trench Dimension : (1.15 mtr w x 1.4mtr x1500 mtr) | Cum | 2415 | 293.78 | 709478.7
4.2 | Dispose of excavated soil(after back filling)at site. | per Cum/Mtr | 60375 | 1.31 | 79091.25
4.3 | Supply & Filling with fine river sand after/before laying of Cable inside the trench | Cum | 313.5 | 796.4 | 249671.4
4.4 | PCC for Construction of RCC Cable trench (M-10 grade/1:3:6 ratio PCC) | CUM | 142.5 | 5237.8 | 746386.5
4.5 | Construction of RCC cable trench & prefabricated RCC partition slab for Width: 950 mm, Depth: 1400 mm, Length : 1500 Mtr (M-20 grade/1:1.5:3 ratio TCC) | CUM | 615 | 7565.71 | 4652911.65
4.6 | Supply of rod(TATA/RINL/SAIL), bending ,cutting and binding for prefabricated RCC slabs for cable joint chamber. | MT | 40 | 68623.36 | 2744934.4
| Supply and Erection of Route Marker along the Cable routes at an interval of 30 Mtrs as per the drawing with civil works | No | 51 | 1000 | 51000
| TOTAL OF CIVIL WORKS |  |  |  | 90314305.212
| PART-E, SCHEDULE-2C (ERECTION PART FOR LAYING OF 132 KV UG CABLE)=TOTAL ELECTRICAL WORKS+TOTAL CIVIL WORKS |  |  |  | 124781544.792
| GST @ 18% on PART-E SCHEDULE-2C (FOR LAYING OF 132 KV UG CABLE) |  |  |  | 22460678.0626
| PART-E, SCHEDULE-2C (ERECTION & CIVILWORKS PART FOR LAYING OF 132 KV UG CABLE) including GST |  |  |  | 147242222.8546
| Manager (Fin.) |  | Deputy General Manager (El)
| E.H.T (Const.) Division, |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  | OPTCL, Keonjhar

## abstract
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
ABSTRACT
#REF!
Sl. No. | DESCRIPTION | AMOUNT IN INR
1 | PART- A : Construction of proposed 220/132KV GIS at Palaspanga | 1055923461
2 | PART-B : Constructin of 220KV D/C line from proposed Basudevpur GSS to Palaspanga | 365843690.7669
2 | PART-C : 220KV 1CX1000sqmm XLPE Copper cable | 225683097.2355
2 | PART-D : Constructin of 02No. 220KV feeder bay extension at 220/132/33KV Tuurmunga | 145453738
| Total Cost of Project (Sl. No. 1+2) | 1792903987.0024
Or say |  | 1792903987
506169574
9438411256.0312
1799232980
13536717797.0312

## VIIA PALASPANGA SS
ODISHA POWER TRANSMISSION CORPORATION LIMITED
| SCHEDULE-VIIA_ SUPPLY PART FOR 220/132KV GIS S/S AT PALASPANGA | NAME OF THE WORK:- Upgradation of 132/33kV GSS Palaspanga to 220/132/33kV GIS S/s and construction of 220KV D/C line from 400/220KV Basudevpur GSS to proposed 220/132KV GIS at Palaspanga with 02Nos. Of 220kV feeder bay extension at Turumunga GSS
PART -I | DESCRIPTION OF ITEMS (SCHEDULE-VIIA-PALASPANGA SS) | 220/132 kV GIS Substation Palaspanga: 220KV GIS Bay-5 Nos.(FDR-2,AUTO-2,B/C-1) 132KV AIS Bay-4Nos.(AUTO-2, FDR-2)
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNITS | Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | OGST@9% | CGST@9% | Total Unit Price | TOTAL PRICE IN RS, | PRICE REFERENCE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9= (8x4)
ELECTRICAL WORKS
1 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100). [TWO MAIN BUS SYSTEM] The following shall be considered: 1. CT Ratio and sizing shall be done during detailed Engineering. 2. Circuit Breaker shall be purly Spring-Spring mechanism. No Hydraulic component shall be allowed in the Breaker mechanism. 3. The CB shall have 3 level pressure switch for Gas zone tripping before lockout stage.
1.1 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated Transformer feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer (5 core), bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 Bus Duct Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, SF6 Gas, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch etc. to complete Transformer feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 19782364.22 | 1780412.7798 | 1780412.7798 | 23343189.7796 | 46686379.5592 | Ranua estimate | 46686379.5592 |  | 46686379.5592 | 0
1.2 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer (5 core), bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), high speed fault making motorised grounding switch, stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 Bus Duct Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, SF6 Gas, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch etc. to complete Line feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 19782364.22 | 1780412.7798 | 1780412.7798 | 23343189.7796 | 46686379.5592 | Ranua estimate |  |  | 46686379.5592 | 0
1.3 | BUS BAR MODULE WITH VT: 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated /3 ph common, SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), disconnectors, bus bar grounding switch, SF6 gas monitoring system, PD sensors (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers, Absorbent, Limit Switches, SF6 Gas etc. to complete the bus bars with VTs & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 8121755 | 730957.95 | 730957.95 | 9583670.9 | 19167341.8 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 19167341.8 | 0
1.4 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnector switches, disconnector with safety grounding switch(es). Stand alone Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers, Absorbent, Limit Switch, SF6 Gas etc. to complete Bus Coupler bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 1 | 15907377 | 1431663.93 | 1431663.93 | 18770704.86 | 18770704.86 | Ranua estimate |  |  | 18770704.86 | 0
1.5 | Portable Partial Discharge(PD) monitoring system: 245 KV system shall have Portable Partial Discharge(PD) monitoring system & shall be capable for measuring PD in charged GIS environment ,bandwidth in order of 100 MHz–2GHz & provision to select a wide range of intermediate bandwidths and the principle of operation shall be based on UHF principle of detection. The Detection and measurement of PD and bouncing particles having in built large coloured LCD for displaying and storing facility in the instrument for further analysis to locate actual source of PD such as free conducting particles, floating components, voids in spacers, particle on spacer surfaces etc. There shall be minimum six channels for measuring at a time. This includes all accessories. | SET | 1 | 2233492.73 | 201014.3457 | 201014.3457 | 2635521.4214 | 2635521.4214 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 2635521.4214 | 0
1.6 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed] outside GIS Hall alongwith associated Support structure arrangement, bends, joints, accessories & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. (The GI Bus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 1200 | 45894.639 | 4130.5175 | 4130.5175 | 54155.674 | 64986808.824 | Badakushasthali SS 3.6 |  |  | 64986808.824 | 0
1.7 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type (31mm/kV)) and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply with IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with tubular type HDG support structure. - SF6 to air bushing shall be placed as close to the GIS building (for both feeder and TRF bays) as practicable to reduce length of Bus Duct used which shall be as per the approved drawing. | No | 18 | 716720.234 | 64504.8211 | 64504.8211 | 845729.8761 | 15223137.7691 | Gopalpur SS 1.8 |  |  | 15223137.7691 | 0
1: 2; 2: 220 kV AIS Switchyard |  |  |  | 0 | 0
2.1 | 245 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 379430 | 34148.7 | 34148.7 | 447727.4 | 2686364.4 | CD 24-25-SS-54 |  |  | 2686364.4 | 0
1: 2.2; 2: 245KV, 2000A, 50KA, Isolator (AIS) including post insulators (8 KN) as per TS suitable for SCADA operation |  |  |  | 0 | 0
2.2.1 | 245KV Single Isolator with Earth switch (for feeder bay) (AIS) | SET | 2 | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 1831043.6656 | CD 24-25-SS-5 |  |  | 1831043.6656 | 0
2.2.2 | 245KV Single Isolator without Earth switch (for Transformer bay) (AIS) | SET | 2 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 1408165.1776 | CD 24-25-SS-6 |  |  | 1408165.1776 | 0
2.3 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 12 | 21353 | 1921.77 | 1921.77 | 25196.54 | 302358.48 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 302358.48 | 0
2.4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 12 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 1012284.948 | CD 24-25-SS-30 |  |  | 1012284.948 | 0
2.6 | 220KV XLPE cable, 1000 sqmm single core annealed Copper cable with corrugated aluminium sheath as per TS.(for interconnection from LV side of Transformers to AIS equipments) | Mtr | 0 | 18369.8 | 1653.282 | 1653.282 | 21676.364 | 0 | CD 24-25-SS-151 |  |  | 0 | 0
1: 3; 2: 132KV AIS SY Equipments |  |  |  | 0 | 0
3.1 | 120 KV METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No. | 12 | 29179.14 | 2626.1226 | 2626.1226 | 34431.3852 | 413176.6224 | CD 24-25-SS-31 |  |  | 413176.6224 | 0
1: 3.2; 2: 145 KV, 2000A, 40kA ISOLATORS (with 8kN post insulators); 9= (8x4): 0 |  |  |  | 0 | 0
3.2.1 | 132KV Single Isolator without Earth Switch,2000A | SET | 4 | 231941.65 | 20874.7485 | 20874.7485 | 273691.147 | 1094764.588 | CD 24-25-SS-11 |  |  | 1094764.588 | 0
3.2.2 | 132KV Double Isolator without Earth Switch,2000A | SET | 2 | 431137 | 38802.33 | 38802.33 | 508741.66 | 1017483.32 | CD 24-25-SS-13 |  |  | 1017483.32 | 0
3.2.3 | 132KV Double Isolator with Earth Switch,2000A | SET | 2 | 534828.58 | 48134.5722 | 48134.5722 | 631097.7244 | 1262195.4488 | CD 24-25-SS-125 |  |  | 1262195.4488 | 0
3.2.4 | 132KV Single Isolator with double breake SI beam mounted,2000A | SET | 1 | 267414.29 | 24067.2861 | 24067.2861 | 315548.8622 | 315548.8622 | CD 24-25-SS-14 |  |  | 315548.8622 | 0
3.3 | 145 KV Solid core Bus Post Insulators-6kN (AIS) | Nos. | 18 | 9610.2496 | 864.9225 | 864.9225 | 11340.0945 | 204121.701 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1 |  |  | 204121.701 | 0
3.6 | 145 KV, 800-400-200/1-1-1-1A,40 KA, 4 core Single Phase Current Transformer (3 Nos PX CLASS & 1 No. 0.2s CLASS, Vk, Ie as per CT sufficiency calculation ) | Nos | 12 | 232701.42 | 20943.1278 | 20943.1278 | 274587.6756 | 3295052.1072 | CD 24-25-SS-24 |  |  | 3295052.1072 | 0
3.7 | 145KV SF6 Circuit Breakers with supporting structures | Nos | 4 | 571890.4 | 51470.136 | 51470.136 | 674830.672 | 2699322.688 | CD 24-25-SS-3 |  |  | 2699322.688 | 0
3.8 | 145 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 163753.99 | 14737.8591 | 14737.8591 | 193229.7082 | 1159378.2492 | CD 24-25-SS-55 |  |  | 1159378.2492 | 0
1: 4; 2: BUS BAR & CIRCUIT MATERIALS; 9= (8x4): 0 |  |  |  | 0 | 0
4.1 | ACSR MOOSE CONDUCTOR | KM | 1 | 428317.61 | 38548.5849 | 38548.5849 | 505414.7798 | 505414.7798 | CPC PO No.1178 dtd.26.09.25 |  |  | 505414.7798 | 0
4.2 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | MTR | 120 | 1736.43 | 156.2787 | 156.2787 | 2048.9874 | 245878.488 | Neulopoi Estimate |  |  | 245878.488 | 0
4.3 | 120 KN Antifog Porcelain Disc Insulator | NOS. | 1008 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 856444.3776 | CD 24-254-TL-54 |  |  | 856444.3776 | 0
4.4 | 90 KN Antifog Porcelain Disc insulator | NOS. | 341 | 668.53 | 60.1677 | 60.1677 | 788.8654 | 269003.1014 | CD 24-25-TL ACCE.-53 |  |  | 269003.1014 | 0
1: 5; 2: HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT: 220 kV: 1. 220KV Line is with ACSR Zebra. Connections from ACSR Zebra Line to equipment shall be with single ACSR Moose. 2. 220KV Eqpt.-Eqpt. connections shall be with single ACSR moose/4" IPS Al Tube. 3. Single Isolators with ES shall be installed on 220 kV line bays and GIB from GIS shall be terminated at the Isolators through with suitable connectors. 4. Single Isolators without ES shall be installed on 220 kV Transformer bays and GIB from GIS shall be terminated at the Isolators with suitable connectors. 5. GIB from 220KV GIS shall be terminated at the SF6 to Air Bushings. 132 kV: 1.132KV Main Bus shall be with Twin ACSR Moose (300mm spacing) and Reserve bus shall be with single ACSR Moose. 2. Equipment to Equipment connections through single ACSR Moose. The hardware fittings shall be of 160KN & 90KN for 220KV system and 120KN and 90KN for 132KV system. The UTS of the twin hardware fittings shall be suitably chosen for twin insulators of the above mentioned UTS. The hardware fittings shall be single anchored and without turn buckle. The clamps & connectors shall be of compression type. The qty of clamps & connectors shall be as per the approved drawing. |  |  |  | 0 | 0
5.1 | 220KV Single suspension H/W fitting suitable for single ACSR Moose (drop clamp) | NOS. | 6 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 24534.5364 | CD24-25-TL ACCE.-07 |  |  | 24534.5364 | 0
5.2 | 132 KV Single Tension H/W fitting suitable for single ACSR Moose | NOS. | 48 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 159916.2432 | CD24-25-TL ACCE.-9 |  |  | 159916.2432 | 0
5.3 | 132 KV Double Tension H/W fitting suitable for twin ACSR Moose | NOS | 24 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 143212.2576 | CD24-25-TL ACCE.-10 |  |  | 143212.2576 | 0
5.4 | 132 KV Single suspension H/W fitting suitable for single ACSR Moose (drop clamp) | NOS. | 24 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 98138.1456 | CD24-25-TL ACCE.-07 |  |  | 98138.1456 | 0
5.5 | 132 KV Single suspension H/W fitting suitable for twin ACSR Moose (through clamp) | NOS. | 12 | 5275.69 | 474.8121 | 474.8121 | 6225.3142 | 74703.7704 | CD24-25-TL ACCE.-08 |  |  | 74703.7704 | 0
5.6 | Clamps & connectors etc (220KV & 132KV) required to complete the project: as per requirement and as per instruction of Engineer in Charge. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | TENTATIVE |  |  | 590000 | 0
1: 6; 2: DESIGN OF SUBSTATION EARTHING SYSTEMS and DSLP and SUPPLY of materials for the following: (a) The Soil resistivity for the substation area is to be measured and approved by OPTCL. (b) The Earth Mat design and layout is to prepared based on the soil resistivity and approved by OPTCL. (c) Laying of earth-mat conductors of Hot dip galvanized 75 x 10 mm, excavation of earth for laying of earth flat as per approved design & drawing, welding/jointing, application of two coats of Zinc Paint, wrapping of HT Tape etc of ground conductors & etc with back filling and good compaction. The spacing between the earth FLATS not more than 5 Mtrs (both way) and to be buried at depth of 700mm minimum from the finished ground level. (d) At intersections, GI rods shall be welded 75 mm width on both sides. After welding, zinc-rich paint shall be applied at the joints to prevent corrosion. |  |  |  | 0 | 0
2: (e) 50 mm, 3 mtr long Heavy duty perforated GI pipes: for treated earth pits (with details of treatment as per IS). This shall be used of equipment earthing and also along the periphery of the switchyard i.e. near the fencing. (f) Provision of water taps with supply of all materials inside the switch yard areas and peripheral for treated earth pit for watering the treated earth pits. (g) The erection of risers of size 50 x 6 mm / 75 x 10 mm GI flats including welding/jointing, application of two coats of bituminous Paint, wrapping of HT Tape etc as per requirement. This is as per approved drawing and specification. (h) This includes earthing provision for switchyard buildings. (i) DSLP of Switchyard and its buildings as described below. NOTE: Earthing design and philosophy shall be as per IEEE 80, 81, IS 3043, CBIP Manual on Earthing of AC Power Systems and OPTCL TS. Detail earthing design shall be submitted by the agency considering soil restivity survey. |  |  |  | 0 | 0
6.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying in earth mat (spacing maximum 5m both way) | MT | 30 | 82451 | 7420.59 | 7420.59 | 97292.18 | 2918765.4 | Struture weight RC |  |  | 2918765.4 | 0
6.2 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Raiser from the burial earth mat to equipment, structure, building lightning protection etc) | MT | 15 | 82451 | 7420.59 | 7420.59 | 97292.18 | 1459382.7 | Struture weight RC |  |  | 1459382.7 | 0
6.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos | 200 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 538311.28 | CD24-25-TL-08 |  |  | 538311.28 | 0
7 | Design and Supply of Direct Stroke Lightening Protection System: (As per TS, approved drawings and directions of Engineer-in-Charge.) using IEC 62305 / Razevig method / National Building Code. The scope includes design and supply of all materials (excluding switchyard columns and lighting cum lightning mast) for DSLP of entire switchyard area under present scope, all buildings, Auto Transformers etc.. Includes all materials such as Shield wires, Horizontal Conductor & Down conductor, Droppers, Earth electrodes, Test link, Cleats, lugs, Air termination rods/ Lightning spike, PG Clamp, D Shackle. etc. and all other accessories (except specified above at 6.1-6.3) to complete the system in full shape. Earthing of the DSLP system is included in the scope. NOTE: Switchyard columns and lighting cum lightning mast specified under different line item. All other items and accessories required except columns and LCLM are included the scope of supply. | Lot | 1 | 78127.84 | 7031.5056 | 7031.5056 | 92190.8512 | 92190.8512 | Basudevpur Estimate |  |  | 92190.8512 | 0
8 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network to each treated earth pit as per approved drawing. | Lot | 1 | 578812 | 52093.08 | 52093.08 | 682998.16 | 682998.16 | Neulpoi Estimate |  |  | 682998.16 | 0
1: 9; 2: G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS. |  |  |  | 0 | 0
9.1 | G.I Cable Trays(size: 450x75x2500mm) | Mtrs | 2000 | 781.2 | 70.308 | 70.308 | 921.816 | 1843632 | Autonagar Sl no- 14.1 |  |  | 1843632 | 0
9.2 | G.I Cable Trays(size: 300x75x2500mm) | Mtrs | 2500 | 624.75 | 56.2275 | 56.2275 | 737.205 | 1843012.5 | Autonagar Sl no- 14.2 |  |  | 1843012.5 | 0
9.3 | G.I Cable Trays(size: 150x75x2500mm) | Mtrs | 2500 | 469.35 | 42.2415 | 42.2415 | 553.833 | 1384582.5 | Autonagar Sl no- 14.3 |  |  | 1384582.5 | 0
9.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 8 | 82451 | 7420.59 | 7420.59 | 97292.18 | 778337.44 | CPC Purchase for Structure |  |  | 778337.44 | 0
9.5 | 250mm dia PVC Pipe | Mtrs | 200 | 392.47 | 35.3223 | 35.3223 | 463.1146 | 92622.92 |  |  |  | 92622.92 | 0
9.6 | 110mm dia PVCPipe | Mtrs | 250 | 294.35 | 26.4915 | 26.4915 | 347.333 | 86833.25 |  |  |  | 86833.25 | 0
9.7 | 50mm dia PVC Pipe | Mtrs | 700 | 220.77 | 19.8693 | 19.8693 | 260.5086 | 182356.02 |  |  |  | 182356.02 | 0
9.8 | Hard Conduit, PVC pipe bends & other PVC accessories required for 250mm,110mm & 50mm dia as above | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 |  |  |  | 59000 | 0
1: 10; 2: SWITCH YARD STRUCTURES STEEL HDG - LATTICE TYPE FOR TOWER COLUMN, BEAMS & PIPE TYPE FOR ALL EQUIPMENT STRUCTURE ( INCLUDING FOUNDATION BOLTS - ITS NUTS, ITS WASHERS, ITS PLATE ETC ). |  |  |  | 0 | 0
1: 10.1; 2: DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS & DIFFERENT TYPE OF BEAMS WITH DETAILS |  |  |  | 0 | 0
1: 10.1.1; 2: P1S-Columns including earth spikes for 220 KV (NOMINAL UNIT WT- 4.676 MT); 3: Nos; 4: 7 |  |  |  | 0 | 0
1: 10.1.2; 2: Q1-Beams for 220 KV (NOMINAL UNIT WT- 1.598 MT); 3: Nos; 4: 4 |  |  |  | 0 | 0
1: 10.1.3; 2: T1S - 132 KV(NOMINAL UNIT WT- 1.092 MT); 3: NOS; 4: 8 |  |  |  | 0 | 0
1: 10.1.4; 2: T4S - 132KV (NOMINAL UNIT WT- 0.849 MT); 3: NOS; 4: 4 |  |  |  | 0 | 0
1: 10.1.5; 2: DIFFERENT TYPE OF BEAMS WITH DETAILS |  |  |  | 0 | 0
1: 10.1.6; 2: G1 - 132 KV(NOMINAL UNIT WT- 0.576 MT); 3: NOS; 4: 8 |  |  |  | 0 | 0
1: 10.1.8; 2: G2 - 132 KV(NOMINAL UNIT WT- 0.851 MT); 3: NOS; 4: 4 |  |  |  | 0 | 0
10.1.9 | TOTAL WEIGHT OF COLUMN & BEAM INCLUDING FOUNDATION BOLTS, - ITS NUTS, WASHERS PLATE ETC | MT | 59.268 | 82451 | 7420.59 | 7420.59 | 97292.18 | 5766312.9242 | CPC Purchase for Structure |  |  | 5766312.9242 | 0
10.1.10 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 5.93 | 102000 | 9180 | 9180 | 120360 | 713734.8 | CPC Purchase for Structure |  |  | 713734.8 | 0
1: 10.2; 2: DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV & 132KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC ) |  |  |  | 0 | 0
1: 10.2.1; 2: 220 KV Single Isolator with Earth Switch (1.477MT); 3: set; 4: 2 |  |  |  | 0 | 0
1: 10.2.2; 2: 220 KV Single Isolator without Earth Switch (1.4277MT); 3: set; 4: 2 |  |  |  | 0 | 0
1: 10.2.3; 2: 220 KV Surge Arrester (0.41); 3: Nos; 4: 12 |  |  |  | 0 | 0
1: 10.2.4; 2: 220 KV IVT (0.41); 3: Nos; 4: 6 |  |  |  | 0 | 0
1: 10.2.5; 2: 220 KV Post Insulator (1.86); 3: Nos; 4: 12 |  |  |  | 0 | 0
1: 10.2.6; 2: SINGLE ISOLATORS without ES-132KV ( 0.621 MT); 3: SET; 4: 4 |  |  |  | 0 | 0
1: 10.2.7; 2: Double isolator without ES 132 KV (1.105MT); 3: SET; 4: 2 |  |  |  | 0 | 0
1: 10.2.7; 2: Double isolator with ES 132 KV (1.105MT); 3: SET; 4: 2 |  |  |  | 0 | 0
1: 10.2.8; 2: CTS-132 KV (0.207 MT)); 3: SET; 4: 12 |  |  |  | 0 | 0
1: 10.2.9; 2: Surge Arrester-132 kV (0.172MT); 3: SET; 4: 12 |  |  |  | 0 | 0
1: 10.2.10; 2: BPI-132 KV (0.296MT); 3: SET; 4: 18 |  |  |  | 0 | 0
1: 10.2.11; 2: Strutcure for Cable termination (0.296MT); 3: SET; 4: 18 |  |  |  | 0 | 0
10.3 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 57.54 | 82451 | 7420.59 | 7420.59 | 97292.18 | 5598192.0372 | CPC Purchase for Structure |  |  | 5598192.0372 | 0
10.4 | Gl bolts ,Nuts, washers plainn & spring etc for the above structures | MT | 5.75 | 102000 | 9180 | 9180 | 120360 | 692070 | CPC Purchase for Structure |  |  | 692070 | 0
10.5 | GI Foundation bolts & nuts(3nos) with plate & other washers as required | MT | 4 | 102000 | 9180 | 9180 | 120360 | 481440 | CPC Purchase for Structure |  |  | 481440 | 0
11 | 40-metre-high lattice-type (HDG) lighting-cum-lightning mast with landing platforms, including LED lighting fixtures with control gear panels, suitable for Wind Zone-V, complete with all accessories such as the lighting control panel, required armoured copper cables, and other associated items. The number and capacity of lighting fixtures shall be determined based on illumination design to achieve the desired lux level. Suitable landing platforms shall be provided to enable access to the luminaires for repair and maintenance. The design and drawings of the structure shall be vetted by CPRI/IITs. | NOS | 2 | 34728.75 | 3125.5875 | 3125.5875 | 40979.925 | 81959.85 | Neulopoi Estimate |  |  | 81959.85 | 0
1: 12; 2: POWER CABLES, 1.1KV, XLPE insulated PVC sheathed, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.) |  |  |  | 0 | 0
12.1 | 3.5 CX300 mm² XLPE | KM | 1 | 1027095.19 | 92438.5671 | 92438.5671 | 1211972.3242 | 1211972.3242 | CD SS 134 |  |  | 1211972.3242 | 0
12.2 | 3.5 CXI85 mm² XLPE | KM | 1.5 | 488678.88 | 43981.0992 | 43981.0992 | 576641.0784 | 864961.6176 | CD SS 132 |  |  | 864961.6176 | 0
12.3 | 3.5CX120 mm² XLPE | KM | 0.5 | 459114.77 | 41320.3293 | 41320.3293 | 541755.4286 | 270877.7143 | CD SS 131 |  |  | 270877.7143 | 0
12.4 | 3.5 CX70 mm² XLPE | KM | 0.8 | 265690.44 | 23912.1396 | 23912.1396 | 313514.7192 | 250811.7754 | CD SS 129 |  |  | 250811.7754 | 0
12.5 | 3.5 CX35 mm² XLPE | KM | 1.2 | 147505.32 | 13275.4788 | 13275.4788 | 174056.2776 | 208867.5331 | CD SS 127 |  |  | 208867.5331 | 0
12.6 | 4 CX 16 mm² XLPE | KM | 1 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 136626.8074 | CD SS 125 |  |  | 136626.8074 | 0
12.7 | 4 CX 6 mm2 XLPE | KM | 2.5 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 341567.0185 | CD 24-25-SS-125 |  |  | 341567.0185 | 0
12.8 | 2CX 6 mm2 XLPE | KM | 3 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 409880.4222 | CD 24-25-SS-125 |  |  | 409880.4222 | 0
1: 13; 2: CONTROL CABLES, 1.1 KV, XLPE insulated PVC sheathed, ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule) |  |  |  | 0 | 0
13.1 | 4 CX 2.5 mm2 XLPE | KM | 5 | 123673.44 | 11130.6096 | 11130.6096 | 145934.6592 | 729673.296 | CD SS 109 |  |  | 729673.296 | 0
13.2 | 5 CX 2.5 mm2XLPE | Mtrs | 6 | 184820 | 16633.8 | 16633.8 | 218087.6 | 1308525.6 | BADAKUSTHASTHALI 16.2.2 |  |  | 1308525.6 | 0
13.3 | 7CX 2.5 mm²XLPE | KM | 6 | 187201.82 | 16848.1638 | 16848.1638 | 220898.1476 | 1325388.8856 | CD SS 110 |  |  | 1325388.8856 | 0
13.4 | 10 CX 2.5 mm2 XLPE | KM | 6 | 254413.65 | 22897.2285 | 22897.2285 | 300208.107 | 1801248.642 | CD SS 111 |  |  | 1801248.642 | 0
13.5 | 12 CX 2.5 mm2XLPE | MTR | 6 | 289730 | 26075.7 | 26075.7 | 341881.4 | 2051288.4 | BADAKUSTHASTHALI 16.2.5 |  |  | 2051288.4 | 0
13.6 | 16 CX 2.5 mm2XLPE | KM | 3 | 387033.75 | 34833.0375 | 34833.0375 | 456699.825 | 1370099.475 | CD SS 112 |  |  | 1370099.475 | 0
13.7 | 19 CX 2.5 mm2XLPE | KM | 2.5 | 448832.3 | 40394.907 | 40394.907 | 529622.114 | 1324055.285 | CD SS 113 |  |  | 1324055.285 | 0
13.8 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTR | 300 | 448.8 | 40.392 | 40.392 | 529.584 | 158875.2 | CD 24-25-SS-113 |  |  | 158875.2 | 0
1: 13.9; 2: Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI |  |  |  | 0 | 0
13.9.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 | 296 | 26.64 | 26.64 | 349.28 | 523920 | Neulopoi Estimate |  |  | 523920 | 0
13.9.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 200 | 59.322 | 5.339 | 5.339 | 70 | 14000 | Neulopoi Estimate |  |  | 14000 | 0
1: 14; 2: SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(includes switchyard, colony street and other street area) The qty of Switchyard lights and Street lights shll be as per the approved lighting design calculation. |  |  |  | 0 | 0
14.1 | SUB-STATION SWITCH YARD LIGHTING : IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear, GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each). (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE CABLE ITEMS AS INDICATED ABOVE ) | NOS | 50 | 13891.5 | 1250.235 | 1250.235 | 16391.97 | 819598.5 | Neulpoi Estimate |  |  | 819598.5 | 0
14.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. | NOS | 40 | 34728.75 | 3125.5875 | 3125.5875 | 40979.925 | 1639197 | Neulpoi Estimate |  |  | 1639197 | 0
1: 15; 2: Design and Supply of Air Conditioning System: (As per TS, approved drawings and directions of Engineer-in-Charge.) |  |  |  | 0 | 0
2: Supply of 2 Ton Split type Air Conditioners [both indoor and outdoor units] (Inverter, five star latest model - LG/Hitachi /Carrier/Mitsubishi Heavy Industries/Daikin/Voltas/O' General Make) with copper condensor having remote control. Scope includes all other additional accessories such as Automatic Voltage Stabilizers, copper piping, copper cable, insulation over copper pipe, PVC corrrugated drain pipes, steel brackets for holding outdoor units, first filling of refrigerant and all other accessories necessary for completion of the AC system. |  |  |  | 0 | 0
2: Air conditioning system shall be designed to maintain the inside Dry Bulb Temperature below 24 °C. Bidder shall submit necessary design calculations for OPTCL's approval. The qty of ACs shall be as per the approved design. Compressor of AC shall have minimum 5 years Warranty from the date of commissioning. Following item description also includes AC Control Panel(s) made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 16 amp industrial socket & plug for each unit of AC etc (As per specification) for the following buildings. Number of such panels shall be as per reqirement and approved drawings. |  |  |  | 0 | 0
2: Additional requirement for GIS hall relay panel room, VRLA Battery room, CRB - Panel/HMI room, CRB - LT AC/DC room, Switchyard Kisok etc (as applicable): At least 50% spare/Stand by Air-Conditioning capacity shall be provided. Supply of Logic controller for Auto Switch ON & OFF of AC units as follows: • Standby units shall come in to operation automatically when the running main unit fails • Main and standby units shall be changed over periodically • Following alarms shall be provided: a. Compressor On/OFF condition of each unit b. Compressor failure of each unit c. Power OFF to AC unit d. High temperature in room |  |  |  | 0 | 0
2: Temperature transducer shall be provided to monitor the temperature. The Temperature transducer shall have the following specification: (Sensor : Air temperature sensor (indoor use), Output : 4 to 20mA, Temperature range : -5°C to 60°C, Resolution : 0.1°C, Accuracy : 0.5°C or better.) |  |  |  | 0 | 0
15.1 | Air conditioning System for Control Room Building (Extension of CR building)- VRLA Battery room, HMI Room, Communication Room, ets. Includes supply of AC Control Panel with one nos controller for each AC. | Nos | 16 | 67305.4751 | 6057.4928 | 6057.4928 | 79420.4606 | 1270727.3704 | Neulopoi Estimate |  |  | 1270727.3704 | 0
15.2 | Air conditioning System for 220 kV GIS Building - Relay panel room. Includes supply of AC Control Panel with one nos of controller for each AC. | Nos | 15 | 67305.4751 | 6057.4928 | 6057.4928 | 79420.4606 | 1191306.9097 | Neulopoi Estimate |  |  | 1191306.9097 | 0
1: 16; 2: 220 KV GIS hall -Design and Supply of GIS Hall Ventilation System: (As per TS, approved drawings and directions of Engineer-in-Charge.) Each Ventilation system shall consist of two 100% capacity systems, one set operating and one set stand-by. Fresh outdoor air shall be filtered before being blown into the GIS hall by the air fans to avoid dust accumulation on components present in the GIS hall. To ensure that the air being supplied to the GIS hall is free from dust particles, a minimum two stage dust filtration process shall be supplied, with pre filters and fine filters. The ventilation system shall reduce dust particles of 5 microns in size with at least 99% efficiency. This includes supply of AHU , pre filters, fine filters, motorized exhaust dampers with local control, all types of ducting, arrangement to install ducts on walls, louvers, grills, all types of dampers, insulations, control panels, cabling, all types of civil work etc.and all other materials and accessories to complete the work. The compartments shall have ventilation openings with fine wire mesh of brass to prevent the entry of insects and to reduce to a minimum the entry of dirt and dust. The ventilation of the GIS hall shall be positive pressure type with minimum 2 air change cycles per hour or as per recommendation of GIS manufacturer, whichever is higher. The pressure inside the GIS hall shall be maintained 5 mm of water above the atmospheric pressure. Silencers are to be used to keep the noise level below 60 dB. Agency will submit design document to justify capacity and numbers of AHUs and other equipment to be installed. The GIS hall needs to be in positive pressure before starting Installation. |  |  |  | 0 | 0
16.1 | Ventilation System for 220KV GIS Hall as per technical specification. | LOT | 1 | 474451.29 | 42700.6161 | 42700.6161 | 559852.5222 | 559852.5222 | BADAKUSHASTHALI 52.2 |  |  | 559852.5222 | 0
17 | GIS Hall exhaust system: Exhaust fans for installation at 1 feet above the GIS hall floor level for exhaust of SF6 gas. Sufficient numbers of exhaust fans of required capacity to be provided for 1 air change per hour, accordingly calculation to be submitted. The exhaust outlet shall be directed downwards at the outer side of the GIS hall and shall be fixed with aluminum mesh at outlet. The exhaust fans shall have louvers for automatic closing when not in use. Control of the system shall be from the SAS-HMI room. Includes supply of panels and other associated materials. | LOT | 1 | 75000 | 6750 | 6750 | 88500 | 88500 | TENTATIVE |  |  | 88500 | 0
1: 18; 2: FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC (REFER TS-VOUIIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE -1) |  |  |  | 0 | 0
18.1 | FOAM TYPE-9 LTRS | NOS | 20 | 7443.53 | 669.9177 | 669.9177 | 8783.3654 | 175667.308 | Neulopoi Estimate |  |  | 175667.308 | 0
18.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 4 | 57572.16 | 5181.4944 | 5181.4944 | 67935.1488 | 271740.5952 | Neulopoi Estimate |  |  | 271740.5952 | 0
18.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 11599.4 | 1043.946 | 1043.946 | 13687.292 | 82123.752 | Neulopoi Estimate |  |  | 82123.752 | 0
18.4 | CO2 - 4.5 KGS | NOS | 15 | 24761.6 | 2228.544 | 2228.544 | 29218.688 | 438280.32 | Neulopoi Estimate |  |  | 438280.32 | 0
18.5 | CO2 - 9 KGS | NOS | 10 | 36604.1 | 3294.369 | 3294.369 | 43192.838 | 431928.38 | Neulopoi Estimate |  |  | 431928.38 | 0
18.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 43111.11 | 3879.9999 | 3879.9999 | 50871.1098 | 203484.4392 | Neulopoi Estimate |  |  | 203484.4392 | 0
18.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & CANOPY (3 mm thick) | SET | 6 | 6268.54 | 564.1686 | 564.1686 | 7396.8772 | 44381.2632 | Neulopoi Estimate |  |  | 44381.2632 | 0
18.8 | 9 litre water type | Nos. | 6 | 1991 | 179.19 | 179.19 | 2349.38 | 14096.28 | Ranua estimate |  |  | 14096.28 | 0
18.9 | 4.5 kg DCP type | Nos. | 6 | 2680.19 | 241.2171 | 241.2171 | 3162.6242 | 18975.7452 | Ranua estimate |  |  | 18975.7452 | 0
18.1 | 50 Litres Mechanical Foam type | Nos. | 2 | 9572.11 | 861.4899 | 861.4899 | 11295.0898 | 22590.1796 | Ranua estimate |  |  | 22590.1796 | 0
1: 19; 2: Design and Supply of Addressable type Smoke & Heat detection system: (As per TS, approved drawings and directions of Engineer-in-Charge.) Addressable type Smoke, Heat detector, Beam Detector, Reflector for Beam Detector for the following buildings including all accessories, the Addressable type Main control panel (Microprocessor based 10 loop fire alarm control panel) expandable upto 16 loops (minimum) fully networkable with each loop capable of taking 99 devices, alpha- numeric liquid crystal display. The panel shall be soft addressable type. The panel shall be able to give pinpoint location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have inbuilt rectifier, Loop cards, provision for externel & internal printer, LCD unit to indicate Fire/Fault Signal with address and analog output, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with SAS system, wall mounting loop powered addressable type hooter with all accessories, addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module, MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection, Junction boxes, response indicator, EOL resistance etc. Beam detector and reflectors shall be used only in the GIS halls. Agency shall submit drawings and design. Quantity of various items such as detector, RI, hooter, MCP etc. as per approved design. |  |  |  | 0 | 0
19.1 | 220 kV GIS Building | LOT | 1 | 295715.93 | 26614.4337 | 26614.4337 | 348944.7974 | 348944.7974 | BADAKUSHATHALI 58 |  |  | 348944.7974 | 0
19.3 | Control room Building (Extension of CR building) | LOT | 1 | 295715.93 | 26614.4337 | 26614.4337 | 348944.7974 | 348944.7974 |  |  |  | 348944.7974 | 0
1: 20; 2: SUBSTATION AUTOMATION SYSTEM FOR 220/33 KV SUBSTATION ON PRP MODE: Design, engineering, drawing, supervision, installation, testing & commissioning of Substation Automation system (IEC 61850) for (Complete 220 kV and 132 kV system) along with Supply of the following 220 and 132 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type. |  |  |  | 0 | 0
20.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification) system (for 220 & 132 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Double jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 | 2032114.47 | 182890.3023 | 182890.3023 | 2397895.0746 | 2397895.0746 | Neulopoi Estimate |  |  | 2397895.0746 | 0
20.2 | RCC Communication Panel; comprising of: 1. Substation Ethernet Switches (Layer-3 type)- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Doublle jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | SET | 1 | 611935 | 55074.15 | 55074.15 | 722083.3 | 722083.3 | LoA No.221,Dt.01.02.25 (Neulpoi) |  |  | 722083.3 | 0
20.3 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | SET | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000 | Tentative |  |  | 1180000 | 0
1: 20.4; 2: Operator Workstations- 02 Nos |  |  |  | 0 | 0
1: 20.5; 2: Engineering workstation |  |  |  | 0 | 0
1: 20.6; 2: Workstation for RAS (Remote Access System) |  |  |  | 0 | 0
1: 20.7; 2: Black & whiter Laser jet Printer-1Nos |  |  |  | 0 | 0
1: 20.8; 2: Inverters - 3 KVA (Main & Stand by) |  |  |  | 0 | 0
1: 20.9; 2: Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. |  |  |  | 0 | 0
1: 20.12; 2: 220 KV SIDE PROTECTION PANEL - Single Panel (1 Bay in One Panel) with IEC 61850-ED-2 PRP on FO |  |  |  | 0 | 0
20.13 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | CD SS 37 |  |  | 6833575.0304 | 0
20.14 | 220KV, 160MVA Auto Transformer Protection Panel: Differential (Main-I & Mai-II of separate make), saparate numerical REF, Backup Protection and other aux relays including LBB trip relays & Bay control units (BCU) as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 3576298.55 | 321866.8695 | 321866.8695 | 4220032.289 | 8440064.578 | CD SS 38 |  |  | 8440064.578 | 0
20.15 | 220KV Bus Coupler Protection Panel: Backup Protection Relays and other aux relays including LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 1 | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 1438647.3742 | CD SS 39 |  |  | 1438647.3742 | 0
20.16 | 220 KV BUS-BAR PROTECTION PANEL(s) (Centralized Architecture): Complete bus bar protection system for proposed bays and Provision for bus bar protection for future bays (at least four nos) and with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 1 | 3809977.15 | 342897.9435 | 342897.9435 | 4495773.037 | 4495773.037 | CD SS 40 |  |  | 4495773.037 | 0
20.17 | 132KV Transformer Protection: 2 nos BCU, separate numeric backup relay, separate numeric REF relay and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 3047951.72 | 274315.6548 | 274315.6548 | 3596583.0296 | 7193166.0592 | CD SS 43 |  |  | 7193166.0592 | 0
20.17 | 132KV Feeder Protection: 2 nos BCU, separate numeric backup relay, separate numeric REF relay and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 2438385.38 | 219454.6842 | 219454.6842 | 2877294.7484 | 5754589.4968 | CD SS 42 |  |  | 5754589.4968 | 0
1: 21; 2: AC & DC SYSTEM |  |  |  | 0 | 0
1: 21.1; 2: AC SYSTEM : Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS: |  |  |  | 0 | 0
21.1.1 | MAIN AC DB (Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type ACB with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection). The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 1265537.64 | 113898.3876 | 113898.3876 | 1493334.4152 | 1493334.4152 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 1493334.4152 | 0
21.1.2 | ACDB (Indoor Type) WITH BUS 1, BUS 2, BUS 3, Bus Coupler 1 & Bus Coupler 2: HAVING 400A Motorized MCCB for automatic operation in Incomers and Bus couplers with electrical interlock system. With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected with two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 892752.3 | 80347.707 | 80347.707 | 1053447.714 | 1053447.714 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 1053447.714 | 0
21.1.3 | Main Lighting Distribution Board (having 250A MCCB as Incomer) as per TS (witc DB-1,DB-2 & B/C) with mechanical Interlock through castle lock. | SET | 1 | 221618.31 | 19945.6479 | 19945.6479 | 261509.6058 | 261509.6058 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 261509.6058 | 0
21.1.4 | Indoor Lighting Distribution Board as per TS. (WITH DB-1,DB-2 & B/C) | SET | 1 | 28071.65 | 2526.4485 | 2526.4485 | 33124.547 | 33124.547 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 33124.547 | 0
21.1.5 | Emergency Lighting Distribution Board as per specification. | SET | 1 | 24378.02 | 2194.0218 | 2194.0218 | 28766.0636 | 28766.0636 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 28766.0636 | 0
21.1.6 | Indoor Receptacle Board as per Specification | SET | 2 | 8864.73 | 797.8257 | 797.8257 | 10460.3814 | 20920.7628 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 20920.7628 | 0
21.1.7 | Outdoor Kiosk For Station Transformer: as per TS with 3 NOS. OF Cut-Outs (1000 Amps) at the Incoming side, 1No. of 3 phase SFU (1000 Amps) at the Outgoing and suitable Busbar arrangement for termination of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 73216.5 | 6589.485 | 6589.485 | 86395.47 | 172790.94 | Neulopoi Estimate |  |  | 172790.94 | 0
21.1.8 | Outdoor Kiosk for Switchyard Lights: as per TS having timer control for switching the lights ON & OFF. | SET | 6 | 51553.26 | 4639.7934 | 4639.7934 | 60832.8468 | 364997.0808 | Neulopoi Estimate |  |  | 364997.0808 | 0
21.1.10 | Outdoor Kiosk for Street Lights: as per TS having timer control for switching the lights ON & OFF. | NOS | 4 | 51553.26 | 4639.7934 | 4639.7934 | 60832.8468 | 243331.3872 | Neulopoi Estimate |  |  | 243331.3872 | 0
21.1.11 | Outdoor Receptacle Board: (Transformer filtration purpose): as per TS | NOS | 2 | 51553.26 | 4639.7934 | 4639.7934 | 60832.8468 | 121665.6936 | Neulopoi Estimate |  |  | 121665.6936 | 0
21.1.12 | Outdoor Receptacle Board: (Welding & other uses) : as per TS | NOS | 4 | 51553.26 | 4639.7934 | 4639.7934 | 60832.8468 | 243331.3872 | Neulopoi Estimate |  |  | 243331.3872 | 0
21.1.13 | Bay Marshalling Kiosk (Outdoor type): as per TS, (2 nos on 220 kV bay & 4 Nos for 132KV bays ) | Nos | 6 | 21058.65 | 1895.2785 | 1895.2785 | 24849.207 | 149095.242 |  |  |  | 149095.242 | 0
21.1.14 | CT Out Door Console Boxes: As per TS (Outdoor type) | Nos | 4 | 64455 | 5800.95 | 5800.95 | 76056.9 | 304227.6 | Neulopoi Estimate |  |  | 304227.6 | 0
21.1.15 | PT Outdoor Console Boxes: as per TS | Nos | 4 | 64455 | 5800.95 | 5800.95 | 76056.9 | 304227.6 | Neulopoi Estimate |  |  | 304227.6 | 0
1: 22.3; 2: DC SYSTEM |  |  |  | 0 | 0
22.3.1 | 220 V MAIN DCDB in Control Room Building (HAVING DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE protection (with BUS-1, BUS-2 & B/C). Consider separate source(DC1 & DC 2) to each DCDB of Bay Kiosks, local supply of CRB such as emergency lighting, SAS system etc. & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered ( with 20% spare). Incoming and outgoing ratings of MCBs shall be decided as per panel load during detail engineering. The construction shall be as per the TS. | SET | 1 | 375905.74 | 33831.5166 | 33831.5166 | 443568.7732 | 443568.7732 | CD 24-25-SS-79 |  |  | 443568.7732 | 0
22.3.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 1 | 429612.38 | 38665.1142 | 38665.1142 | 506942.6084 | 506942.6084 | Neulopoi Estimate |  |  | 506942.6084 | 0
22.3.3 | Stationary PLANTE TYPE Battery, 350 Ah (C10 rate) for 220 V DC (Cells: 107 Nos, 2V Nominal/Cell) as per TS and IS 15549 & IEC 60896-21/22. (The battery shall be capable of giving 1200 or more charge/discharge cycles at 80% DOD at an average temperature of 27º Celsius. The battery sets shall have a minimum expected life of 20 years at float operation.) Agency shall furnish battery sizing calculation, selection of number of cells, float and Boost voltages as per IEEE- 485. Duty cycle for sizing calculation shall be 3h for continious load, 1 hour for emergency load and 1 min for momentary load. | SET | 1 | 2043381.24 | 183904.3116 | 183904.3116 | 2411189.8632 | 2411189.8632 | CD 24-25-SS-71 |  |  | 2411189.8632 | 0
22.3.4 | FLOAT CUM BOOST Battery Charger for offered 350 Ah VRLA Type Battery (107 cells): Float Charging: 2.13-2.27 V per cell, Boost Charging: 2.28-2.32 V per cell. (FC 35A/ BC 70A) Input from AC Source I & II without automatic selection. Filter circuit shall be provided to limit the ripple content (Peak to Peak) in the output voltage to 1%, irrespective of the DC load level. a. The battery charger shall support both automatic and manual control of output voltage and current, selectable via a mode selector switch. In automatic mode during float charging, the output voltage shall remain within ±1% of the set value under AC input voltage variation of ±10%, frequency variation of ±5%, combined variation of ±10%, and DC load variation from no load to full load. b. Battery chargers shall operate on constant voltage characteristics across the full load range (zero to full load) at float voltage, ensuring the battery remains fully charged without harmful overcharge. c. Load limiters with drooping characteristics shall be provided, which: * Gradually reduce output voltage when the DC load current exceeds the preset limit (in automatic voltage control mode). * Prevent damage or fuse failure during sustained overloads or short circuits in the DC system. * Ensure the charger does not trip under overload or external short circuit conditions. | SET | 1 | 400396.18 | 36035.6562 | 36035.6562 | 472467.4924 | 472467.4924 | CD 24-25-SS-72 |  |  | 472467.4924 | 0
23 | Maintenance Testing Equipment (All equipment shall comply to the TS and as per list below) | Lot | 1 | 2452380 | 220714.2 | 220714.2 | 2893808.4 | 2893808.4 | LOA NO.530,DT.25.04.2025 (RANUA GIS) |  |  | 2893808.4 | 0
1: 23.1; 2: 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 23.2; 2: 10KV Insulation Tester with 15m test lids (Megger- S1-1068 / Sonel-MIC 10K1); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 23.3; 2: Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 23.4; 2: Digital Multimeter (Megger / Fluke); 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 23.5; 2: Digital Clamp meter (Megger/Fluke/Motwane); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 23.6; 2: Leakage current clamp meterAC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu); 3: Set; 4: 1 |  |  |  | 0 | 0
1: 23.7; 2: SF6 Gas Leakage Detector (Wika/DILO); 3: Pairs; 4: 1 |  |  |  | 0 | 0
1: 23.8; 2: Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin/Scope); 3: Nos; 4: 6 |  |  |  | 0 | 0
1: 23.9; 2: Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico); 3: Set; 4: 2 |  |  |  | 0 | 0
1: 23.1; 2: Electrical Rubber Hand Gloves; 3: Pairs; 4: 6 |  |  |  | 0 | 0
1: 23.11; 2: Portable High Beam Light (rechargeable); 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 23.12; 2: Desktop Computer: (HP/Lenovo/Dell) (i) Processor-Intel Core i7 11th Gen or better (ii) RAM- 8GB DDR4 or More (iii) ROM- 512GB SSD (iv) Monitor- 21.5" FHD (1920 x 1080) or higher (v) Graphics- Onboard/Integrated (vi) OS- Genuine Windows 11 Pro (vii) Webcam- 720P Logitech (viii) Speaker- 2 nos Stereo type (ix) UPS 600VA (APC/V Guard); 3: Set; 4: 2 |  |  |  | 0 | 0
1: 23.14; 2: Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson); 3: Nos; 4: 1 |  |  |  | 0 | 0
24 | Supply of Office Furniture: Godrej make (As per details below). | Lot | 1 | 578812.5 | 52093.125 | 52093.125 | 682998.75 | 682998.75 | Neulopoi Estimate |  |  | 682998.75 | 0
1: 24.1; 2: For Control Room, conference room, office rooms, Library, testing room etc |  |  |  | 0 | 0
1: 24.1.1; 2: 5ftX3ft executive table with drawer on both sides; 3: Nos; 4: 4 |  |  |  | 0 | 0
1: 24.1.2; 2: 4.5ft X 2.5ft Table with one side drawer; 3: Nos; 4: 7 |  |  |  | 0 | 0
1: 24.1.3; 2: Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use.; 3: Set; 4: 1 |  |  |  | 0 | 0
1: 24.1.4; 2: Executive revolving, adjustable (height) chairs with arm; 3: Nos; 4: 4 |  |  |  | 0 | 0
1: 24.1.5; 2: Cushion fixed “S” type steel chairs with arm; 3: Nos; 4: 16 |  |  |  | 0 | 0
1: 24.1.6; 2: 6ftX3ft conference table; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 24.1.7; 2: Cushion arm steel chairs for conference table purpose.; 3: Nos; 4: 6 |  |  |  | 0 | 0
1: 24.1.8; 2: 6ft height steel almirah (only with selves) for keeping records and other valuable items.; 3: Nos; 4: 3 |  |  |  | 0 | 0
1: 24.1.9; 2: 6ft height steel almirah with glass doors for library purpose; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 24.1.10; 2: 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement.; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 24.1.11; 2: 4ft steel rack (minimum three selves) for keeping the files and other items.; 3: Nos; 4: 8 |  |  |  | 0 | 0
1: 24.2; 2: For Communication Room |  |  |  | 0 | 0
1: 24.2.1; 2: 5ftX3ft executive table with drawer both sides; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 24.2.2; 2: Executive revolving, adjustable (height) chairs with arm; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 24.2.3; 2: Cushion fixed “S” type steel chairs with arm; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 24.2.4; 2: 6ft height steel almirah (only with selves) for keeping records and other valuable items.; 3: Nos; 4: 1 |  |  |  | 0 | 0
25 | Other Tools And Plants (T&P'S) Requirement (As Per details below). The T & P materials shall be of Taparia/Bosch/Stanley make. | Lot | 1 | 370440 | 33339.6 | 33339.6 | 437119.2 | 437119.2 | Neulopoi Estimate |  |  | 437119.2 | 0
1: 25.1; 2: D Spanner Set (6mm – 42mm); 3: Set; 4: 1 |  |  |  | 0 | 0
1: 25.2; 2: Ring Spanner Set (6mm – 42mm); 3: Set; 4: 1 |  |  |  | 0 | 0
1: 25.3; 2: Box spanner set; 3: Set; 4: 1 |  |  |  | 0 | 0
1: 25.4; 2: Pipe Wrench 24 "; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.5; 2: Pipe Wrench 18 "; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.6; 2: Adjustable spanner -12”(slide wrench); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.7; 2: Adjustable spanner -18”(slide wrench); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.8; 2: Insulated cutting plier (standard size); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.9; 2: Nose Plier (standard size); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.1; 2: Screw Driver set |  |  |  | 0 | 0
1: a; 2: 12” Plain head; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: b; 2: 12” star head; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: c; 2: 8” Plain head; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: d; 2: 6” plain head; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: e; 2: 6” star head; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 25.11; 2: Set of screw driver cum line tester; 3: Set; 4: 1 |  |  |  | 0 | 0
1: 25.12; 2: Allen Key set; 3: Set; 4: 1 |  |  |  | 0 | 0
1: 25.13; 2: Files |  |  |  | 0 | 0
1: a; 2: Flat File-12”; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: b; 2: Flat file-6”; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: c; 2: Round file- 12”; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: d; 2: Round file- 6”; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.14; 2: Hammer with Handle |  |  |  | 0 | 0
1: a; 2: 1 lb; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: b; 2: 2 lb; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: c; 2: ½ lb; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 25.15; 2: Steel Tape (Any reputed make) |  |  |  | 0 | 0
1: a; 2: 5Mtr; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: b; 2: 30Mtr; 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.16; 2: Crow bar (Any reputed make) |  |  |  | 0 | 0
1: a; 2: 5ft; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: b; 2: 3ft; 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 25.17; 2: Oil Cane (Any reputed make); 3: Nos; 4: 2 |  |  |  | 0 | 0
1: 25.18; 2: Hand Drill Machine (impact drill) with key (Make-Bosch/Black & Decker); 3: Nos; 4: 1 |  |  |  | 0 | 0
1: 25.19; 2: Vacuum Cleaner (at least 15L) (Make-Eureka Forbes / Black & Decker / Phillips / Karcher); 3: No; 4: 1 |  |  |  | 0 | 0
26 | Self supproted cum extendable Ladder-25ft (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 | 69457.5 | 6251.175 | 6251.175 | 81959.85 | 81959.85 | Neulopoi Estimate |  |  | 81959.85 | 0
27 | Self supproted platform Ladder- 12feet (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 | 52093.13 | 4688.3817 | 4688.3817 | 61469.8934 | 61469.8934 | Neulopoi Estimate |  |  | 61469.8934 | 0
28 | 20 Ltr (at least) Storage Water Cooler (Voltas/Bluestar only) | Nos | 1 | 347287.5 | 31255.875 | 31255.875 | 409799.25 | 409799.25 | Neulopoi Estimate |  |  | 409799.25 | 0
29 | Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | Nos | 1 | 17364.38 | 1562.7942 | 1562.7942 | 20489.9684 | 20489.9684 | Neulopoi Estimate |  |  | 20489.9684 | 0
1: 30; 2: ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0
30.1 | 24 fibre optic approach cable including HDPE pipes | KM | 1 | 93762.74 | 8438.6466 | 8438.6466 | 110640.0332 | 110640.0332 | CD24-25-TEL-34 |  |  | 110640.0332 | 0
30.2 | Installation hardware set (HDPE duct, HDPE coupling etc) for 24Fibre FOAC | KM | 1 | 159579.27 | 14362.1343 | 14362.1343 | 188303.5386 | 188303.5386 | CD24-25-TEL-31 |  |  | 188303.5386 | 0
30.3 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at Other end 400KV and 220 kV S/s | SET | 14 | 119714.04 | 10774.2636 | 10774.2636 | 141262.5672 | 1977675.9408 | Neulopoi Estimate |  |  | 1977675.9408 | 0
30.4 | 48V , 500Ah, maintenance free VRLA battery set | NO | 2 | 119332.12 | 10739.8908 | 10739.8908 | 140811.9016 | 281623.8032 | CD 24-25-TEL-02 |  |  | 281623.8032 | 0
30.5 | SMPS based battery charger of 125A suitable for 48V, 500Ah VRLA battery | NO | 2 | 177821.28 | 16003.9152 | 16003.9152 | 209829.1104 | 419658.2208 | CD 24-25-TEL-08 |  |  | 419658.2208 | 0
30.6 | 48 V DC board (having 100A DC MCCB as incomer, E/F (earth leakage), under & over voltage as per specification (DC DB-1,DC DB-2 & B/C). | SET | 1 | 137402 | 12366.18 | 12366.18 | 162134.36 | 162134.36 | Neulopoi Estimate |  |  | 162134.36 | 0
30.7 | Optical Line Terminal Equipent(OLTE), STM16 type (5 MSP) SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module support upto 150kms ( 02 Nos.) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 25792.45 | 2321.3205 | 2321.3205 | 30435.091 | 30435.091 | Neulopoi Estimate |  |  | 30435.091 | 0
30.8 | Supply of FODP(Fibre Optic Distribution panel) 24F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 67421.04 | 6067.8936 | 6067.8936 | 79556.8272 | 159113.6544 | CD 24-25-TEL-30 |  |  | 159113.6544 | 0
30.9 | Voice gateway 2x(FXS) | Nos | 1 | 53000 | 4770 | 4770 | 62540 | 62540 | Autonagar Sl no- 20.4 |  |  | 62540 | 0
30.1 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | LOT | 1 | 231525 | 20837.25 | 20837.25 | 273199.5 | 273199.5 | Neulopoi Estimate |  |  | 273199.5 | 0
31 | Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. Description of system as below: | Lot | 1 | 1157625 | 104186.25 | 104186.25 | 1365997.5 | 1365997.5 | Neulopoi Estimate |  |  | 1365997.5 | 0
2: Design and Supply for IP Based VMS (Server Based with VMS software), which shall include ONVIF Compliant Colour Cameras with Night Vision(Bullet/Done/PTZ), PTZ Controller, Server (Rack mounted/Tower type) Based NVR with VMS Software, NAS Storage, Mounting arrangement for cameras, cables (Armoured/Un armoured FO/Ethernet/AC/DC/HDMI etc.), HDPE Pipes, Ethernet Switches, UPS, Battery, LIU,POE Injectors, Media Converters, Surge Protection Device (SPD), Ethernet Surge Protectors (ESP), Outdoor/Indoor Junction Boxes/Panels, Main display unit (32 inch Full HD), Keyboard, Mouse, Routers, Networking Rack etc. including any other hardware or software to complete the system as per TS. |  |  |  | 0 | 0
2: An additional display unit (32 inch Full HD) shall also be provided in the security shed for monitoring purpose as per TS. |  |  |  | 0 | 0
2: Any other materials (Hardware & Software) required at the substation for connection of VMS system with remote control center of OPTCL including configuration of the same are also included in the scope of supply. (Configuration at Remote Control Center not the scope of the Contractor.) |  |  |  | 0 | 0
2: Network Topology: Ring |  |  |  | 0 | 0
2: No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations so as to avoid blind spots. |  |  |  | 0 | 0
2: The following areas are to be covered without any blind spots: |  |  |  | 0 | 0
2: 1. Entry and exits of Store and Equipment storage Platforms/Open stockyard - Bullet cameras |  |  |  | 0 | 0
2: 2. All entry and exits of Control room building, 220kV GIS Building(s) - Bullet cameras |  |  |  | 0 | 0
2: 3. All gates of substation and switchyard - Bullet cameras |  |  |  | 0 | 0
2: 4. Control Room Building (Inside Areas) - Panel Room, HMI Room, Communication Room, LT(AC/DC) Panel Room, Battery Room. - Bullet/Dome cameras |  |  |  | 0 | 0
2: 5. 220kV & 33kv GIS Building (Inside Areas) - GI Switchgear Hall, Panel Room - Bullet/Dome cameras |  |  |  | 0 | 0
2: 6. Entry and Exit of Security Shed cum main gate complex - Bullet cameras |  |  |  | 0 | 0
2: 7. Entry and Exit of FFPH (if in scope) - Bullet cameras |  |  |  | 0 | 0
2: 8. Switchyard areas (All voltage levels) - PTZ Cameras |  |  |  | 0 | 0
2: 9. Transformers and Reactors under present scope- Bullet/PTZ cameras |  |  |  | 0 | 0
2: 10. Substation boundary wall |  |  |  | 0 | 0
2: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. |  |  |  | 0 | 0
1: 32; 2: Essential Tools & Plants as per Technical Specification |  |  |  | 0 | 0
32.1 | SF6 gas analyzer: Portable type instruments (A). In-built calibration facility. (B). Sensitivity of the equipment shall not be affected by any atmospheric conditions like dust, humidity, heat, wind etc. (C). Equipment shall work on zero gas loss principle i.e. gas should be pumped back to the compartment after measurement without any exposure to the atmosphere.(D). Equipment shall be supplied with suitable regulator which can be used to connect SF6 cylinder if required. (E). Following acidic/impurities products should be detected as per IEC 60480 and IEC 60376 (i) SF6 purity – Range: 0-100 % & Accuracy: +/- 0.5 %, (ii) Dew point - Range : -60 to +20 deg C & Accuracy: +/- 0.5 deg C, (iii) SO2 - Range : 0-150 ppm & Accuracy : +/- 2 %,(iv) CF4 – Range : 0-60% vol & Accuracy : +/- 1 % , (v) HF - Range : 0-200ppm & Accuracy : +/- 5 %, (F). Instrument should work on AC source as well as on rechargeable battery, (G). Input pressure: upto 10 bar h. It should be housed in a robust IP67 case with wheels. | SET | 1 | 885979.81 | 79738.1829 | 79738.1829 | 1045456.1758 | 1045456.1758 | Badakusasthali 37.1 |  |  | 1045456.1758 | 0
32.2 | SF6 gas leak detector: The detector shall be portable, battery operated with built in battery charger, hand held type and having a minimum SF6 gas leakage sensitivity of 5gm/year. The sensor shall be connected through a flexible wand for easy accessibility to joints, seals and couplings in GIS equipment and provided with a protection filter. The equipment shall have on/off switch & suitable indicating lamps/LEDs, variable pitch audible signal for leakage indication, and a head phone jack. The equipment shall have automatic zeroing of background signals suitable for detecting SF6 gas leakage in charged switchyard AIS/GIS. The test kit shall be compatible for EMI/EMC environment as per IEC 1000. [DILO/WIKA] | SET | 1 | 37053.85 | 3334.8465 | 3334.8465 | 43723.543 | 43723.543 | Badakusasthali 37.2 |  |  | 43723.543 | 0
32.3 | SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant with spares for 5 years Operation. The plant necessary for filling and evacuating the SF6 gas in the switchgear shall be supplied to enable any maintenance work to be carried out. This shall include all the necessary gas cylinders for temporarily storing the evacuated SF6 gas. The capacity of the temporary storage facilities shall at least be sufficient for storing the maximum quantity of gas that could be removed from at least one phase of one complete bay. The minimum capacity of evacuation plant shall be: Vacuum Pump: 63 M3/Hour. Suction/Compression Pump: 15 M3/Hour (Delivery). The evacuation equipment shall be provided with all the necessary pipes, couplings, flexible tubes and valves for coupling up to the switchgear for filling or evacuating all the gases. The gases compartments shall be fitted with permanent non-return valves through which the gas is pumped into or evacuated form the compartments. [DILO make] | SET | 1 | 2464271.74 | 221784.4566 | 221784.4566 | 2907840.6532 | 2907840.6532 | Badakusasthali 37.3 |  |  | 2907840.6532 | 0
33 | 250 KVA Outdoor type silent Diesel Generator with control panel having adequate mechanical & electrical protection as per IS/IEC/TS. Max voltage variation: ± 1%, Max freq variation ± 2%. Voltage adjustment range -90% to +110%, Max vibration level 250um, Emergency Shutdown feature. Start/Stop: DG sets shall auto-start and take full load within 30 seconds of power failure. Feature for start/stop manually from remote as well as local. Alternator: 415V AC, 3Ph,50Hz, Rated PF 0.8, Brushless/SelfExcited, Class H insulation, 1500 rpm, with 10% overload capacity for 1 hour every 12 hours of continuous operation as per IS15999/IEC 60034. Engine: Multi cyliner, V type or Inline type, 1500 rpm, 4 stroke, Turbo Charged, Water Cooled, Battery Operated - Auto Start, Electronic Governer, Condensate traps shall be given on exhaust pipe, Diesel driven, as per IS 10002/BS 5514/ISO 3046/ IS 13018. Battery: Lead Acid, 24V DC, 180 AH, 2 Sets Charger: Float cum Boost SMPS Based, Ripple 1% max Fuel Tank & Pump: Tank: 990 liter, 2mm MS Sheet with Oil resistant paint, with Level Indicator, Filling Inlet with removable screen, outlet, drain plug, an air vent, air-breather and necessary piping with erection of the same as per Indian Explosive Act of 1932. Pump: Electrically Driven, Adequate to fill the fuel tank in 30 minutes Accuostic Enclosure: Sheet thickness 2 mm min, Rockwool insulation (min 50 mm thick) with fire resistant thermosetting resin, Noise level as per CPCB norms with a max of 75 dBA at a distance of 1 m. Emission standards: as per Latest MOEF/ CPCB/ SPCB guidelines. | SET | 1 | 1619543.0475 | 145758.8743 | 145758.8743 | 1911060.7961 | 1911060.7961 | BADAKUSHASTHALI 41 |  |  | 1911060.7961 | 0
2: AMF Panel: Auto/Manual operation, IP 52, Controller, Metering CT (CL1, 15VA), Protection CT (Vk 300V, RCT 0.25 ohm) ions, Indications [DG Mains ON, Charger ON, DG Breaker ON/OFF, LT Source 1 ON, LT Source 2 ON] Controller: Microprocessor based, IEC 61850 compliant [for monitoring, meaurement , protection and control] * Meaurement: V, I, f, PF, O/P kVA, O/P kW, Speed, Run time, Lube Oil Pr., Coolant temp. etc. * Protection/Shurdown Functions: Differential, Short circuit protection, Over speed, Over Load, UV/OV, Low Lube OIl pressure, High Coolant Temp., High Enclosure Temp., Alternator Fault * Warning: Protection trip, Fail to crank, High/Low battery voltage, DG fail to start, Low fuel in tank * Indication (LED): DG running, Local/Remote mode, Manual/Auto mode, Warning, Shutdown. This includes all instrument transformers, internal wiring, indications and control switchgear etc. required to complete the system. |  |  |  | 0 | 0
34 | EOT Crane for GIS building for 220 kV GIS: Double Girder EOT Crane for GIS building for 220 kV GIS station, 5T Capacity safe working load & minimum height of crane have shall be 8.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. Sufficient head clearance (1800mm.) above the crane top level to the bottom of the Roof beam shall be provided. | SET | 1 | 1429768.75 | 128679.1875 | 128679.1875 | 1687127.125 | 1687127.125 | BADAKUSHASTHALI 51 |  |  | 1687127.125 | 0
35 | BEST QUALITY & APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 40 | 2894.06 | 260.4654 | 260.4654 | 3414.9908 | 136599.632 | Neulopoi Estimate |  |  | 136599.632 | 0
1: 36; 2: Supply of Auto Transformer with spares as per technical specification & conducting the type tests as per the TS. |  |  |  | 0 | 0
36.1 | 220/132 KV, 200 MVA Auto Transformer with spares as per TS | Nos | 2 | 152741375.112 | 13746723.7601 | 13746723.7601 | 180234822.6322 | 360469645.2643 | CD63 |  |  | 360469645.2643 | 0
36.2 | The following type tests shall be carried out in presence of Purchaser’s representative on one unit out of the lot at the discretion of the purchaser. (a) Temperature Rise Test. (b) Measurement of Zero Sequence Impedance. (c) Auxiliary Power Consumption.. (d) Vacuum Test (e) Pressure Test (f) IP-55 Test (on one of the marshalling boxes) | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS |  |  | 590000 | 0
36.3 | NCTs for the Auto Transformers | Lot | 2 | 53153.9 | 4783.851 | 4783.851 | 62721.602 | 125443.204 | CD SS-24/25-28 |  |  | 125443.204 | 0
36.4 | Digital RTCC Panel with 2 nos of Digital RTCC relays (for 2 Auto Transformers) and cutouts for additional Two Relays. | Lot | 1 | 1500000 | 135000 | 135000 | 1770000 | 1770000 | Tentative |  |  | 1770000 | 0
36.5 | Online Drying out system for Auto Transformer | Lot | 2 | 1000000 | 90000 | 90000 | 1180000 | 2360000 | P.O No.953/000591,Dt.22.05.23 of Sr.GM,CC (500MVA ICT-3 N. Duburi) |  |  | 2360000 | 0
37 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System): Suitable for 220/132/33 KV, 160 MVA Auto Transformer as per Technical Specification & latest standard. | Nos | 2 | 1500000 | 135000 | 135000 | 1770000 | 3540000 | LS |  |  | 3540000 | 0
1: 38; 2: MODIFICATION FOR EXISTING 33KV OUT-GOING FEEDERS (4No.) |  |  |  | 0 | 0
38.1 | Supply of 33KV XLPE Cables (1CX300Sqmm): Single core annealed copper cable with Aluminium corrugated sheath as per technical specification | Km | 3.2 | 3266724.02 | 294005.1618 | 294005.1618 | 3854734.3436 | 12335149.8995 | CD 2024-25-156 |  |  | 12335149.8995 | 0
38.2 | 33kV Out door type termination kit | No. | 32 | 11401.29 | 1026.1161 | 1026.1161 | 13453.5222 | 430512.7104 | CD 2024-25-157 |  |  | 430512.7104 | 0
38.3 | HDG DP STRUCTURE FOR 33KV OUT GOING FEEDERS SUITABLE FOR TERMINATION OF 33KV CABLE: each shall comprise of [2X9.0Mtrs (ISBM:200x100mm(min) RS joist (beam), suitable channles(ISMC 100X50) for bracings & base for fixing 33kV Isolator & SA and suitable angles (L50X50X6) & different size steel plate of 10mm thick & suitable GI pipe for the isolator from the operating arm to operating mechanism box etc. Provision for support to the 33KV cable (both incoming & outgoint) along with stay set with required nuts & bolts | Set | 8 | 89570.9594 | 8061.3863 | 8061.3863 | 105693.7321 | 845549.8571 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC |  |  | 845549.8571 | 0
38.4 | 33kV Metal Oxide Surge arrester | No. | 24 | 9416.38 | 847.4742 | 847.4742 | 11111.3284 | 266671.8816 | CD 2024-25-32 |  |  | 266671.8816 | 0
2: TOTAL OF PART-I _SCHEDULE VIIA_SUPPLY COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION (PART-A + PART-B) including GST@18%; 9= (8x4): 730561974.9617 |  |  | 361706886.4934 | 0
0
1: B; 2: Part-B_Supply_Mandatory spares |  |  |  | 0
SL NO | DESCRIPTION OF ITEMS(SCHEDULE-VIIA-LINE) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | Unit | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) (INR) | OGST@9% | CGST@9% | Total Unit Price | TOTAL PRICE IN RS,
1: 1; 2: SPARES FOR 245KV GIS |  |  |  | 0 | 0
1.1 | 245kV Cable Termination Kit including cable to Air bushing suitable for Outdoor for 220KV feeders and Transformers suitable for 1C x 1000 sqmm Copper Cable. | Nos | 1 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 1265156.0452 | PARADEEP PLASTIC PARK |  |  | 1265156.0452 | 0
1.2 | 245kV Cable Termination Kit suitable for Indoor for 220KV feeders and Transformers suitable for 1C x 1000 sqmm Copper Cable. (Termination at GIS) | Nos | 1 | 1072166.14 | 96494.9526 | 96494.9526 | 1265156.0452 | 1265156.0452 | PARADEEP PLASTIC PARK |  |  | 1265156.0452 | 0
1.3 | Set of spares for local control cabinet (LCC) including M.C.B.(1 nos for each rating used), fuses (3 nos each rating), time relays ( 1 nos for each rating), all type of auxiliary relay (1 nos for each type) & contactors (1 nos for each type), lamps (3 nos for each type), semaphore (3 nos for each type), terminals ( 50 nos), push buttons ( 3 nos for each type) etc for 245KV GIS | SET | 1 | 310704.068 | 27963.3661 | 27963.3661 | 366630.8002 | 366630.8002 | PARADEEP PLASTIC PARK |  |  | 366630.8002 | 0
1.4 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for 245KV GIS : 2 nos. of each type | Set | 1 | 108530.85 | 9767.7765 | 9767.7765 | 128066.403 | 128066.403 | PARADEEP PLASTIC PARK |  |  | 128066.403 | 0
1.5 | Trip coil assembly with resistor for 245KV GIS Circuit breaker | Set | 4 | 5565.29 | 500.8761 | 500.8761 | 6567.0422 | 26268.1688 | PARADEEP PLASTIC PARK |  |  | 26268.1688 | 0
1.6 | Closing coil assembly with resistor for 245KV GIS Circuit breaker | Set | 4 | 5565.29 | 500.8761 | 500.8761 | 6567.0422 | 26268.1688 | PARADEEP PLASTIC PARK |  |  | 26268.1688 | 0
1.7 | Auxiliary contacts for 245KV GIS circuit breaker | Set | 2 | 20871.63 | 1878.4467 | 1878.4467 | 24628.5234 | 49257.0468 | PARADEEP PLASTIC PARK |  |  | 49257.0468 | 0
1.8 | Limit switch & Auxiliary contacts for 245KV GIS DS and ES | Set | 2 | 41741.24 | 3756.7116 | 3756.7116 | 49254.6632 | 98509.3264 | PARADEEP PLASTIC PARK |  |  | 98509.3264 | 0
1.9 | SF6 gas in steel bottle 52 Kg / bottle | Set | 2 | 116547.47 | 10489.2723 | 10489.2723 | 137526.0146 | 275052.0292 | PARADEEP PLASTIC PARK |  |  | 275052.0292 | 0
1.1 | Spring charge motor for 245KV GIS circuit breakers | Set | 1 | 20871.63 | 1878.4467 | 1878.4467 | 24628.5234 | 24628.5234 | PARADEEP PLASTIC PARK |  |  | 24628.5234 | 0
1.11 | Complete Drive for 245KV GIS circuit breaker: | Set | 1 | 20871.21 | 1878.4089 | 1878.4089 | 24628.0278 | 24628.0278 | PARADEEP PLASTIC PARK |  |  | 24628.0278 | 0
1.12 | Complete drive mechanism for disconnect switches and grounding switches for 245KV GIS | Set | 1 | 208712.21 | 18784.0989 | 18784.0989 | 246280.4078 | 246280.4078 | PARADEEP PLASTIC PARK |  |  | 246280.4078 | 0
1.13 | Motor for disconnect switches and grounding switches for 245KV GIS | Set | 1 | 27828.5 | 2504.565 | 2504.565 | 32837.63 | 32837.63 | PARADEEP PLASTIC PARK |  |  | 32837.63 | 0
1.14 | Complete drive mechanism for fast acting grounding switches for 245KV GIS | Set | 1 | 132184.61 | 11896.6149 | 11896.6149 | 155977.8398 | 155977.8398 | PARADEEP PLASTIC PARK |  |  | 155977.8398 | 0
1.15 | Motor for fast acting grounding switches for 245KV GIS | Set | 1 | 27828.5 | 2504.565 | 2504.565 | 32837.63 | 32837.63 | PARADEEP PLASTIC PARK |  |  | 32837.63 | 0
1.16 | Locking device to keep the Disconnectors and Earthing switches in close or Open position in case of removal of driving mechanism for 245KV GIS. | Set | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | PARADEEP PLASTIC PARK |  |  | 59000 | 0
1: 3; 2: 245 KV, 2000A, 50KA ISOLATORS |  |  |  | 0 | 0
3.1 | Fixed & Moving Contact Assembly set for One complete Isolator | Set | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | PARADEEP PLASTIC PARK |  |  | 59000 | 0
4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | Nos | 3 | 59726.14 | 5375.3526 | 5375.3526 | 70476.8452 | 211430.5356 | PARADEEP PLASTIC PARK |  |  | 211430.5356 | 0
1: 10; 2: Spares for Protection system |  |  |  | 0 | 0
1: 10.1; 2: 220 KV side |  |  |  | 0 | 0
10.1.1 | Distance Protection Relay (Main-I) | Nos | 1 | 211865 | 19067.85 | 19067.85 | 250000.7 | 250000.7 | PARADEEP PLASTIC PARK |  |  | 250000.7 | 0
10.1.2 | Distance Protection Relay (Main-II) | Nos | 1 | 211865 | 19067.85 | 19067.85 | 250000.7 | 250000.7 | PARADEEP PLASTIC PARK |  |  | 250000.7 | 0
10.1.3 | Differential Protection Relay (Main-I) | Nos | 1 | 220339 | 19830.51 | 19830.51 | 260000.02 | 260000.02 | PARADEEP PLASTIC PARK |  |  | 260000.02 | 0
10.1.4 | Backup O/C & E/F Relay | Nos | 1 | 220339 | 19830.51 | 19830.51 | 260000.02 | 260000.02 | PARADEEP PLASTIC PARK |  |  | 260000.02 | 0
10.1.5 | BCU | Nos | 1 | 516011 | 46440.99 | 46440.99 | 608892.98 | 608892.98 | PARADEEP PLASTIC PARK |  |  | 608892.98 | 0
10.1.6 | HV REF Relay | Nos | 1 | 11695 | 1052.55 | 1052.55 | 13800.1 | 13800.1 | PARADEEP PLASTIC PARK |  |  | 13800.1 | 0
10.1.7 | LV REF Relay | Nos | 1 | 11695 | 1052.55 | 1052.55 | 13800.1 | 13800.1 | PARADEEP PLASTIC PARK |  |  | 13800.1 | 0
10.1.8 | Bus VT Selection Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66 | PARADEEP PLASTIC PARK |  |  | 25000.66 | 0
10.1.9 | Master Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66 | PARADEEP PLASTIC PARK |  |  | 25000.66 | 0
10.1.10 | Busbar Trip Relay | Nos | 1 | 21187 | 1906.83 | 1906.83 | 25000.66 | 25000.66 | PARADEEP PLASTIC PARK |  |  | 25000.66 | 0
10.1.11 | DC Supervision Relay | Nos | 1 | 6780 | 610.2 | 610.2 | 8000.4 | 8000.4 | PARADEEP PLASTIC PARK |  |  | 8000.4 | 0
10.1.12 | TC Supervision Relay | Nos | 1 | 6780 | 610.2 | 610.2 | 8000.4 | 8000.4 | PARADEEP PLASTIC PARK |  |  | 8000.4 | 0
B | TOTAL SUPPLY OF MANDATORY SPARES FOR SUB-STATION (PART-B) | [6 empty] | 6094482.028
2: TOTAL SUPPLY OF SUBSTATION + MANDATORY SPARES (PART-A + PART-B) INCLUDING GST; 9= (8x4): 736656456.9897 |  |  |  | 736656456.9897 | 0
Note on E154: OPTCL: Rectified
Note on E155: OPTCL: Rectified

## VIIB PALASPANGA SS
ODISHA POWER TRANSMISSION CORPORATION LIMITED
PART -II | SCHEDULE VIIB _ ELECTRICAL ERECTION FOR 220/132KV GIS S/S AT PALASPANGA | NAME OF THE WORK:- Upgradation of 132/33kV GSS Palaspanga to 220/132/33kV GIS S/s and construction of 220KV D/C line from 400/220KV Basudevpur GSS to proposed 220/132KV GIS at Palaspanga with 02Nos. Of 220kV feeder bay extension at Turumunga GSS
| DESCRIPTION OF ITEMS | 220/132 kV GIS Substation Palaspanga: 220KV GIS Bay-5 Nos.(FDR-2,AUTO-2,B/C-1) 132KV AIS Bay-4Nos.(AUTO-2, FDR-2)
SL. No. | ERECTION,TESTING & COMMISSIONING OF ELECTRICAL EQUIPMENT INCLUDING CIVIL WORKS OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNITS | Qty | BASIC PRICE PER UNIT (Taxable Value) In Rs | OGST@9% | CGST@9% | BASIC PRICE PER UNIT including GST | TOTAL PRICE IN RS. | PRICE REFERENCE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9= (8x4)
ELECTRICAL ERECTION WORKS (PART-A)
1 | 245KV GIS EQUIPMENT : Erection, Testing and commissioning of the GIS equipment.
1.1 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated Transformer feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer (5 core), bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 Bus Duct Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, SF6 Gas, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch etc. to complete Transformer feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 125000 | 11250 | 11250 | 147500 | 295000 | Ranua estimate | 295000
1.2 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer (5 core), bus-bar disconnectors with common grounding switch, Motorised disconnectors with safety grounding switch(es), high speed fault making motorised grounding switch, stand alone Local control cubicle, SF6 gas monitoring system for complete bay, SF6 Bus Duct Termination Arrangeement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, SF6 Gas, O- ring & gaskets, Nuts, Bolts & Washers Absorbent, Limit Switch etc. to complete Line feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 125000 | 11250 | 11250 | 147500 | 295000 | Ranua estimate | 295000
1.3 | BUS BAR MODULE WITH VT: 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated /3 ph common, SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), disconnectors, bus bar grounding switch, SF6 gas monitoring system, PD sensors (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers, Absorbent, Limit Switches, SF6 Gas etc. to complete the bus bars with VTs & its earthing arrangement for the GIS equipment with earthing strips of adequate size(as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 2 | 125000 | 11250 | 11250 | 147500 | 295000 | Ranua estimate | 295000
1.4 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnector switches, disconnector with safety grounding switch(es). Stand alone Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets, Nuts, Bolts & Washers, Absorbent, Limit Switch, SF6 Gas etc. to complete Bus Coupler bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | SET | 1 | 125000 | 11250 | 11250 | 147500 | 147500 | Ranua estimate | 147500
1.5 | Portable Partial Discharge(PD) monitoring system: 245 KV system shall have Portable Partial Discharge(PD) monitoring system & shall be capable for measuring PD in charged GIS environment ,bandwidth in order of 100 MHz–2GHz & provision to select a wide range of intermediate bandwidths and the principle of operation shall be based on UHF principle of detection. The Detection and measurement of PD and bouncing particles having in built large coloured LCD for displaying and storing facility in the instrument for further analysis to locate actual source of PD such as free conducting particles, floating components, voids in spacers, particle on spacer surfaces etc. There shall be minimum six channels for measuring at a time. This includes all accessories. | SET | 1 | 4500 | 405 | 405 | 5310 | 5310 | Ranua estimate | 5310
1.6 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed] outside GIS Hall alongwith associated Support structure arrangement, bends, joints, accessories & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. (The GI Bus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 1200 | 700 | 63 | 63 | 826 | 991200 | Ranua estimate | 991200
1.7 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type (31mm/kV)) and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply with IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with tubular type HDG support structure. - SF6 to air bushing shall be placed as close to the GIS building (for both feeder and ICT bays) as practicable to reduce length of Bus Duct used which shall be as per the approved drawing. | No | 18 | 15000 | 1350 | 1350 | 17700 | 318600 | Ranua estimate | 318600
1: 2; 2: 220 kV AIS Switchyard |  | 0
2.1 | 245 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | RC 25-27 SS-10.10.h.(i) | 111124.494
1: 2.2; 2: 245KV, 2000A, 50KA, Isolator (AIS) including post insulators (8 KN) as per TS suitable for SCADA operation |  | 0
2.2.1 | 245KV Single Isolator with Earth switch (for feeder bay) (AIS) | SET | 2 | 33153.68 | 2983.8312 | 2983.8312 | 39121.3424 | 78242.6848 | RC 25-27 SS-10.10.d.(i) | 78242.6848
2.2.2 | 245KV Single Isolator without Earth switch (for Transformer bay) (AIS) | SET | 2 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 70517.4608 | RC 25-27 SS-10.10.b.(i) | 70517.4608
2.3 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 12 | 2853.72 | 256.8348 | 256.8348 | 3367.3896 | 40408.6752 | RC 25-27 SS-10.10.j.(i) | 40408.6752
2.4 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 12 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 73686.7992 | RC 25-27 SS-10.10.i.(i) | 73686.7992
1: 3; 2: 132KV AIS SY Equipments |  | 0
3.1 | 120 KV METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No. | 12 | 4532.4 | 407.916 | 407.916 | 5348.232 | 64178.784 | RC 25-27 SS-10.2.g.(i) | 64178.784
1: 3.2; 2: 145 KV, 2000A, 40kA ISOLATORS (with 8kN post insulators) |  | 0
3.2.1 | 132KV Single Isolator without Earth Switch,2000A | SET | 4 | 14058.83 | 1265.2947 | 1265.2947 | 16589.4194 | 66357.6776 | RC 25-27 SS-10.2.b.(i) | 66357.6776
3.2.2 | 132KV Double Isolator without Earth Switch,2000A | SET | 2 | 22662.01 | 2039.5809 | 2039.5809 | 26741.1718 | 53482.3436 | RC 25-27 SS-10.2.d.(i) | 53482.3436
3.2.3 | 132KV Double Isolator with Earth Switch,2000A | SET | 2 | 24760.35 | 2228.4315 | 2228.4315 | 29217.213 | 58434.426 | RC 25-27 SS-10.2.e.(i) | 58434.426
3.2.4 | 132KV Single Isolator with double breake SI beam mounted,2000A | SET | 1 | 12590 | 1133.1 | 1133.1 | 14856.2 | 14856.2 | RC 25-27 SS-10.2.c.(i) | 14856.2
3.3 | 145 KV Solid core Bus Post Insulators-6kN (AIS) | Nos. | 18 | 1846.53 | 166.1877 | 166.1877 | 2178.9054 | 39220.2972 | RC 25-27 SS-10.2.h.(i) | 39220.2972
3.4 | 145 KV, 800-400-200/1-1-1-1A,40 KA, 4 core Single Phase Current Transformer (3 Nos PX CLASS & 1 No. 0.2s CLASS, Vk, Ie as per CT sufficiency calculation ) | Nos | 12 | 8057.6 | 725.184 | 725.184 | 9507.968 | 114095.616 | RC 25-27 SS-10.2.f.(i) | 114095.616
3.5 | 145KV SF6 Circuit Breakers with supporting structures | Nos | 4 | 50360.01 | 4532.4009 | 4532.4009 | 59424.8118 | 237699.2472 | RC 25-27 SS-10.2.a.(i) | 237699.2472
3.8 | 145 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 8057.6 | 725.184 | 725.184 | 9507.968 | 57047.808 | RC 25-27 SS-10.2.f.(i) |  | 57047.808 | 0
1: 4; 2: BUS BAR STRINGING: Supply of labour, T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, Single or Double Hard-wares Fittings, spacers, Clamp & connectors, as per requirements, Jumpers, connections to Equipments (with ACSR Moose or Al. IPS tube), testing, commissioning etc. as per the instruction of Engineer-in charge. |  | 0
4.1 | ACSR MOOSE CONDUCTOR (Twin) | Mtrs | 300 | 252.05 | 22.6845 | 22.6845 | 297.419 | 89225.7 | RC 25-27 SS-14.f.(i) | 89225.7
4.2 | ACSR MOOSE CONDUCTOR (Single) | Mtrs | 100 | 184.65 | 16.6185 | 16.6185 | 217.887 | 21788.7 | RC 25-27 SS-14.e.(i) | 21788.7
4.3 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | Mtrs | 120 | 236.4407 | 21.2797 | 21.2797 | 279 | 33480 | LoA No.339,Dt.06.06.2022 (Turumunga 1stBoQ) | 33480
1: 5; 2: SUBSTATION EARTHING SYSTEMS: As per the approved earth mat design based on the soil resistivity. |  | 0
5.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying | Mtrs | 5086 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 661783.1996 | RC 25-27 SS-21.10.vi(b) | 661783.1996
5.2 | EARTHING CONDUCTOR; 50X6 mm Gl Flat for Raiser from the burial earth mat to equipment, structure, building lightning protection etc) | Mtrs | 6279 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 817014.6894 | RC 25-27 SS-21.10.v(b) | 817014.6894
5.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 200 | 2993 | 269.37 | 269.37 | 3531.74 | 706348 | RC 25-27 SS-21.3 | 706348
5.5 | Direct Stroke Lightening Protection System: (As per TS, approved drawings and directions of Engineer-in-Charge.) using IEC 62305 / Razevig method / National Building Code. The scope includes design and supply of all materials (excluding switchyard columns and lighting cum lightning mast) for DSLP of entire switchyard area under present scope, all buildings, ICT and reactors. Includes all materials such as Shield wires, Horizontal Conductor, Down conductor, Droppers, Earth electrodes, Test link, Cleats, lugs, Air termination rods/ Lightning spike, PG Clamp, D Shackle. etc. and all other accessories to complete the system in full shape. Earthing of the DSLP system is included in the scope. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | LS | 118000
1: 6; 2: G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained & High Quality ISI mark PVC-U selfit Pipe, PVC elbow bend,PVC Tee etc suitable for under ground burrial (HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better) as per TS. |  | 0
6.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 2000 | 80 | 7.2 | 7.2 | 94.4 | 188800 | AUTONAGAR 15.1 | 188800
6.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 2500 | 80 | 7.2 | 7.2 | 94.4 | 236000 | AUTONAGAR 15.2 | 236000
6.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 2500 | 80 | 7.2 | 7.2 | 94.4 | 236000 | AUTONAGAR 15.3 | 236000
6.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 8 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 54122.0688 | RC Page 14 (3.10) | 54122.0688
6.5 | 250mm dia PVC Pipe | MTRS | 200 | 80 | 7.2 | 7.2 | 94.4 | 18880 | LS | 18880
6.6 | 110mm dia PVCPipe | MTRS | 250 | 80 | 7.2 | 7.2 | 94.4 | 23600 | LS | 23600
6.7 | 50mm dia PVC Pipe | MTRS | 700 | 80 | 7.2 | 7.2 | 94.4 | 66080 | LS | 66080
6.8 | PVC pipe bends & other PVC accessories required for 250mm,110mm & 50mm dia as above | Lot | 1 | 10000 | 900 | 900 | 11800 | 11800 | LS | 11800
1: 7; 2: SWITCH YARD STRUCTURES STEEL HDG - LATTICE TYPE FOR TOWER COLUMN, BEAMS & PIPE TYPE FOR ALL EQUIPMENT STRUCTURE ( INCLUDING FOUNDATION BOLTS - ITS NUTS, ITS WASHERS, ITS PLATE ETC ) FOR 220/33 KV CLASS (Weight in brackets are only indicative - Actual weight shall be as per approved BOM. Measurement shall be done accordingly.) |  | 0
1: 7.1; 2: DIFFERENT TYPE OF LATICE TYPE COLUMNS WITH DETAILS & DIFFERENT TYPE OF BEAMS WITH DETAILS |  | 0
1: 7.1.1; 2: P1S-Columns including earth spikes for 220 KV (NOMINAL UNIT WT- 4.676 MT); 3: Nos; 4: 7 |  | 0
1: 7.1.2; 2: Q1-Beams for 220 KV (NOMINAL UNIT WT- 1.598 MT); 3: Nos; 4: 4 |  | 0
1: 7.1.3; 2: T1S - 132 KV(NOMINAL UNIT WT- 1.092 MT); 3: NOS; 4: 8 |  | 0
1: 7.1.4; 2: T4S - 132KV (NOMINAL UNIT WT- 0.849 MT); 3: NOS; 4: 4 |  | 0
1: 7.1.5; 2: DIFFERENT TYPE OF BEAMS WITH DETAILS |  | 0
1: 7.1.6; 2: G1 - 132 KV(NOMINAL UNIT WT- 0.576 MT); 3: NOS; 4: 8 |  | 0
1: 7.1.7; 2: G2 - 132 KV(NOMINAL UNIT WT- 0.851 MT); 3: NOS; 4: 4 |  | 0
7.1.8 | TOTAL WEIGHT OF COLUMN & BEAM INCLUDING FOUNDATION BOLTS, - ITS NUTS, WASHERS PLATE ETC | MT | 59.268 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 407621.2768 | RC 25-27 SS-16.1 | 407621.2768
7.1.9 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 5.93 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 40784.136 | RC 25-27 SS-16.1 | 40784.136
1: 7.2; 2: DIFFERENT TYPE OF TUBULAR SUPPORT STRUCTURES HDG TYPE FOR ALL 220KV & 33KV EQUIPMENT INCLUDING FOUNDATION BOLT - ITS NUTS, ITS WASHERS, ITS PLATE ETC ) |  | 0
1: 7.2.1; 2: 220 KV Single Isolator with Earth Switch (1.477MT); 3: set; 4: 2 |  | 0
1: 7.2.2; 2: 220 KV Single Isolator without Earth Switch (1.4277MT); 3: set; 4: 2 |  | 0
1: 7.2.3; 2: 220 KV Surge Arrester (0.41); 3: Nos; 4: 12 |  | 0
1: 7.2.4; 2: 220 KV IVT (0.41); 3: Nos; 4: 6 |  | 0
1: 7.2.5; 2: 220 KV Post Insulator (1.86); 3: Nos; 4: 12 |  | 0
1: 7.2.6; 2: SINGLE ISOLATORS without ES-132KV ( 0.621 MT); 3: SET; 4: 4 |  | 0
1: 7.2.7; 2: Double isolator without ES 132 KV (1.105MT); 3: SET; 4: 2 |  | 0
1: 10.2.7; 2: Double isolator with ES 132 KV (1.105MT); 3: SET; 4: 2 |  |  | 0 | 0
1: 7.2.8; 2: CTS-132 KV (0.207 MT)); 3: SET; 4: 12 |  | 0
1: 7.2.9; 2: Surge Arrester-132 kV (0.172MT); 3: SET; 4: 12 |  | 0
1: 7.2.10; 2: BPI-132 KV (0.296MT); 3: SET; 4: 18 |  | 0
1: 7.2.11; 2: Strutcure for Cable termination (0.296MT); 3: SET; 4: 18 |  | 0
7.3 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 57.54 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 395736.7933 | RC 25-27 SS-16.1 | 395736.7933
7.4 | Gl bolts ,Nuts, washers plainn & spring etc for the above structures | MT | 5.75 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 39546.1689 | RC 25-27 SS-16.1 | 39546.1689
7.5 | GI Foundation bolts & nuts(3nos) with plate & other washers as required | MT | 4 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 27510.3784 | RC 25-27 SS-16.1 | 27510.3784
8 | 40-metre-high lattice-type (HDG) lighting-cum-lightning mast with landing platforms, including LED lighting fixtures with control gear panels, suitable for Wind Zone-V, complete with all accessories such as the lighting control panel, required armoured copper cables, and other associated items. The number and capacity of lighting fixtures shall be determined based on illumination design to achieve the desired lux level. Suitable landing platforms shall be provided to enable access to the luminaires for repair and maintenance. The design and drawings of the structure shall be vetted by CPRI/IITs. | NOS | 2 | 50000 | 4500 | 4500 | 59000 | 118000 | LS | 118000
1: 9; 2: SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS)(includes switchyard, colony street and other street area) |  | 0
9.1 | SUBSTATION SWITCH YARD LIGHTING(Flood light): ERECTION OF FIXTURES & LAMPS (LED) of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switchgear,etc.(Lighting fixtures are to be fixed rigidly on the Column & lighting cum lightning must at a suitable height so that the required lux can be maintained).As per technical specification for the followings. I. Substation Area | NOS | 50 | 2651.53 | 238.6377 | 238.6377 | 3128.8054 | 156440.27 | RC 25-27 SS-32.10 | 156440.27
9.2 | STREET LIGHTING: Installation of HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. Poles shall be installed on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes installation of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI junction box, GI Conduit etc. & as per technical specification. | NOS | 40 | 2219.6 | 199.764 | 199.764 | 2619.128 | 104765.12 | Neulopoi estimate | 104765.12
1: 10; 2: GENERAL EQUIPMENT & SUBSTATION ACCESSORIES including Supply & fixing of Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building. Cable sealing to be done with Multi-diameter type flexible modular based sealing blocks of different sizes. |  | 0
1: 10.1; 2: Laying of supplied Power Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor. |  | 0
10.1.1 | 3.5 CX300 mm² XLPE | Mtrs | 1000 | 2284.14 | 205.5726 | 205.5726 | 2695.2852 | 2695285.2 | RC 25-27 SS 17.20(xiv) | 2695285.2
10.1.2 | 3.5 CXI85 mm² XLPE | Mtrs | 1500 | 1732.79 | 155.9511 | 155.9511 | 2044.6922 | 3067038.3 | RC 25-27 SS 17.20(xii) | 3067038.3
10.1.3 | 3.5CX120 mm² XLPE | Mtrs | 500 | 1023.93 | 92.1537 | 92.1537 | 1208.2374 | 604118.7 | RC 25-27 SS 17.20(x) | 604118.7
10.1.4 | 3.5 CX70 mm² XLPE | Mtrs | 800 | 685.24 | 61.6716 | 61.6716 | 808.5832 | 646866.56 | RC 25-27 SS 17.20(viii) | 646866.56
10.1.5 | 3.5 CX35 mm² XLPE | Mtrs | 1200 | 519.83 | 46.7847 | 46.7847 | 613.3994 | 736079.28 | RC 25-27 SS 17.20(vi) | 736079.28
10.1.6 | 4 CX 16 mm² XLPE | Mtrs | 1000 | 275.67 | 24.8103 | 24.8103 | 325.2906 | 325290.6 | RC 25-27 SS 17.20(iv) | 325290.6
10.1.7 | 4 CX 6 mm2 XLPE | Mtrs | 2.5 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 464.7135 | RC 25-27 SS 17.20(ii) | 464.7135
10.1.8 | 2CX 6 mm2 XLPE | Mtrs | 3 | 130 | 11.7 | 11.7 | 153.4 | 460.2 | Tentative | 460.2
1: 10.2; 2: Laying of supplied Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor. |  | 0
10.2.1 | 4 CX 2.5 mm2 | Mtrs | 5000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 325326 | RC 25-27 SS 17.10(ii) | 325326
10.2.2 | 5 CX 2.5 mm2 | Mtrs | 6000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 390391.2 | RC 25-27 SS 17.10(ii) | 390391.2
10.2.3 | 7CX 2.5 mm² | Mtrs | 6000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 390391.2 | RC 25-27 SS 17.10(ii) | 390391.2
10.2.4 | 10 CX 2.5 mm2 | Mtrs | 6000 | 63 | 5.67 | 5.67 | 74.34 | 446040 | RC 25-27 SS 17.10(vi) | 446040
10.2.5 | 12 CX 2.5 mm2 | Mtrs | 6000 | 63 | 5.67 | 5.67 | 74.34 | 446040 | RC 25-27 SS 17.10(vi) | 446040
10.2.6 | 16 CX 2.5 mm2 | Mtrs | 3000 | 63 | 5.67 | 5.67 | 74.34 | 223020 | RC 25-27 SS 17.10(vi) | 223020
10.2.7 | 19 CX 2.5 mm2 | Mtrs | 2500 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 232371.5 | RC 25-27 SS 17.10(vix | 232371.5
10.2.8 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 300 | 1023.93 | 92.1537 | 92.1537 | 1208.2374 | 362471.22 | RC24-25-SS-G-2.0.X | 362471.22
10.2.9 | HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better & ITS ACCESSORIES LIKE ALL TYPE OF SOCKETS & BENDS FOR TAKING CABLE FROM TRENCH TO EQUIPMENT MB etc | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | LS | 59000
1: 10.3; 2: Laying of supplied screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI with termination at required equipment including supply & fixing of lugs, Ferrules, clamps, connectors, glands, fixing of cable trays, including supply of N&B, Link plates, Cable Markers, Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements, laying of Earthing Flats, earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor. |  | 0
10.3.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 139422.9 | RC 25-27 SS 36.iv | 139422.9
10.3.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 200 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 18589.72 | RC 25-27 SS 36.iv | 18589.72
1: 11; 2: AIRCONDITIONING: Installation of 2T capacity Split Air Conditioning Units: including AC Control Panel(s) made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 16 amp industrial socket & plug for each unit of AC etc (As per specification) for the following buildings as per the approved drawing. Commissioning of Logic controller for Auto Switch ON & OFF of AC units depending on requirement at various rooms/halls as per approved drawing. Temperature transducer shall be also be installed to monitor the temperature. The Temperature transducer shall have the following specification: (Sensor : Air temperature sensor (indoor use), Output : 4 to 20mA, Temperature range : -5°C to 60°C, Resolution : 0.1°C, Accuracy : 0.5°C or better.) |  | 0
11.1 | Air conditioning System for Control Room Building- VRLA Battery room, HMI Room, Communication Room, ets. Includes supply of AC Control Panel with one nos controller for each AC. | Nos | 16 | 5000 | 450 | 450 | 5900 | 94400 | Neulopoi estimate | 94400
11.2 | Air conditioning System for 220 kV GIS Building - Relay panel room. Includes supply of AC Control Panel with one nos of controller for each AC. | Nos | 15 | 5000 | 450 | 450 | 5900 | 88500 | Neulopoi estimate | 88500
1: 12; 2: 220 KV GIS hall -ventilation system through ducting with 04 air change cycle per hour (Pressurization type ventilation system) as per technical specification |  | 0
12.1 | Ventilation System for 220KV GIS Hall as per technical specification. | LOT | 1 | 60000 | 5400 | 5400 | 70800 | 70800 | LS | 70800
12.3 | GIS Hall exhaust system: Exhaust fans for installation at 1 feet above the GIS hall floor level for exhaust of SF6 gas. Sufficient numbers of exhaust fans of required capacity to be provided for 1 air change per hour, accordingly calculation to be submitted. The exhaust outlet shall be directed downwards at the outer side of the GIS hall and shall be fixed with aluminum mesh at outlet. The exhaust fans shall have louvers for automatic closing when not in use. Control of the system shall be from the SAS-HMI room. Includes supply of panels and other associated materials. | LOT | 1 | 30000 | 2700 | 2700 | 35400 | 35400 | LS | 35400
1: 13; 2: INSTALLATION AND PLACEMENT OF FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTED FIRE EXTINGUSHERS SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC (REFER TS-VOLIIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE -1) |  | 0
13.1 | FOAM TYPE-9 LTRS | NOS | 20 | 165 | 14.85 | 14.85 | 194.7 | 3894 | Neulopoi estimate | 3894
13.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 4 | 336 | 30.24 | 30.24 | 396.48 | 1585.92 | Neulopoi estimate | 1585.92
13.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 135 | 12.15 | 12.15 | 159.3 | 955.8 | Neulopoi estimate | 955.8
13.4 | CO2 - 4.5 KGS | NOS | 15 | 156 | 14.04 | 14.04 | 184.08 | 2761.2 | Neulopoi estimate | 2761.2
13.5 | CO2 - 9 KGS | NOS | 10 | 155 | 13.95 | 13.95 | 182.9 | 1829 | Neulopoi estimate | 1829
13.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 145 | 13.05 | 13.05 | 171.1 | 684.4 | Neulopoi estimate | 684.4
13.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & CANOPY (3 mm thick) | SET | 6 | 336 | 30.24 | 30.24 | 396.48 | 2378.88 | Neulopoi estimate | 2378.88
13.8 | 9 litre water type | Nos. | 6 | 145 | 13.05 | 13.05 | 171.1 | 1026.6 | Neulopoi estimate assumed | 1026.6
13.9 | 4.5 kg DCP type | Nos. | 6 | 145 | 13.05 | 13.05 | 171.1 | 1026.6 | Neulopoi estimate assumed | 1026.6
13.1 | 50 Litres Mechanical Foam type | Nos. | 2 | 145 | 13.05 | 13.05 | 171.1 | 342.2 | Neulopoi estimate assumed | 342.2
1: 14; 2: SUBSTATION AUTOMATION SYSTEM FOR 400/220/33 KV SUBSTATION ON PRP MODE: Supervision, installation , testing & commissioning of Substation Automation system alongwith as per technical specification. The work related to connctivity of the substation SAS with OPTCL Main Control Center (remote) shall also be considered. |  | 0
14.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification) system (for All 132 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Double jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | Neulopoi estimate | 118000
14.2 | RCC Communication Panel; comprising of: 1. Substation Ethernet Switches (Layer-3 type)- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Doublle jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | SET | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | Neulopoi estimate assumed | 23600
14.3 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Nos | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | Neulopoi estimate | 23600
14.4 | Operator Workstations | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Tentative | 59000
1: 14.5; 2: Engineering workstation |  | 0
1: 14.6; 2: Workstation for RAS (Remote Access System) |  | 0
1: 14.7; 2: Black & whiter Laser jet Printer-1Nos |  | 0
1: 14.8; 2: Inverters - 3 KVA (Main & Stand by) |  | 0
1: 14.9; 2: Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. |  | 0
14.1 | Aux. BCU for Substation Auxilliary System (Datas for monitoring of Station AC, Station DC, Lighting, Fire fighting, Air conditioning, Diesel generator etc. as per the site requirement) compliant to IEC 61850 - ED-2 protocol with PRP on FO. Power Supply 220V DC. | SET | 1 | 21000 | 1890 | 1890 | 24780 | 24780 | Badakushasthali 24.2 | 24780
14.11 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | No | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | Badakushasthali 24.3 | 23600
1: 15; 2: 220 KV SIDE PROTECTION PANEL - Single Panel (1 Bay in One Panel) with IEC 61850-ED-2 PRP on FO |  | 0
15.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 75271.4448 | RC25-27 SS 18.10(iv) | 75271.4448
15.2 | 220KV, 160MVA Auto Transformer Protection Panel: Differential (Main-I & Mai-II of separate make), saparate numerical REF, Backup Protection and other aux relays including LBB trip relays & Bay control units (BCU) as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 75271.4448 | RC25-27 SS 18.10(iv) | 75271.4448
15.3 | 220KV Bus Coupler Protection Panel: Backup Protection Relays and other aux relays including LBB trip relays & BCU as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | NOS | 1 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 37635.7224 | RC25-27 SS 18.10(iv) | 37635.7224
15.4 | 220 KV BUS-BAR PROTECTION PANEL(s) (Centralized Architecture): Complete bus bar protection system for proposed bays and Provision for bus bar protection for future bays (at least four nos) and with all other relays & components required for complete protection, control etc as per TS compliant to IEC 61850-ED-2 protocol with PRP on FO. Supply 220V DC dual source with 2 nos DCCOs. | SET | 1 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 37635.7224 | RC25-27 SS 18.10(iv) | 37635.7224
15.5 | 132KV Transformer Protection: 2 nos BCU, separate numeric backup relay, separate numeric REF relay and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 28957.02 | 2606.1318 | 2606.1318 | 34169.2836 | 68338.5672 | RC25-27 SS 18.10(vi) | 68338.5672
20.17 | 132KV Feeder Protection: 2 nos BCU, separate numeric backup relay, separate numeric REF relay and other auxiliary relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC dual source with 2 nos DCCOs. | NOS | 2 | 21822.67 | 1964.0403 | 1964.0403 | 25750.7506 | 51501.5012 | RC25-27 SS 18.10(v) |  | 51501.5012 | 0
1: 16; 2: AC & DC SYSTEM |  | 0
1: 16.1; 2: AC SYSTEM : Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS: |  | 0
16.1.1 | MAIN AC DB,(HAVING A 1600 A, 50KA, DRAWOUT TYPE ACB WITH Numerical SAS complaint protective relay for O/C , E/F, UV, OV etc FACILITY and MECH & ELECT INTERLOCK FACILITY.(MAIN DB-1,MAIN DB-2 WITH B/C). The outgoing of the station Transformers shall be the two incomers for the Mian ACDB. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% / at least 1 no. (whichever is higher) spares of each rating feeder. The cosntruction of the Main ACDB shall be as per the TS. The Main ACDB shall be suitable for automatic switching and shall be operated from SAS when on manual mode. | SET | 1 | 7357.07 | 662.1363 | 662.1363 | 8681.3426 | 8681.3426 | Neulopoi estimate | 8681.3426
16.1.2 | ACDB (HAVING 800A MCCB in Incomer and Bus couplers with electrical interlock system) AS PER SPECIFICATION (With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected from two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads.). The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching ON & OFF. | SET | 1 | 7357.07 | 662.1363 | 662.1363 | 8681.3426 | 8681.3426 | Neulopoi estimate | 8681.3426
16.1.3 | Main Lighting Distribution Board (having 250A MCCB as Incomer) as per TS (witc DB-1,DB-2 & B/C) with mechanical Interlock through castle lock. | SET | 1 | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278 | Neulopoi estimate | 8208.3278
16.1.4 | Indoor Lighting Distribution Board as per TS. (WITH DB-1,DB-2 & B/C) | SET | 1 | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278 | Neulopoi estimate | 8208.3278
16.1.5 | Emergency Lighting Distribution Board as per specification. | SET | 1 | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278 | Neulopoi estimate | 8208.3278
16.1.6 | Indoor Receptacle Board as per Specification | SET | 2 | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 16416.6556 | Neulopoi estimate | 16416.6556
16.1.7 | Outdoor Kiosk For Station Transformer: as per TS with 3 NOS. OF Cut-Outs (1000 Amps) at the Incoming side, 1No. of 3 phase SFU (1000 Amps) at the Outgoing and suitable Busbar arrangement for termination of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 8673 | 780.57 | 780.57 | 10234.14 | 20468.28 | Neulopoi estimate | 20468.28
16.1.8 | Outdoor Kiosk for Switchyard Lights: as per TS having timer control for switching the lights ON & OFF. | SET | 6 | 5900 | 531 | 531 | 6962 | 41772 | Neulopoi estimate | 41772
16.1.10 | Outdoor Kiosk for Street Lights: as per TS having timer control for switching the lights ON & OFF. | NOS | 4 | 5900 | 531 | 531 | 6962 | 27848 | Neulopoi estimate | 27848
16.1.11 | Outdoor Receptacle Board: (Transformer filtration purpose): as per TS | NOS | 2 | 3005.2696 | 270.4743 | 270.4743 | 3546.2181 | 7092.4362 | Neulopoi estimate | 7092.4362
16.1.12 | Outdoor Receptacle Board: (Welding & other uses) : as per TS | NOS | 4 | 3005.2696 | 270.4743 | 270.4743 | 3546.2181 | 14184.8723 | Neulopoi estimate | 14184.8723
16.1.13 | Bay Marshalling Kiosk (Outdoor type): as per TS, (10 nos on 220 kV bay, 10 Nos for 400 kv bays, 3 Nos for 33KV bays ) | Nos | 6 | 6601 | 594.09 | 594.09 | 7789.18 | 46735.08 | Neulopoi estimate | 46735.08
16.1.14 | CT Out Door Console Boxes: As per TS (Outdoor type) | Nos | 4 | 3005.2696 | 270.4743 | 270.4743 | 3546.2181 | 14184.8723 | RC-25-26-SS-H.1.6 | 14184.8723
16.1.15 | PT Outdoor Console Boxes: as per TS | Nos | 4 | 3005.2696 | 270.4743 | 270.4743 | 3546.2181 | 14184.8723 | RC-25-26-SS-H.1.7 | 14184.8723
1: 16.2; 2: DC SYSTEM |  | 0
16.2.1 | 220 V MAIN DCDB in Control Room Building (HAVING DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE protection (with BUS-1, BUS-2 & B/C). Consider separate source(DC1 & DC 2) to each DCDB of Bay Kiosks, local supply of CRB such as emergency lighting, SAS system etc. & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered ( with 20% spare). Incoming and outgoing ratings of MCBs shall be decided as per panel load during detail engineering. The construction shall be as per the TS. | SET | 1 | 8147.22 | 733.2498 | 733.2498 | 9613.7196 | 9613.7196 | Neulopoi estimate | 9613.7196
16.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 1 | 6779 | 610.11 | 610.11 | 7999.22 | 7999.22 | Neulopoi estimate | 7999.22
16.2.3 | Stationary Plante Battery, 350 Ah (C10 rate) for 220 V DC (Cells: 107 Nos + 3 Nos, 2V Nominal/Cell) as per TS and IS 15549 & IEC 60896-21/22. Installation. Testing and commissioning of the VRLA Battery Set. | SET | 1 | 19640.41 | 1767.6369 | 1767.6369 | 23175.6838 | 23175.6838 | RC 25-27-SS-20.(i) | 23175.6838
16.2.4 | FLOAT CUM BOOST Battery Charger for offered 800 Ah VRLA Type Battery: Installation. Testing and commissioning of the VRLA Battery Charger. | SET | 1 | 5455.68 | 491.0112 | 491.0112 | 6437.7024 | 6437.7024 | RC 25-27-SS-18.50 | 6437.7024
17 | Maintenance Testing Equipment (All equipment shall comply to the TS and as per list below) | Lot | 1 | 3389 | 305.01 | 305.01 | 3999.02 | 3999.02 | Neulopoi estimate | 3999.02
1: 17.1; 2: Demonstration of the 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C); 3: Nos; 4: 1 |  | 0
1: 17.2; 2: Demonstration of the 10KV Insulation Tester with 15m test lids (Megger- S1-1068 / Sonel-MIC 10K1); 3: Nos; 4: 1 |  | 0
1: 17.3; 2: Demonstration of the Digital Earth Tester (Facility with soil resistivity measurement) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625); 3: Nos; 4: 1 |  | 0
1: 17.4; 2: Demonstration of the Digital Multimeter (Megger / Fluke); 3: Nos; 4: 2 |  | 0
1: 17.5; 2: Demonstration of the Digital Clamp meter (Megger/Fluke/Motwane); 3: Nos; 4: 1 |  | 0
1: 17.6; 2: Demonstration of the Leakage current clamp meterAC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu); 3: Nos; 4: 1 |  | 0
1: 17.7; 2: Demonstration of the SF6 Gas Leakage Detector (Kika/DILO); 3: Nos; 4: 1 |  | 0
1: 17.8; 2: Demonstraion of the Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico); 3: Set; 4: 6 |  | 0
1: 17.9; 2: Demonstraion of the Portable High Beam Light (rechargeable); 3: Nos; 4: 2 |  | 0
1: 17.1; 2: Installation of the Desktop Computer: (HP/Lenovo/Dell) complete with all accessories including webcam and speakers and validation of the Genuine Windows Operating System; 3: Set; 4: 2 |  | 0
1: 17.11; 2: Installation of the UPS 600VA (APC/V Guard) and verification of the backup; 3: Nos; 4: 2 |  | 0
1: 17.12; 2: Installation of the Laser Printer, Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson); 3: Nos; 4: 1 |  | 0
18 | Office Furniture: Godrej make (As per details below). Placing In Control Room, Communication Room, Conference Room, Office Rooms, Library, Testing Lab etc. | Lot | 1 | 10000 | 900 | 900 | 11800 | 11800 | LS | 11800
1: 18.1; 2: For Control Room, conference room, office rooms, Library, testing room etc |  | 0
1: 18.2; 2: 5ftX3ft executive table with drawer on both sides; 3: Nos; 4: 4 |  | 0
1: 18.3; 2: 4.5ft X 2.5ft Table with one side drawer; 3: Nos; 4: 7 |  | 0
1: 18.4; 2: Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use.; 3: Set; 4: 1 |  | 0
1: 18.5; 2: Executive revolving, adjustable (height) chairs with arm; 3: Nos; 4: 4 |  | 0
1: 18.6; 2: Cushion fixed “S” type steel chairs with arm; 3: Nos; 4: 16 |  | 0
1: 18.7; 2: 6ftX3ft conference table; 3: Nos; 4: 1 |  | 0
1: 18.8; 2: Cushion arm steel chairs for conference table purpose.; 3: Nos; 4: 6 |  | 0
1: 18.9; 2: 6ft height steel almirah (only with selves) for keeping records and other valuable items.; 3: Nos; 4: 3 |  | 0
1: 18.1; 2: 6ft height steel almirah with glass doors for library purpose; 3: Nos; 4: 2 |  | 0
1: 18.11; 2: 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement.; 3: Nos; 4: 2 |  | 0
1: 18.12; 2: 4ft steel rack (minimum three selves) for keeping the files and other items.; 3: Nos; 4: 8 |  | 0
1: 18.13; 2: For Communication Room |  | 0
1: 18.14; 2: 5ftX3ft executive table with drawer both sides; 3: Nos; 4: 1 |  | 0
1: 18.15; 2: Executive revolving, adjustable (height) chairs with arm; 3: Nos; 4: 1 |  | 0
1: 18.16; 2: Cushion fixed “S” type steel chairs with arm; 3: Nos; 4: 2 |  | 0
1: 18.17; 2: 6ft height steel almirah (only with selves) for keeping records and other valuable items.; 3: Nos; 4: 1 |  | 0
19 | De-Mineralised Plant of 50 L/Hr or more for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) | Nos | 1 | 1590 | 143.1 | 143.1 | 1876.2 | 1876.2 | Neulopi estimate | 1876.2
20 | Installation & demo of the 20 Ltr Storage Water Cooler (Voltas/Bluestar only) for performance | Nos | 2 | 1590 | 143.1 | 143.1 | 1876.2 | 3752.4 | Neulopi estimate | 3752.4
21 | Installation and demo of the Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only for performance | Nos | 2 | 1590 | 143.1 | 143.1 | 1876.2 | 3752.4 | Neulopi estimate | 3752.4
22 | BEST QUALITY & APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 40 | 20 | 1.8 | 1.8 | 23.6 | 944 | Neulopi estimate | 944
1: 23; 2: INSTALLATION & COMMISSIONING OF ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | Neulopi estimate | 0
23.1 | 48 fibre optic approach cable including HDPE pipes | KM | 1 | 70800 | 6372 | 6372 | 83544 | 83544 | Neulopi estimate | 83544
23.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at Other end 400KV and 220 kV S/s | SET | 14 | 35400 | 3186 | 3186 | 41772 | 584808 | Neulopi estimate | 584808
23.3 | 48V , 500Ah, maintenance free VRLA battery set | NO | 2 | 5892.12 | 530.2908 | 530.2908 | 6952.7016 | 13905.4032 | RC-25-27-39.ii | 13905.4032
23.4 | SMPS based battery charger of 125A suitable for 48V, 500Ah VRLA battery | NO | 2 | 7800 | 702 | 702 | 9204 | 18408 | Neulopi estimate | 18408
23.5 | 48 V DC board (having 100A DC MCCB as incomer, E/F (earth leakage), under & over voltage as per specification (DC DB-1,DC DB-2 & B/C). | SET | 1 | 7800 | 702 | 702 | 9204 | 9204 | Neulopi estimate | 9204
23.6 | Optical Line Terminal Equipent(OLTE), STM16 type (5 MSP) SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module support upto 150kms ( 02 Nos.) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 150000 | 13500 | 13500 | 177000 | 177000 | Neulopi estimate | 177000
23.7 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 7080 | 637.2 | 637.2 | 8354.4 | 16708.8 | Neulopi estimate | 16708.8
23.8 | Earth flat, cable tray, telephone cable, ACDB, DCDB, foundation rail, Junction Box, Cat 5 cable & Misc items | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | Neulopi estimate | 236000
23.9 | Voice gateway 2x(FXS) | Nos | 1 | 15000 | 1350 | 1350 | 17700 | 17700 | LS | 17700
24 | INSTALLATION & COMMISSIONING OF Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. Description of system as below: | LOT | 1 | 45000 | 4050 | 4050 | 53100 | 53100 | Neulopoi estimate | 53100
25 | SF6 gas analyzer: Demonstartion of the performance of the instrument | SET | 1 | 5000 | 450 | 450 | 5900 | 5900 | LS | 5900
26 | SF6 gas leak detector: Demonstartion of the performance of the instrument | SET | 1 | 5000 | 450 | 450 | 5900 | 5900 | LS | 5900
27 | SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant Demonstartion of the performance of the instrument | SET | 1 | 5000 | 450 | 450 | 5900 | 5900 | LS | 5900
28 | Lifting, installation, testing, commissioning of the 250KVA Diesel generator and other accessories required for complete installation in compliance with the Standard applicable, specifications and the manufacturer’s instructions, with all statuatory approvals for 250 KVA outdoor type silent Generator with control panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature, and with Stator CT for differential protection as per Technical spec. Metering CT for DG to be provided with installation of meter as per statutory requirement. Indoor AMF panel with switchgears also included. | NOS | 1 | 79083 | 7117.47 | 7117.47 | 93317.94 | 93317.94 | LoA No.221,Dt.01.02.25 (Neulpoi) | 93317.94
1: 29; 2: Installation, Testing and Commissioning of Transformers: Receiving the Transformers and its accessories from nearest OPTCL stores, dragging and installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & P's. |  | 0
29.1 | 220/132KV, 160 MVA Auto Transformer | Nos | 2 | 382132.12 | 34391.8908 | 34391.8908 | 450915.9016 | 901831.8032 | RC-25-27-ss-22.2.2.(a).i | 901831.8032
29.2 | Digital RTCC panel. | Lot | 1 | 18465.34 | 1661.8806 | 1661.8806 | 21789.1012 | 21789.1012 | RC25-27-SS-18.20 | 21789.1012
29.3 | Testing & commisioning of the Digital RTCC relays for each trasnformer. The DM & the Marshalling box of the transformer shall be wired with the RTCC relay and tested for its performance locally(HMI of relay) and through SAS. | Lot | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | LS | 23600
29.4 | NCTs including its mounting arragement as per TS. | Lot | 2 | 3000 | 270 | 270 | 3540 | 7080 | LS | 7080
29.5 | Online Drying out system for Auto transformers | Lot | 2 | 30000 | 2700 | 2700 | 35400 | 70800 | LS | 70800
29.5 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System): Suitable for 220/132/33 KV, 160 MVA Auto Transformer as per Technical Specification & latest standard. | Set | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000 | Neulopoi estimate | 1180000
1: 30; 2: Installation & commissioning of Addressable type Smoke & Heat detection system: (As per TS, approved drawings and directions of Engineer-in-Charge.) Addressable type Smoke, Heat detector, Beam Detector, Reflector for Beam Detector for the following buildings including all accessories, the Addressable type Main control panel (Microprocessor based 10 loop fire alarm control panel) expandable upto 16 loops (minimum) fully networkable with each loop capable of taking 99 devices, alpha- numeric liquid crystal display. The panel shall be soft addressable type. The panel shall be able to give pinpoint location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have inbuilt rectifier, Loop cards, provision for externel & internal printer, LCD unit to indicate Fire/Fault Signal with address and analog output, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with SAS system, wall mounting loop powered addressable type hooter with all accessories, addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module, MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection, Junction boxes, response indicator, EOL resistance etc. Beam detector and reflectors shall be used only in the GIS halls. Agency shall submit drawings and design. Quantity of various items such as detector, RI, hooter, MCP etc. as per approved design. |  | 0
30.1 | 220 kV GIS Building | LOT | 1 | 300000 | 27000 | 27000 | 354000 | 354000 | LS | 354000
30.3 | Control room Building | LOT | 1 | 300000 | 27000 | 27000 | 354000 | 354000 | LS | 354000
1: 31; 2: MODIFICATION FOR EXISTING 33KV OUT-GOING FEEDERS (4No.) |  |  | 0 | 0
31.1 | Laying of 33KV XLPE Cables (1CX300Sqmm): Single core annealed copper cable with Aluminium corrugated sheath as per technical specification (From 33KV SY to nearest TPNODL end/RMU having each phase one run) | Km | 3.2 | 95392.5 | 8585.325 | 8585.325 | 112563.15 | 360202.08 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC |  | 360202.08 | 0
31.2 | Erection 33kV Out door type termination kit | No. | 32 | 4769.62 | 429.2658 | 429.2658 | 5628.1516 | 180100.8512 |  |  | 180100.8512 | 0
38.3 | HDG DP STRUCTURE FOR 33KV OUT GOING FEEDERS SUITABLE FOR TERMINATION OF 33KV CABLE: each shall comprise of [2X9.0Mtrs (ISBM:200x100mm(min) RS joist (beam), suitable channles(ISMC 100X50) for bracings & base for fixing 33kV Isolator & SA and suitable angles (L50X50X6) & different size steel plate of 10mm thick & suitable GI pipe for the isolator from the operating arm to operating mechanism box etc. Provision for support to the 33KV cable (both incoming & outgoint) along with stay set with required nuts & bolts | Set | 8 | 38157 | 3434.13 | 3434.13 | 45025.26 | 360202.08 |  |  | 360202.08 | 0
2: TOTAL ELECTRICAL WORKS (SCHEDULE-VIIB) OF S/S including GST@18%; 9= (8x4): 25486002.4531 |  | 24476948.1327

## VIIC PALASPANGA SS
ODISHA POWER TRANSMISSION CORPORATION LIMITED
PART -II | SCHEDULE VIIC _ CIVIL WORKS FOR 220/132KV GIS S/S AT PALASPANGA | NAME OF THE WORK:- Upgradation of 132/33kV GSS Palaspanga to 220/132/33kV GIS S/s and construction of 220KV D/C line from 400/220KV Basudevpur GSS to proposed 220/132KV GIS at Palaspanga with 02Nos. Of 220kV feeder bay extension at Turumunga GSS
220/132 kV GIS Substation Palaspanga: 220KV GIS Bay-5 Nos.(FDR-2,AUTO-2,B/C-1) 132KV AIS Bay-4Nos.(AUTO-2, FDR-2)
| DESCRIPTION OF ITEMS | Unit | Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | OGST@9% | CGST@9% | Total Unit Price | TOTAL PRICE IN RS, | PRICE REFERENCE
CIVIL ERECTION WORKS (PART-C) |  | 3 | 4 | 5 | 6 | 7 | 8 | 9=4x8 | 10
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 6500 | 5.87 | 0.5283 | 0.5283 | 6.9266 | 45022.9 | RC SS 25-27-1.10 | 45022.9
1.2 | Soil investigation : Supply of labour,T&P and other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. (15.00mtrs) | [8 empty] | 0
1.4.1 | Normal foundation (Boring up to 7.0m depth) | PER POINT | 3 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 101022.1836 | RC25-27 TL 1.5(a) | 101022.1836
1.4.2 | Under ream pile foundation (boring up to 15.0m depth) | PER POINT | 2 | 38609.34 | 3474.8406 | 3474.8406 | 45559.0212 | 91118.0424 | RC25-27 TL 1.5(b) | 91118.0424
2 | LEVELLING OF S/S AREA:Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification. | [8 empty] | 0
2.1 | Cutting of earth from substation area, filling & compaction of the usable earth in the substation area and disposal of the unusable soil beyond the substation area including all T & P, labour, carriage etc complete in all respect as per the direction of Engineer in Charge. (Total Volume= 26551.131cum) | [8 empty] | 0
2.1.1 | Soft/loose soil | Cum | 300 | 187.16 | 16.8444 | 16.8444 | 220.8488 | 66254.64 | RC-25-27-SS-1.20(i) | 66254.64
2.1.2 | Dense/ Compact soil | Cum | 400 | 296.35 | 26.6715 | 26.6715 | 349.693 | 139877.2 | RC-25-27-SS-1.20(ii) | 139877.2
2.1.3 | Soft/Disintegrated rock[not requiring blasting] | Cum | 250 | 608.29 | 54.7461 | 54.7461 | 717.7822 | 179445.55 | RC-25-27-SS-1.20(iii) | 179445.55
2.2.1 | Filling with borrowed earth & compaction: beyond the substation area & up to 100mtrs lead as per the direction of Engineer in Charge. | Cum | 1000 | 658.65 | 59.2785 | 59.2785 | 777.207 | 777207 | RC-25-27-SS-1.30(ii) | 777207
2.2..2 | Filling with borrowed earth beyond 100 mtrs lead as per the direction of Engineer in Charge. | Cum | 1200 | 1170.92 | 105.3828 | 105.3828 | 1381.6856 | 1658022.72 | RC-25-27-SS-1.30(iii) | 1658022.72
3 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod(FE-500), coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation, concreting, shoring & shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal / column structures and equipment support & others as per the technical specification and approved drawings. (RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. | [8 empty] | 0
3.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge. | [8 empty] | 0
3.1.1 | Normal Soil(SOFT/LOOSE) | Cum | 300 | 187.17 | 16.8453 | 16.8453 | 220.8606 | 66258.18 | RC-SS-25-27-2.10 | 66258.18
3.1.2 | Dence Compact/Muddy/ PS/FS- Soil | Cum | 2800 | 296.35 | 26.6715 | 26.6715 | 349.693 | 979140.4 | RC-SS-25-27-2.10 | 979140.4
3.1.3 | Soft Rock/Disintegrated rock (not requiring blasting) | Cum | 2500 | 662.88 | 59.6592 | 59.6592 | 782.1984 | 1955496 | RC-SS-25-27-2.10 | 1955496
3.1.4 | Hard Rock required blasting | Cum | 700 | 1091.81 | 98.2629 | 98.2629 | 1288.3358 | 901835.06 | RC-SS-25-27-2.10 | 901835.06
3.2 | Plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in for the above column/ equipment/marshalling box foundations for column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all required materials, labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 300 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 2144730.24 | RC-SS-25-27-3.2(i) | 2144730.24
3.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20), including supply of Labour all materials like cement, coarse and fine aggregates, shuttering, proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 1450 | 8751.26 | 787.6134 | 787.6134 | 10326.4868 | 14973405.86 | RC-SS-25-27-3.40(i) | 14973405.86
3.4 | Supply of steel different sizes(TATA/RINL/SAIL/JSW make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 200 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 15100323.12 | RC-SS-25-27-3.5(i) | 15100323.12
4 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge. | [8 empty] | 0
| (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | [8 empty] | 0
| (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | [8 empty] | 0
| (4) Fly ash Brickwork with fly ash Brick, plastering (1:6 Ratio) & curing, wherever required including the supply of labour, material, cement, etc. | [8 empty] | 0
| (5) For Cable trench sections 2-2, 3-3, 4-4, the outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. For section 1-1, the slabs shall be placed over the walls of the cable trench. (6)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. | [8 empty] | 0
| (7) Precast of RCC covers (1:1.5:3) with MS sheet(2mm) frame and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (8) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted. | [8 empty] | 0
| (9) Cable Trenches Inside The Control Room Shall Be Covered With M.S Chequered Plate(Duly Painted As Per Instruction Of Engg In Charge) Including Standard Support Stand {Hd Galvanised (M.S Joist , Channel, Angle). Stoppers shall be fixed at the underneath so that the chequered shall not be falling into the cable trench in any case. | [8 empty] | 0
| Cable trench with covers | [8 empty] | 0
4.1 | Section 1-1 ( Inside clearance- Wall to wall-1400mm, Top to bottom-1275mm, Concrete thickness- Wall-100mm, Bed/floor-100mm), The design is similar to Section 2-2, but the cable trays are arranged on both side of the cable trench. | Mtrs | 850 | 10000 | 900 | 900 | 11800 | 10030000 | Neulopoi Estimate | 10030000
4.2 | Section 2- 2 | Mtrs | 550 | 9000 | 810 | 810 | 10620 | 5841000 | Neulopoi Estimate | 5841000
4.3 | Section 3-3 | Mtrs | 500 | 9000 | 810 | 810 | 10620 | 5310000 | Neulopoi Estimate | 5310000
4.4 | Section 4-4 | Mtrs | 600 | 5000 | 450 | 450 | 5900 | 3540000 | Neulopoi Estimate | 3540000
4.5 | CABLE TRENCH FOR LAYING OF 220KV XLPE CABLE FOR 02NO. 220KV BAYS (For 8NO. UG CABLE from dead end tower to 220KV SY)= 1000MTR | Mtrs | 1000 | 10000 | 900 | 900 | 11800 | 11800000 | Neulopoi Estimate
4.6 | CABLE TRENCH FOR DIVERSION OF EXISTING 04NO. 33KV FEEDERS THROUGH UG CABLE Section 3-3 (UG cable for 2No. Feeders in one cable trench) | Mtrs | 400 | 10000 | 900 | 900 | 11800 | 4720000 | Neulopoi Estimate | 4720000
5 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | NOS | 2 | 200000 | 18000 | 18000 | 236000 | 472000 | Neulopoi Estimate | 472000
6 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing ) | [8 empty] | 0
6.1 | Road crossing for | [8 empty] | 0
6.2 | Section 1-1 | Lot | 1 | 400000 | 36000 | 36000 | 472000 | 472000 | Neulopoi Estimate | 472000
6.3 | Section 2- 2 | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Neulopoi Estimate | 295000
6.4 | Section 3-3 | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Neulopoi Estimate | 295000
7 | 220 KV GIS building: Design, engineering and construction of switch yard buildings including piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification (The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification. Shutter door of GIS building shall be motor operated. The (internal) area for GIS hall is 264 sqr. mtr appox. and shall accomodate the following: a. All the GIS equipment required for the project. b. Space for 02 Nos. of future GIS Bays c. LCC for the GIS bays (existing and future bays). d. Maintenance area inside GIS hall e. EOT crane Additional 88 sqr. mtr. (internal area) shall be constructed for the follwoing rooms. a. Relay Panel room for the above existing and future bays. b. AHU room Clear internal height of GIS Hall from FFL to Lowest obstruction at roof shall be 11 m minimum or as per actual requirement, whichever is higher. [Actual requirement of height of GIS hall shall be decided considering hook height of the crane as recommended by the GIS manufacturer and maintaining sufficient head clearance (minimum 1.8 meter) above the crane top level to the bottom of lowest obstruction at roof (roof beams). The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. This work includes anti-termite treatment, plinth protection, fire-fighting, electrification etc. to complete the work in full shape. | [8 empty] | 0
7.1 | Earthwork excavation (for any work, open cast or pile foundations including cost of boring etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 379200 | 34128 | 34128 | 447456 | 447456 | LS | 447456 | As the area of control room for 200KV is different of 400 KV control room , Rates are taken LS and not from Neulopoie estimate
7.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 222000 | 19980 | 19980 | 261960 | 261960 | LS | 261960
7.3 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. This also includes the pile (including cost of boring) or open foundation as per the design based on the actual soil condition of the site. | Lot | 1 | 4965568.0704 | 446901.1263 | 446901.1263 | 5859370.3231 | 5859370.3231 | LS | 5859370.3231
7.4 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 1825051.032 | 164254.5929 | 164254.5929 | 2153560.2178 | 2153560.2178 | LS | 2153560.2178
7.5 | Flooring of GIS room shall be epoxy paint of adequate thickness & Flooring adjacent panel rooms shall be with vitrified digital tiles with dado as per technical spec & approved drawings. | Lot | 1 | 1597531.032 | 143777.7929 | 143777.7929 | 1885086.6178 | 1885086.6178 | LS | 1885086.6178
7.6 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 1171291.032 | 105416.1929 | 105416.1929 | 1382123.4178 | 1382123.4178 | LS | 1382123.4178
7.7 | Provision of ceiling in the adjacent panel room area as per specification mentioned in the civil section & approved drawings. Provision of window blinders in the Panel room. | Lot | 1 | 1309531.032 | 117857.7929 | 117857.7929 | 1545246.6178 | 1545246.6178 | LS | 1545246.6178
7.8 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC with double layer glaze(taughned)of 6mm & windows shall have aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 1609051.032 | 144814.5929 | 144814.5929 | 1898680.2178 | 1898680.2178 | LS | 1898680.2178
7.9 | Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc. (of Legrand make),fixing of lighting fixtures & switchgear , Erection of all Lighting FIXTURES & LAMPS (LED), D.C emergency lighting (including supply). Internal Concealed wiring for Cable connection for Internet LAN, socket for using Telephone including supply of all materials,board,connectors etc as required should also be considered. Cabling for EOT crane including supply and installation of Switch Board panel required for EOT crane. This is as per approved drawing and direction of Engineer In charge. | Lot | 1 | 566138.772 | 50952.4895 | 50952.4895 | 668043.751 | 668043.751 | LS | 668043.751
7.1 | Provision of smoke and fire detection & Alarmsystem of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 235497.3984 | 21194.7659 | 21194.7659 | 277886.9301 | 277886.9301 | LS | 277886.9301
7.11 | Provision of rails & other arrangement including all type of Civil works for EOT crane. This is as per the standard practice adopted in GIS sub-station and as directed by the Engineer in Charge | Lot | 1 | 744000 | 66960 | 66960 | 877920 | 877920 | LS | 877920
7.12 | Provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. It includes supply of all types of materials of reputed make, labour etc to complete the work. | Lot | 1 | 49531.032 | 4457.7929 | 4457.7929 | 58446.6178 | 58446.6178 | LS | 58446.6178
7.13 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint (plastic emulsion). Refer the specification. | Lot | 1 | 505531.032 | 45497.7929 | 45497.7929 | 596526.6178 | 596526.6178 | LS | 596526.6178
7.14 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 72704.8656 | 6543.4379 | 6543.4379 | 85791.7414 | 85791.7414 | LS | 85791.7414
7.15 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 124901.136 | 11241.1022 | 11241.1022 | 147383.3405 | 147383.3405 | LS | 147383.3405
7.16 | Provision of Building earthing: Design,Engg,supply & erection with civil works for: (a) Protection from Lightning & (b) other conventional earthing | Lot | 1 | 68640 | 6177.6 | 6177.6 | 80995.2 | 80995.2 | LS | 80995.2
7.17 | Erection of EOT Crane for GIS building for 220 KV GIS station (5T/7T Capacity safe working load & minimum height of crane have shall be 9.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. | Lot | 1 | 116475.408 | 10482.7867 | 10482.7867 | 137440.9814 | 137440.9814 | LS | 137440.9814
8 | EXTENSION OF CONTROL ROOM CUM OFFICE BUILDING: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, bick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. It shall be ensured that the various room sizes are sufficient to accomodate the offered equipment. | [8 empty] | 0
8.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas)using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 19986.624 | 1798.7962 | 1798.7962 | 23584.2163 | 23584.2163 | LS | 23584.2163
8.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 1899793.95 | 170981.4555 | 170981.4555 | 2241756.861 | 2241756.861 | LS | 2241756.861
8.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 3104356.935 | 279392.1241 | 279392.1241 | 3663141.1833 | 3663141.1833 | LS | 3663141.1833
8.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 714237.2475 | 64281.3523 | 64281.3523 | 842799.952 | 842799.952 | LS | 842799.952
8.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 184279.77 | 16585.1793 | 16585.1793 | 217450.1286 | 217450.1286 | LS | 217450.1286
8.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 97061.694 | 8735.5525 | 8735.5525 | 114532.7989 | 114532.7989 | LS | 114532.7989
8.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 62337.995 | 5610.4195 | 5610.4195 | 73558.8341 | 73558.8341 | LS | 73558.8341
8.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 413866.1325 | 37247.9519 | 37247.9519 | 488362.0364 | 488362.0364 | LS | 488362.0364
8.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 52944.948 | 4765.0453 | 4765.0453 | 62475.0386 | 62475.0386 | LS | 62475.0386
8.12 | Supplying, fitting and Fixing Matt finish full body vitrified Acid proof tiles in floor and in dado upto lintel level of Battery room of 10MM thick, size 300mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 75000 | 6750 | 6750 | 88500 | 88500 | LS | 88500
8.13 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 31456.528 | 2831.0875 | 2831.0875 | 37118.703 | 37118.703 | LS | 37118.703
8.14 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 112165.08 | 10094.8572 | 10094.8572 | 132354.7944 | 132354.7944 | LS | 132354.7944
8.15 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 127666.182 | 11489.9564 | 11489.9564 | 150646.0948 | 150646.0948 | LS | 150646.0948
8.16 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 32408.47 | 2916.7623 | 2916.7623 | 38241.9946 | 38241.9946 | LS | 38241.9946
8.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 129429.9 | 11648.691 | 11648.691 | 152727.282 | 152727.282 |  | 152727.282
8.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (In toilets, rest rooms) | Lot | 1 | 70951.0725 | 6385.5965 | 6385.5965 | 83722.2655 | 83722.2655 |  | 83722.2655
8.19 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board, Vision glass panel (1.5ft x 1ft) and paisting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (All except in toilets & rest rooms) | Lot | 1 | 349150.818 | 31423.5736 | 31423.5736 | 411997.9652 | 411997.9652 |  | 411997.9652
8.2 | Supplying, fitting and fixing of M.S grills, Grill window (as per I.S. specification and as per approved drawings) in proper position in all floors as per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 118410.72 | 10656.9648 | 10656.9648 | 139724.6496 | 139724.6496 |  | 139724.6496
8.21 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [8 empty] | 0
8.21.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 313902.498 | 28251.2248 | 28251.2248 | 370404.9476 | 370404.9476 |  | 370404.9476
8.21.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 101515.94 | 9136.4346 | 9136.4346 | 119788.8092 | 119788.8092 |  | 119788.8092
8.21.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 9298.75 | 836.8875 | 836.8875 | 10972.525 | 10972.525 |  | 10972.525
8.22 | Supplying, fitting and fixing of Stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc with cost, conveyance, cost of all labour,labour cess, T&P etc. required for the work complete in all respect as per direction of the Engineer-in-charge. | Lot | 1 | 50521.27 | 4546.9143 | 4546.9143 | 59615.0986 | 59615.0986 |  | 59615.0986
8.23 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 100978.98 | 9088.1082 | 9088.1082 | 119155.1964 | 119155.1964 |  | 119155.1964
8.24 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 66936.46 | 6024.2814 | 6024.2814 | 78985.0228 | 78985.0228 |  | 78985.0228
8.25 | Providing and fixing of UPVC sliding windows in the Control room Building as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 574776 | 51729.84 | 51729.84 | 678235.68 | 678235.68 |  | 678235.68
8.26 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 173473.8 | 15612.642 | 15612.642 | 204699.084 | 204699.084 |  | 204699.084
8.27 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 12652.79 | 1138.7511 | 1138.7511 | 14930.2922 | 14930.2922 |  | 14930.2922
8.28 | Providing and fixing removable Raised/False Flooring System in the control room as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 364390 | 32795.1 | 32795.1 | 429980.2 | 429980.2 |  | 429980.2
8.29 | Plinth Potection for control room building as per the provided drawing and as per sepcification in TS. | Lot | 1 | 92194.88 | 8297.5392 | 8297.5392 | 108789.9584 | 108789.9584 |  | 108789.9584
8.3 | Construction of covered drain for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 330956.09 | 29786.0481 | 29786.0481 | 390528.1862 | 390528.1862 |  | 390528.1862
8.31 | Provision of PHD and other fittings of Jaguar make for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. Provision of rain water discharge pipes at different locations and two nos of over head water tank of 2000 ltrs capacity etc as per requirement and approved drawing. All bath room & toilet shall have water & termite proof doors and provision of sliding louvers with exhaust fan. | Lot | 1 | 388460.72 | 34961.4648 | 34961.4648 | 458383.6496 | 458383.6496 |  | 458383.6496
8.32 | Construction of septic tank and soak pit for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612 |  | 301871.612
8.34 | Provision for Electrical Work:Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 664911.546 | 59842.0391 | 59842.0391 | 784595.6243 | 784595.6243 |  | 784595.6243
8.35 | Provision of Fire alarm system for the control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 93565 | 8420.85 | 8420.85 | 110406.7 | 110406.7 |  | 110406.7
8.36 | Provision of false ceiling in the control room building (Control room, Office space, Cabins, rest rooms, Communication room, ACDC room & lobby) as per specification mentioned in the civil section & approved drawings including, relay panel room, office room, SAS room, conference room, transit room etc as per direction of the engineer in charge. | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 |  | 295000
9 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,colony area,approach road,control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. | [8 empty] | 0
9.1 | 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section (Inside the substation area) as per approved drawing. (Existing SY road to dismantle & to be reconstructed as per site requirement) | Mtrs | 60 | 9000 | 810 | 810 | 10620 | 637200 | Neulopoi Estimate | 637200
9.2 | Approach Road: 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section (from the Control room to main gate. Existing road to dismantle & to be reconstructed as per site requirement) | Mtrs | 180 | 9000 | 810 | 810 | 10620 | 1911600 | Neulopoi Estimate | 1911600
9.3 | 3.75 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 130 | 9000 | 810 | 810 | 10620 | 1380600 | Neulopoi Estimate | 1380600
10 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts,Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. All the drainage system shall be RCC type with M20 grade concrete. | [8 empty] | 0
10.1 | Storm water drain (RCC type) with slabs as per design above and subsequent approval [Wall thickness: 150 mm, Bed: 150 mm, Wall to wall diistance : 1100mm, Slab thickness: 100 mm] | Mtrs | 200 | 1500 | 135 | 135 | 1770 | 354000 | Neulopoi Estimate | 354000
10.2 | Road side drains(RCC type)-on each side of the 3.75 mtr and 7 mtr concrete roads as per design above & subsequent apporval | Mtrs | 700 | 1000 | 90 | 90 | 1180 | 826000 | Neulopoi Estimate | 826000
10.3 | Road-culverts, drain crossings | Lots | 3 | 525000 | 47250 | 47250 | 619500 | 1858500 | Neulopoi Estimate | 1858500
11 | Foundations for transformers: Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits (for 30% of the tfr oil capacity) below the transformer, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road ). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth. | [8 empty] | 0
11.1 | 160 MVA 220/132KV Auto Transformer | Nos | 2 | 952500 | 85725 | 85725 | 1123950 | 2247900 | paradeep plastic park | 2247900
12 | OIL SUMP PIT (150% of tfr oil capacity of one transformer): Design, engineering, supply of labour, material, equipments and construction of oil sump pit (RCC with ratio 1:1.5:3) including piling if any, all associated works & suitable connectivity oil collector pit provisioned near the transformer to the main oil sump pit and with provision of pump (suitable for handling transformer oil having capacity of 5 HP, with auto level control , including cabling, fixing of control gear & provision of a pump shed (of sufficient size to allow person to install, dismantle, make cable connection & maintain etc) over the oil sump pit). This oil sump pit shall be as per CIGRE standard for the oil collection pit inorder to separate oil from the water. Other piping with necessary valves arrangement shall also be provided to remove water from the oil sump pit. As per spec and approved drawing. | Nos | 1 | 462500 | 41625 | 41625 | 545750 | 545750 | paradeep plastic park | 545750
13 | FIRE FIGHTING (Nitrogen Injection Type Fire Prevention & Extinguishing System) All civil works related to NIFPES as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | [8 empty] | 0
13.1 | 160 MVA 220/132KV Auto Transformer | Lot | 2 | 100000 | 9000 | 9000 | 118000 | 236000 | paradeep plastic park | 236000
14 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls including piling if any as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant Fly ash Bricks).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Painting of the walls as per direction of the Engineer in charge. | Nos | 1 | 562500 | 50625 | 50625 | 663750 | 663750 | paradeep plastic park | 663750
15 | Anti-Weed Treatment :Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 4000 | 17.84 | 1.6056 | 1.6056 | 21.0512 | 84204.8 | Neulopoi Estimate | 84204.8
16 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:3:6 (M10) using 20 mm nominal metal over a lair of good quality river sand of 25 mm and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. Provision of pockets for water perculation into the yard atleast in two meters (both way) appart eachother for the entire PCC area & the pocket shall be provided with 75mm hard PVC pipe having minimum length of 300mm completely burried in the ground. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth from the Switch yard area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. | CUM | 2000 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 14298201.6 | RC-SS-25-27-3.2(i) | 14298201.6
17 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size metals consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 2500 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 9782967 | RC-SS-25-27-5.1 | 9782967
18 | Switch yard fencing: Providing and fixing of G.I Goat mesh fencing (the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. (Including for both new 220/132KV SY & the portion of existing 132KV & 33KV fencing to be dismantled as per site requirement) | Mtr | 600 | 7500 | 675 | 675 | 8850 | 5310000 | Badakushasthali 17 | 5310000
19 | SWITCHYARD GATE: Design, engineering, procurement of labour, material including all associated works for construction and fixing of switch yard gates and switchyard wicket gates as per specification and approved drawing. Switchyard gates shall have RCC pillars on both sides having open or pile founfdation and the gate shall be of stainless steel square pipes of 304 grade. The main entrance gate to switchyard shall have a wicket gate made of the same material. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth, PCC/RCC concreting, supply of cement aggregates, rebar rod etc as per the direction of Engineer In charge. It includes supply of all materials and all other associated works required to complete works as per specification and approved drawings and instruction of engineer in charge. | [8 empty] | 0
19.1 | Switchyard gate (On both sides of 7 m. road of switchyard) | NOS | 1 | 440726.832 | 39665.4149 | 39665.4149 | 520057.6618 | 520057.6618 | Badakusthasthali 7.1 | 520057.6618
19.2 | Wicket gate | NOS | 2 | 50908.54 | 4581.7686 | 4581.7686 | 60072.0772 | 120144.1544 | Badakusthasthali 7.2 | 120144.1544
20 | RETAINING WALL, STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification. RCC retaing wall of 1:1.5:3 M-20 grade where required. | [8 empty] | 0
20.1 | Excavation of all type of soil for stone pitching & Toe wall | Cum | 100 | 296.35 | 26.6715 | 26.6715 | 349.693 | 34969.3 | RC-22-25-27-1.2(i) | 34969.3
20.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 300 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 2144730.24 | RC-SS-25-27-3.2(i) | 2144730.24
20.3 | RR Masonry (1:5) | Cum | 500 | 3000.48 | 270.0432 | 270.0432 | 3540.5664 | 1770283.2 | RC-SS-25-27-6.3 | 1770283.2
20.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 200 | 7369.48 | 663.2532 | 663.2532 | 8695.9864 | 1739197.28 | RC-SS-25-27-3.1(i) | 1739197.28
20.5 | Excavation of all type of soil for Retaining wall | Cum | 500 | 319.88 | 28.7892 | 28.7892 | 377.4584 | 188729.2 | Badakushasthali | 188729.2
20.6 | P.C.C (1:3:6): Lean Concrete Grade M-10 for retaing wall | Cum | 200 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 1429820.16 | RC-SS-25-27-3.2(i) | 1429820.16
20.7 | RCC (1:1.5:3) M-20 or higher Grade as per site requirement | Cum | 300 | 8751.26 | 787.6134 | 787.6134 | 10326.4868 | 3097946.04 | RC-SS-25-27-3.4(i) | 3097946.04
20.8 | Supply of Steel (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 ) of different size (as per design) with cutting, bending, binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under ream Pile) including supply of binding wire with supply of steel rod ( FE-500 as per BIS-1786 ) for retaining wall | MT | 50 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 3775080.78 | RC-SS-25-27-3.5(i) | 3775080.78
21 | STORE SHED+OPEN STOCKYARD:Design, engineering, procurement of labour, material including all associated works for construction of store shed & open stockyard as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no store shed of floor size 10X10 mtr having Fly ash Brick walls and plastering with RCC roof. The flooring shall be of 75 mm thickness PCC (mix ratio1:2:4) over RR masonry works (as per standard practice of flooring). Provision of adequate nos of MS racks (proper paintings also to be done as per the direction of site in charge) for keeping the spare materials. The height of the shed shall be 4mtrs above the plinth. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Foundation shall be as per actual soil condition as per soil test, including piling where required. | Lot | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | Tentative
Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.Store shed door shall have access control system which is sensor operated with key card for entry. Log of all the persons accessing the store shed with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment (including supply of FFE) at strategic location suitable for wall hanging as per direction of engineer in charge. The MS Rod ( FE-500 as per BIS-1786 ) to be used in the building. (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)}
23 | PROVISION OF SAND BED:Design, engineering, procurement of labour, material including all associated works for construction of sand bed as per specification and approved drawing. This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The sand bed size shall be of 10m x 10m constructed with bricks, plastered & painted and the filled with river sand for storing of Transformer Bushings and other Insulators. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | Neulopoi estimate | 118000
24 | RCC Foundations for Octagonal Lighting Poles: Design, engineering, procurement of labour, material including piling if any, all associated works for construction of foundations for octagonal lighting poles as per approved drawings (RCC ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Pcc padding ratio (1:4:8). The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. | Nos | 40 | 10000 | 900 | 900 | 11800 | 472000 | Neulopoi estimate | 472000
25 | COLOUR CODING, BAY MARKING Etc: Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (Red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker (fluorescent type) may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | Neulopoi estimate | 236000
26 | MAIN GATE, WICKET GATE & SECURITY SHED (GATE COMPLEX): The Main gate, wicket gate and the Secirity shed shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation shall be designed as per actual site soil condition and shall be constructed as per approved drawing. | [8 empty] | 0
26.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil & rock as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the surplus earth/unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. This includes cost, conveyance of all materials, all labour, T&P articles required for the work, stacking the useful materials separately, including shoring, shuttering, propping and dewatering if required etc. | Lot | 1 | 35532.43 | 3197.9187 | 3197.9187 | 41928.2674 | 41928.2674 | Neulopoi estimate | 41928.2674
26.2 | Providing and lying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 30322.32 | 2729.0088 | 2729.0088 | 35780.3376 | 35780.3376 | Neulopoi estimate | 35780.3376
26.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundation & base of column work, all column, all beam, all pedestal, all lintel, all chajja, all slab, all projection etc.), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 443372.68 | 39903.5412 | 39903.5412 | 523179.7624 | 523179.7624 | Neulopoi estimate | 523179.7624
26.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, including cost of binding wires, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 339215.964 | 30529.4368 | 30529.4368 | 400274.8375 | 400274.8375 | Neulopoi estimate | 400274.8375
26.5 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 90680.42 | 8161.2378 | 8161.2378 | 107002.8956 | 107002.8956 | Neulopoi estimate | 107002.8956
26.6 | Providing 12 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 14705.25 | 1323.4725 | 1323.4725 | 17352.195 | 17352.195 | Neulopoi estimate | 17352.195
26.7 | Providing 16mm thick cement plaster ( 1:6) finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 16080.99 | 1447.2891 | 1447.2891 | 18975.5682 | 18975.5682 | Neulopoi estimate | 18975.5682
26.8 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 8988.68 | 808.9812 | 808.9812 | 10606.6424 | 10606.6424 | Neulopoi estimate | 10606.6424
26.9 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 8613.92 | 775.2528 | 775.2528 | 10164.4256 | 10164.4256 | Neulopoi estimate | 10164.4256
26.1 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 2071.9 | 186.471 | 186.471 | 2444.842 | 2444.842 | Neulopoi estimate | 2444.842
26.11 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 2782.87 | 250.4583 | 250.4583 | 3283.7866 | 3283.7866 | Neulopoi estimate | 3283.7866
26.12 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 6003.88 | 540.3492 | 540.3492 | 7084.5784 | 7084.5784 | Neulopoi estimate | 7084.5784
26.13 | Providing and fixing of 35mm thick WPC Door Shutter(Solid) with teak edge leaping to the periphery of the shutter with pilishing as per detailed drawing with including, all hardwares & fixtures, SS tower bolt(150mm), Door stopper, SS aldrop(250mm), SS handle(200mm length), ss handle (150mm length) & SS Butt hinges -125mm x 65mm x2.12mm .including cost, conveyance, loading, T&P required for the work etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 12476.16 | 1122.8544 | 1122.8544 | 14721.8688 | 14721.8688 | Neulopoi estimate | 14721.8688
26.14 | Supplying, fitting and fixing of M.S grills for windows, Main Gate, wicket gate etc. (as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge. (W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 | 136012.19 | 12241.0971 | 12241.0971 | 160494.3842 | 160494.3842 | Neulopoi estimate | 160494.3842
26.15 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [8 empty] | 0
26.15.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 36222.67 | 3260.0403 | 3260.0403 | 42742.7506 | 42742.7506 | Neulopoi estimate | 42742.7506
26.15.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 14163.64 | 1274.7276 | 1274.7276 | 16713.0952 | 16713.0952 | Neulopoi estimate | 16713.0952
26.15.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 5032.84 | 452.9556 | 452.9556 | 5938.7512 | 5938.7512 | Neulopoi estimate | 5938.7512
26.16 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 14502.83 | 1305.2547 | 1305.2547 | 17113.3394 | 17113.3394 | Neulopoi estimate | 17113.3394
26.17 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 6770.36 | 609.3324 | 609.3324 | 7989.0248 | 7989.0248 | Neulopoi estimate | 7989.0248
26.18 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 26280 | 2365.2 | 2365.2 | 31010.4 | 31010.4 | Neulopoi estimate | 31010.4
26.19 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 24914.7 | 2242.323 | 2242.323 | 29399.346 | 29399.346 | Neulopoi estimate | 29399.346
26.2 | GFRC Letter: Manufacturing, providing and installation of GFRC mouldings (Glass Fiber Reinforced Concrete) of approved make of thickness 230mm±5mm with pattern, design and colour of approved make to be fixed on/beteween RCC/ block work column or structural work with dry fixing method with all required T & P , manpower and all other material as required for completion of work in all respect. | [8 empty] | 0
i | Per Letter (450mm(h) x 40mm (d) x 50mm (w)) | Nos | 20 | 800 | 72 | 72 | 944 | 18880 | Neulopoi estimate | 18880
ii | OPTCL Logo | Nos | 1 | 1000 | 90 | 90 | 1180 | 1180 | Neulopoi estimate | 1180
26.21 | Electrical works of Main Gate, Wicket gate and Security Shed: As per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) for main gate, wicket gate & security shed to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 244423.62 | 21998.1258 | 21998.1258 | 288419.8716 | 288419.8716 |  | 288419.8716
27 | TRANSIT HOUSE (At Grid Colony): Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile (including cost of boring) as per soil conditions), construction of RCC super structure, bick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. | [8 empty] | 0
27.1 | Earthwork excavation (for any work, open cast or pile foundations including cost of boring etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 301211.02 | 27108.9918 | 27108.9918 | 355429.0036 | 355429.0036 | Neulopoi estimate | 355429.0036
27.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 260559.34 | 23450.3406 | 23450.3406 | 307460.0212 | 307460.0212 | Neulopoi estimate | 307460.0212
27.3 | Providing & laying Plain cement concrete (1:2:4) using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 1676113.36 | 150850.2024 | 150850.2024 | 1977813.7648 | 1977813.7648 | Neulopoi estimate | 1977813.7648
27.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 1676113.36 | 150850.2024 | 150850.2024 | 1977813.7648 | 1977813.7648 | Neulopoi estimate | 1977813.7648
27.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 2232941.16 | 200964.7044 | 200964.7044 | 2634870.5688 | 2634870.5688 | Neulopoi estimate | 2634870.5688
27.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 385242.08 | 34671.7872 | 34671.7872 | 454585.6544 | 454585.6544 | Neulopoi estimate | 454585.6544
27.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 177975.53 | 16017.7977 | 16017.7977 | 210011.1254 | 210011.1254 | Neulopoi estimate | 210011.1254
27.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 104882.42 | 9439.4178 | 9439.4178 | 123761.2556 | 123761.2556 | Neulopoi estimate | 123761.2556
27.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 52842.74 | 4755.8466 | 4755.8466 | 62354.4332 | 62354.4332 | Neulopoi estimate | 62354.4332
27.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 239188.36 | 21526.9524 | 21526.9524 | 282242.2648 | 282242.2648 | Neulopoi estimate | 282242.2648
27.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 51802.87 | 4662.2583 | 4662.2583 | 61127.3866 | 61127.3866 | Neulopoi estimate | 61127.3866
27.12 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 12140.52 | 1092.6468 | 1092.6468 | 14325.8136 | 14325.8136 | Neulopoi estimate | 14325.8136
27.13 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 65578.7 | 5902.083 | 5902.083 | 77382.866 | 77382.866 | Neulopoi estimate | 77382.866
27.14 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 123268.36 | 11094.1524 | 11094.1524 | 145456.6648 | 145456.6648 | Neulopoi estimate | 145456.6648
27.15 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 19217.93 | 1729.6137 | 1729.6137 | 22677.1574 | 22677.1574 | Neulopoi estimate | 22677.1574
27.16 | Providing,Fixing 16m thick Kota stone in floors treads or steps and landing on 20mm thick cement mortar (1:4) (1cement : 4 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. Providing,Fixing 16m thick Kota stone in dado ,riser on 12mm thick cement mortar (1:3) (1cement : 3 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. | Lot | 1 | 44895.68 | 4040.6112 | 4040.6112 | 52976.9024 | 52976.9024 | Neulopoi estimate | 52976.9024
27.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge. | Lot | 1 | 125157.9 | 11264.211 | 11264.211 | 147686.322 | 147686.322 | Neulopoi estimate | 147686.322
27.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. | Lot | 1 | 448363.08 | 40352.6772 | 40352.6772 | 529068.4344 | 529068.4344 | Neulopoi estimate | 529068.4344
27.19 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floorsas per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 91241.08 | 8211.6972 | 8211.6972 | 107664.4744 | 107664.4744 | Neulopoi estimate | 107664.4744
27.2 | Painting: Preparation of the brick wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | 10: Neulopoi estimate | 0
27.20.1 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 280619.13 | 25255.7217 | 25255.7217 | 331130.5734 | 331130.5734 | Neulopoi estimate | 331130.5734
27.20.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 65795.51 | 5921.5959 | 5921.5959 | 77638.7018 | 77638.7018 | Neulopoi estimate | 77638.7018
27.20.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 607.66 | 54.6894 | 54.6894 | 717.0388 | 717.0388 | Neulopoi estimate | 717.0388
27.21 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 71130.56 | 6401.7504 | 6401.7504 | 83934.0608 | 83934.0608 | Neulopoi estimate | 83934.0608
27.22 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 44317.83 | 3988.6047 | 3988.6047 | 52295.0394 | 52295.0394 | Neulopoi estimate | 52295.0394
27.23 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 212292 | 19106.28 | 19106.28 | 250504.56 | 250504.56 | Neulopoi estimate | 250504.56
27.24 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 73317.96 | 6598.6164 | 6598.6164 | 86515.1928 | 86515.1928 | Neulopoi estimate | 86515.1928
27.25 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 3348 | 301.32 | 301.32 | 3950.64 | 3950.64 | Neulopoi estimate | 3950.64
27.26 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8 mm having with water absorption less than 0.5% and conforming to IS:15622 of approved make in all colours and shades in for outdor floors such as footpath, courtyard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 coarse sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge. | Lot | 1 | 21505.13 | 1935.4617 | 1935.4617 | 25376.0534 | 25376.0534 | Neulopoi estimate | 25376.0534
27.27 | Supplying, fitting and fixing in position 16mm thick chequred tile of approved make and quality, colour and size in all floors at all height on 25mm thick bed of cement mortar of mix (1:1) laid in proper slope and gradient with screened and washed sharp sand for mortar and with Portland Slag Cement (PSC) grouted with neat white cement slurry with required quantities of pigments of approved marks watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 15829.76 | 1424.6784 | 1424.6784 | 18679.1168 | 18679.1168 | Neulopoi estimate | 18679.1168
27.28 | Plinth Potection for TRANSIT house as per the provided drawing and as per sepcification in TS. | Lot | 1 | 71707.51 | 6453.6759 | 6453.6759 | 84614.8618 | 84614.8618 | Neulopoi estimate | 84614.8618
27.29 | Construction of covered drain for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 257416.05 | 23167.4445 | 23167.4445 | 303750.939 | 303750.939 | Neulopoi estimate | 303750.939
27.3 | Provision of PH work for the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 570758.62 | 51368.2758 | 51368.2758 | 673495.1716 | 673495.1716 | Neulopoi estimate | 673495.1716
27.31 | Construction of septic tank and soak pit for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612 | Neulopoi estimate | 301871.612
27.32 | Provision of Electrical works the Transit house as per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 467669.25 | 42090.2325 | 42090.2325 | 551849.715 | 551849.715 | Neulopoi estimate | 551849.715
27.33 | Furnishings for Transit House: Supply and installation of the following items- 1. 55 inch Full HD LED TV set of Sony/LG/Samsung make with supply of Set up Box for the television unit with 1 year recharge from the date of commissioning (1set) 2.Durian/Godrej Sofa set (3+1+1) with center table for lobby (1 set) 3. King size cot with mattress & all other amenities like study table with 2 chair (Godrej) in all the bed rooms, bed sheets, pillow etc (Bombay Dyeing/Raymond Home) make. 2 Person wardrobe (Godrej Interio), hangers for hanging cloths in each room for storage of Baggages and Cloths etc. Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) - Total 4 sets for 4 guest rooms 4. Geyser-3 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make (4 set) 5. Dining table with 6 chairs of Durian/Godrej make (1 set) 6. Modular kitchen with exhaust chimney system, gas stove, and required utensils (1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons at a stretch) 7. RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make (1 set) 8. 3 star inverter compressor frost free Refrigerator of 230 Ltr or above capacity, double door type (LG/Samsung/Whirlpool/Godrej/Panasonic Make) (1 set) | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | Neulopoi estimate | 2360000
28 | BOUNDARY WALL (RCC structure, Brickwall type) | [8 empty] | 0
28.1 | BOUNDARY WALL: The boundary wall shall be constructed to a height of 2 mtrs above finished ground level of the substation area with 10” wide brick masonry work with RCC(1:1.5:3) ground tie beam to be rested on the RCC pillars (pillar to pillar distance @ 3mtrs) as per specification. | RM | 280 | 10000 | 900 | 900 | 11800 | 3304000 | Neulopoi estimate | 3304000
28.2 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil and rock as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plinth with sand, compaction, carriage & disposal of the unsuable earth material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | 3: Lot; 4: 1 | 0
28.3 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | 3: Lot; 4: 1 | 0
28.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations & bases of column, Beams, pedestal & column, rcc band etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour, Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | 3: Lot; 4: 1 | 0
28.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | 3: Lot; 4: 1 | 0
28.6 | Providing Brick work with Fly ash bricks 25cm x 12cm x 8cm size having crushing strength not less than 75 kg/cm2 with dimensional tolerance +/ - 2 percent in cement mortar (1:6) ( 1 cement: 6 sand), with all necessary projection, splay cutting, circular moulding, corbelling, etc., including cost of all materials, labour, conveyance, loading ,and unloadining, royalties, scaffolding, watering, curing, sundries, tools and plants, etc., as per the direction of the Engineer-in-charge. | 3: Lot; 4: 1 | 0
28.7 | Providing 16 mm. thick cement plaster in all floors at all height with cement mortar of mix (1:6) with portland slag cement (PSC) finished smooth to inside rough surface of brick masonry walls after racking out joints including watering and curing rounding of corners etc. complete with cost, coveyance, loading and unloading, royalties and ,es of all materials and cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. (Inside) | 3: Lot; 4: 1 | 0
28.8 | Painting of wall surface with weather coat two coats over a coat of primer of approved shade and quality of approved design after cleaning by watering & removing the dirts etc. to the surface to be painted including watering, curing, cost, conveyance of all materials, cost of all labour, brushes, T&P etc. and necessary scaffolding work complete as directed by the Engineer-in-charge. | 3: Lot; 4: 1 | 0
28.9 | Providing and fixing of GI 'Y' angles over the boundary wall at every 1m rigdly & sufficently (at least 200mm) grouted inside the wall for the support of the concertina wire. | 3: Lot; 4: 1 | 0
28.1 | Providing and fixing concertina coil fencing with punched tape concertina coil 600mm dia 10metr openable length (total length90m), having 50nos rounds per 6m length, upto 3m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165kg/sq.mm with tape (0.52mm thick) and weight 43.478 gm/meter. | 3: Lot; 4: 1 | 0
29 | BORE WELL : For the CR, Switchyard and water tank:Design, engineering, procurement of labour, material including all associated works for construction of two nos. bore wells for control room building including switch yard and colony quarters as per specification and approved drawing and instruction of Engineer in charge. This includes supply and fixing and commissioning of two nos 5 HP submersible water pump with starter and other protection. Construction of two nos pump house at ideal location for fixing of the electrical starter units. The pump house be of RCC roof & column and having walls of Brick masonary and plastering and painting with MS door having locking arrangement. The size of the room shall be 2.5mtrsX2.5 mtrs having height of 3 mtrs. as per approved drawing and specification. There shall be approach road to the pump house. This includes supply of materials,labours and T&P & excavation of all type of soils including rock and disposal of excess materials as per instruction of Engineer Incharge. Supply & laying of LV XLPE 3.5CX.35 sqmm cable from ACDB to pump house, control gear & earthing of the system etc to complete the scheme as per approved drawing & instruction of Engineer-in charge. | Nos | 1 | 390000 | 35100 | 35100 | 460200 | 460200 | Badakushasthali 21 | 460200
30 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: As per site condition of the substation and approval of the gardening layout. The qty may vary as per the approved layout and instrcution of engineer in charge. | [8 empty] | 0
30.1 | Provision of gardens/ lawn area with garden grass in front of the control room building & other areas that can be developed as a garden as per the site Engineer's instruction. This include the all required work including the soil treatment for laying of the lawn grass. | sqm | 600 | 590 | 53.1 | 53.1 | 696.2 | 417720 | Neulopoi estimate | 417720
30.2 | Motorised fountain at a suitable location as per instrcution of Engineer in charge. | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Neulopoi estimate | 59000
30.3 | Sprinkler arrangement in the lawn to cover all the lawn area and water tap arrangement at different location to all areas of plantation. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Neulopoi estimate | 59000
30.4 | Flowering plants (Rose, jasmine, hibiscus or as per instruction of Engineer in Charge at least 50 each | Nos | 200 | 50 | 4.5 | 4.5 | 59 | 11800 | Neulopoi estimate | 11800
30.5 | Fruit bering Non Fruit bearing Plants (Mango, guava, Neem, Acacia) as per instruction of Engineer in Charge. 25 nos of each type of trees to be plantedin the free areas immediately after the substation layout paln is finalised. It must be ensured that the plants survive till hand over. Therefore, proper care shall be taken by the contractor. | Nos | 100 | 120 | 10.8 | 10.8 | 141.6 | 14160 | Neulopoi estimate | 14160
30.6 | Decorative Plants for Lawn/garden (varieties of Hedge, thuja) as per instruction of Engineer in Charge | Nos | 150 | 50 | 4.5 | 4.5 | 59 | 8850 | Neulopoi estimate | 8850
30.7 | Decorative plants (foxtail palm of at least 5 ft height) for both side of the 7m road from the main gate as per instruction of the Engineer in charge. | Nos | 100 | 1030 | 92.7 | 92.7 | 1215.4 | 121540 | Neulopoi estimate | 121540
30.8 | Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags as per the direction of Engineer incharge. | Nos | 1 | 8402.78 | 756.2502 | 756.2502 | 9915.2804 | 9915.2804 | Neulopoi estimate | 9915.2804
31 | Breaking of existing concrete foundation for replacement/ renovation work, clearing of debris from SY as per the instruction of Enigineer-in-charge (including supply of T&P, labour etc, necessary for the work) | [8 empty] | 0
31.1 | Existing close store shed (Approx size of 50mX15m) | Cum | 360 | 4152.24 | 373.7016 | 373.7016 | 4899.6432 | 1763871.552 | RC 25-27-3.60 | 1763871.552
31.2 | Existing open store yard (Approx size of 55mX3mX0.5m) | Cum | 82.5 | 4152.24 | 373.7016 | 373.7016 | 4899.6432 | 404220.564 | RC 25-27-3.60
31.3 | Existing approach road & SY road | Cum | 120 | 4152.24 | 373.7016 | 373.7016 | 4899.6432 | 587957.184 | RC 25-27-3.60 | 587957.184
31.4 | Breaking of existing 3-pole & 4-pole MS structures of 33kV Out going feeders | LS | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | LS | 59000
| TOTAL OF CIVIL WORKS (Schedule-VIIC) including GST@18% | 9=4x8: 195805693.1945 | 178830643.8945
Note on B60: OPTCL: Justification of price is not available

## SUMMERY PALASPANGA SS
S U M M A R Y (PART-A) | SUMMARY
NAME OF THE WORK:- Construction of proposed 220/132KV GIS at Palaspanga
Sl.No. | Description | Amount (In INR)
1 | Total Cost of materials (VIIA for Substation) | 736656456.9897
2 | Stock,Storage & Insurance(@3% on Sl.No-1 | 22099693.7097
3 | Sub-Total(1+2) | 758756150.6994
4 | Contigency 3% on Sl.No.3 | 22762684.521
5 | T&P cost @ 2% on Sl.No. 3 | 15175123.014
6 | Transportation @5% on Sl.No.3 | 37937807.535
7 | Sub-Total cost of materials | 834631765.7693
8 | TOTAL of ELECTRICAL WORKS (Erection Charges) (SCHEDULE-VIIB (FOR SUBSTATION)) | 25486002.4531
9 | TOTAL of Civil Works (Erection Charges) SCHEDULE-VIIC (FOR SUBSTATION) | 195805693.1945
10 | Sub-Total (3 to 9) = | 1055923461.4169
11 | Statutory fees | 0
12 | TOTAL COST OF SUB-STATION | 1055923461

## Consolidated (hidden)
Estimate with supply Power Transformer & Statutory Fees
Sl. No. | Description | S/S | Line | Total
1 | Total Cost of Materials | 736656456.9897 | #REF! | #REF!
2 | Stock, storage & Insurance(3% on Sl. No.-01) | 22099693.7097 | #REF! | #REF!
3 | Sub-Total(1+2) | 758756150.6994 | #REF! | #REF!
4 | Contigency @ 3% on sl. No.03 | 22762684.521 | #REF! | #REF!
5 | T&P Cost @ 2% on Sl. No.03 | 15175123.014 | #REF! | #REF!
6 | Transportation @ 5% on Sl. NO. 03 | 37937807.535 | #REF! | #REF!
7 | Sub - Total Cost of Materials | 834631765.7693 | #REF! | #REF!
10 | Tree cutting @20000/- per Kms |  | #REF! | #REF!
11 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection. |  | #REF! | #REF!
12 | Cost towards Erection | 25486002.4531 | #REF! | #REF!
13 | Cost towards Civil | 195805693.1945 | #REF! | #REF!
14 | Total Cost of Supply, Erection and Civil | 1055923461.4169 | #REF! | #REF!
Estimate without supply Power Transformer & Statutory Fees
Sl. No. | Description | S/S | Line | Total
1 | Total Cost of Materials | 367801368.5214 | #REF! | #REF!
2 | Stock, storage & Insurance(3% on Sl. No.-01) | 11034041.0556 | #REF! | #REF!
3 | Sub-Total(1+2) | 378835409.577 | #REF! | #REF!
4 | Contigency @ 3% on sl. No.03 | 11365062.2873 | #REF! | #REF!
5 | T&P Cost @ 2% on Sl. No.03 | 7576708.1915 | #REF! | #REF!
6 | Transportation @ 5% on Sl. NO. 03 | 18941770.4789 | #REF! | #REF!
7 | Sub - Total Cost of Materials | 416718950.5347 | #REF! | #REF!
8 | Tree cutting @20000/- per Kms |  |  | 0
9 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection. |  |  | 0
10 | Cost towards Erection | 25486002.4531 | #REF! | #REF!
11 | Cost towards Civil | 195805693.1945 | #REF! | #REF!
12 | Total Cost of Supply, Erection and Civil | 638010646.1822 | #REF! | #REF!
Estimate without supply Power Transformer & Statutory Fees other cost such as stck, storage, insurance, contingency, T&P cost and Transportation
Sl. No. | Description | S/S | Line | Total
1 | Total Cost of Materials | 367801368.5214 | #REF! | #REF!
2 | Stock, storage & Insurance(3% on Sl. No.-01)
3 | Sub-Total(1+2) | 367801368.5214 | #REF! | #REF!
4 | Contigency @ 3% on sl. No.03
5 | T&P Cost @ 2% on Sl. No.03
6 | Transportation @ 5% on Sl. NO. 03
7 | Sub - Total Cost of Materials | 367801368.5214 | #REF! | #REF!
8 | Tree cutting @20000/- per Kms |  |  |  | 367801368.5214
9 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection. |  |  |  | 368855088.4683
10 | Cost towards Erection | 25486002.4531 | #REF! | #REF!
11 | Cost towards Civil | 195805693.1945 | #REF! | #REF!
12 | Total Cost of Supply, Erection and Civil | 589093064.1689 | #REF! | #REF!
1 | Estimate for Tenedring | #REF!
2 | EMD | #REF!
3 | Tender Paper cast | 29500
4 | Tender Processing Fees | 5900
5 | MAAT (considering 2 years of completion period) | #REF!
6 | Liquid Asset | #REF!
7 | Bid Capacity | #REF!

## VIIA LINE
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 220 KV Transmission line from proposed 400/220KV Basudevpur GSS to Palaspanga GSS along with 2Nos. 220KV Bays extension at proposed 400/220kV Unchabali GSS
Conductor- ACSR ZEBRA |  | Total length of over head line- 25 RKM. Approx.
Earth wire- OPGW |  | Total towers- 85
No. of Ciruit- DC line on DC tower |  | Angle towers- 54Nos., Composite Tower=01No.
SCHEDULE-VIIA-SUPPLY (FOR 220 KV UNCHABALI-PALASPANGA D/C LINE)
Sl. No. |  | Unit | Qnty | IN INR
| DESCRIPTION OF ITEMS |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3 | 4 | 5 |  |  |  | 7=4*6
1 | SUPPLY of following type tested Lattice type Galvanized steel Tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | TOWER SUPER STRUCTURES
1.1.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.250 MT) - 30Nos. | MT | 127.5
1.1.1.1 | +3 EXTENSION ( 0.751 MT) - 14Nos. | MT | 10.514
1.1.1.2 | +6 EXTENSION ( 1.497 MT) - 11Nos. | MT | 16.467
1.1.2 | OB TYPE (30 deg ANGLE ) TOWERS ( 6.343 MT) - 22Nos. | MT | 139.546
1.1.2.1 | +3 EXTENSION ( 1.336 MT) - 13Nos. | MT | 17.368
1.1.2.2 | +6 MTR EXTENSION to OB ( 2.321 MT)- 4Nos. | MT | 9.284
1.1.3 | OC TYPE (60 deg ANGLE ) TOWERS ( 9.014) - 28Nos. | MT | 252.392
1.1.3.1 | +3 EXTENSION ( 1.468 MT) - 11NOS. | MT | 16.148
1.1.3.2 | +6 EXTENSION ( 2.618 MT) - 7NOS. | MT | 18.326
1.1.3.2 | +15 EXTENSION ( 2.618 MT) - 3NOS. | MT | 7.854
1.1.4 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 4 NOS. | MT | 49.752
1.1.4.1 | +6 EXTENSION ( 4.161MT) - 4 NOS. | MT | 16.644
1.5 | MA TYPE MULTI CIRCUIT ( HT-6.303+MS-7.981= 23.001 MT +STUB 1.309 MT) - 20 NOS. | MT
1.5.1 | HT materials for 0 mtr Extension | MT
1.5.2 | MS materials for 0 mtr extension | MT
1.5.3 | +3 EXTENSION ( HT-0.723+ MS-0.944 MT) - 6NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.3 | +6 EXTENSION ( HT-1.186+ MS-1.711 MT) - 4NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5 | MB TYPE ( ANGLE TOWERS) MULTI CIRCUIT ( HT-10.654+MS-12.347= 23.001 MT +STUB 1.309 MT) - 0No. | MT
1.5.1 | HT materials for 0 mtr Extension | MT
1.5.2 | MS materials for 0 mtr extension | MT
1.5.3 | +3 EXTENSION ( HT-1.002+ MS-1.769 MT) -NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.3 | +6 EXTENSION ( HT-1.729+ MS-2.874 MT) -NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.6 | +9 EXTENSION ( 6.488 MT) - 1 NO. | MT
1.5.7 | HT materials for +9 extension (2.402MT) | MT
1.5.8 | MS materials for +9 extension (4.086MT) | MT
1.6 | MC TYPE ( ANGLE TOWERS) MULTI CIRCUIT - (HT-15.658+MS-13.341=28.999MT)- 10Nos. | MT
1.6.2 | HT materials for +0 extension 15.658 MT | MT
1.6.3 | MS materials for +0 extension 13.341 MT | MT
1.6.4 | +3 EXTENSION ( HT-1.559+ MS-2.037 MT) - 3 Nos. | MT
1.6.5 | HT materials for +6 extension 1.559 MT | MT
1.6.6 | MS materials for +6 extension 2.037 MT | MT
1.6.4 | +6 EXTENSION ( HT-2.707+ MS-3.233 MT) - 02 NO. | MT
1.6.5 | HT materials for +6 extension 2.707 MT | MT
1.6.6 | MS materials for +6 extension 3.233 MT | MT
1.6 | DD Type(Composit) Tower (Nominal unit weight- 7.690MT+0.592MT)-1 No | MT | 8.282
1.2 | STUBS & CLEATS
1.2.1 | OA TYPE( 0.230 MT)- 30 | MT | 6.9
1.2.2 | OB TYPE ( 0.436 MT)-22 | MT | 9.592
1.2.3 | OC TYPE ( 0.774 MT)-28 | MT | 21.672
1.2.4 | OC+15 TYPE ( 0.697 MT)- 3 | MT | 2.091
1.2.4 | UR TYPE ( 0.697 MT)- 4 | MT | 2.788
1.2.5 | DD TYPE ( 0.592 MT)- 1 | MT | 0.592
1.3 | TEMPLATES
1.3.1 | OA ( 0.580 MT)- 4Nos. | MT | 2.32
1.3.2 | OB ( 0.794 MT) -4Nos. | MT | 3.176
1.3.3 | OC ( 0.962 MT) - 4Nos. | MT | 3.848
1.3.4 | UR+6 ( 1.476 MT)- 01Nos. | MT | 1.476
1.3.5 | DD ( 0.757 MT)- 01Nos. | MT | 0.757
1.4 | WEIGHT OF THE STRUCTURES (including Towers, stubs & cleats) | MT | 733.712 | 100640.49 | 9057.6441 | 9057.6441 | 118755.7782 | 87132539.5347 | Tower structure R/C No.767, Dt.24.06.2025 of SrGM, CPC
1.5 | MS enamel painted templates | MT | 11.577 | 69832.18 | 6284.8962 | 6284.8962 | 82401.9724 | 953967.6345
1.6 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 37.2645 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 5213355.3881
2 | Supply of the following tower accessories as per technical specification.
2.1 | EARTHING DEVICE | Nos. | 170 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 457564.588 | CD 24-25 Line sl.8
2.2 | DANGER BOARD | Nos. | 85 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 23748.031 | CD 24-25 Line sl.9
2.3 | NUMBER PLATE | Nos. | 170 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 25953.628 | CD 24-25 Line sl.10
2.4 | PHASE PLATE | Nos. | 510 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 60733.656 | CD 24-25 Line sl.11
2.5 | BIRD GUARD | Nos. | 180 | 524.7398 | 47.2266 | 47.2266 | 619.193 | 111454.7412 | LOA NO.137,Dt.16.02.23 (Turumunga -Dhenkikote), Line 2.5
2.6 | ANTICLIMBING DEVICE | Nos. | 85 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 441343.069 | CD 24-25 Line sl.13
2.7 | CIRCUIT PLATE | Nos. | 170 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 20244.552 | CD 24-25 Line sl.12
2.8 | 75X10 MM GI FLAT | MT | 20 | 100640.49 | 9057.6441 | 9057.6441 | 118755.7782 | 2375115.564 | CD 24-25-Line-4
3 | Supply of following POWER CONDUCTORS as per the technical specification
3.1 | ACSR ZEBRA | Kms. | 164.43 | 363162.06 | 32684.5854 | 32684.5854 | 428531.2308 | 70463390.2804 | CD 24-25 Line sl.18
4 | POWER CONDUCTOR ACESSORIES (For ACSR ZEBRA)
4.1 | VIBRATION DAMPER | Nos. | 1014 | 756.44 | 68.0796 | 68.0796 | 892.5992 | 905095.5888 | CD 24-25 Line sl.29
4.2 | MID SPAN JOINT | Nos. | 100 | 797.33 | 71.7597 | 71.7597 | 940.8494 | 94084.94 | CD 24-25 Line sl.34
4.3 | Repair Sleeve | Nos. | 100 | 324.04 | 29.1636 | 29.1636 | 382.3672 | 38236.72 | CD 24-25 Line sl.40
4.4 | Performed Armoured Rod | Set | 180 | 1167.1 | 105.039 | 105.039 | 1377.178 | 247892.04 | CD 24-25 Line sl.26
5 | Supply of the following 220KV SILICON COMPOSITE LR INSULATOR as per the technical specification and as per the instruction of the Engineer in charge.
5.1 | 220KV LOND ROD 160 KN SILICON COMPOSITE INSULATOR | Nos. | 948 | 5058.42 | 455.2578 | 455.2578 | 5968.9356 | 5658550.9488 | CD 24-25 Line sl.64
5.2 | 220KV LOND ROD 90 KN SILICON COMPOSITE INSULATOR (INCLUDING PILOT INSULATOR) | Nos. | 270 | 4219.59 | 379.7631 | 379.7631 | 4979.1162 | 1344361.374 | CD 24-25 Line sl.63
6 | Supply of the following hard ware fittings suitable for ACSR Zebra conductors as per the technical specification.
6.1 | Single Suspension Hard wares fittings (AGS Type, Including Armoured Rod) (1x120kN) | Nos. | 120 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 382131.672 | CD 24-25 Line sl.15
6.2 | Double suspension Hard wares fittings (2x120kN) | Nos. | 60 | 4566.27 | 410.9643 | 410.9643 | 5388.1986 | 323291.916 | CD 24-25 Line sl.16
6.3 | Single Tension Hardware fittings (1 x160kN) | Nos. | 360 | 2076.13 | 186.8517 | 186.8517 | 2449.8334 | 881940.024 | CD 24-25 Line sl.17
6.4 | Double tension Hardware fittings (2x160kN) | Nos. | 294 | 4735.96 | 426.2364 | 426.2364 | 5588.4328 | 1642999.2432 | CD 24-25 Line sl.18
6.5 | “D” Shackle | Nos. | 654 | 310 | 27.9 | 27.9 | 365.8 | 239233.2
6.6 | Hanger | Nos. | 180 | 592 | 53.28 | 53.28 | 698.56 | 125740.8
6.7 | U'-Bolt. | Nos. | 120 | 137 | 12.33 | 12.33 | 161.66 | 19399.2
7 | Supply of OPGW Cable & Hardware fittings
7.1 | Supply of OPGW(DWSM) Fibre Optic Cable 24F | KM | 25.375 | 190400 | 17136 | 17136 | 224672 | 5701052 | CD24-25-TEL-23
7.2 | Hardware set for 24F OPGW as per the list below required per Km. like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Earth bond,Link plates | KM | 25 | 22597.72 | 2033.7948 | 2033.7948 | 26665.3096 | 666632.74 | CD 24-25-TEL-24
7.3 | Joint Box (splice enclosure),24F | NO. | 10 | 4525.2 | 407.268 | 407.268 | 5339.736 | 53397.36 | CD 24-25-TEL-27
| TOTAL SCHEDULE-VII A (FOR 220 KV UNCHABALI-PALASPANGA D/C LINE) | [6 empty] | 185603450.4337
| Estimator |  |  | Deputy General Manager (Elect.),
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar
Weight of different type G.I Nuts and Bolts for the above structures (1.13*3+170.28*3+25062+50.02+1.19*16+212.37*16+43.4*10+1.34*25+301.55*25+50.5*13+98.34*4+3.88*7+346.25*7+42.35*3+71.04*3+9.86*9+401.21*9+97.28*8+5.03*10+346.25*10+188.29*4+304.66*6+14.65*3+984.84*3+113.8+19.74+18.84+23.28+35.57+35.04+25.14+41.97*2+35=29,814.63kg)

## VIIB VIIC LINE
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 220 KV Transmission line from proposed 400/220KV Basudevpur GSS to Palaspanga GSS along with 2Nos. 220KV Bays extension at proposed 400/220kV Unchabali GSS
Conductor- ACSR ZEBRA |  | Total length of over head line- 25 RKM. Approx.
Earth wire- OPGW |  | Total towers- 85
No. of Ciruit- DC line on DC tower |  | Angle towers- 54Nos., Composite Tower=01No.
PART SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (220KV TURUMUNGA-BASUDEVPUR D/C LINE ) | [9 empty] | 49.4
Sl. No. | DESCRIPTION OF ITEMS | Unit | QTY | IN INR
| DESCRIPTION OF ITEMS |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4X8 | 10
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. This includes supply of all labourers, T&P, head loading of all type of structures, & other materials required for erection. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1.1 | TOWER SUPER STRUCTURES
1.1.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.250 MT) - 30Nos. | MT | 127.5
1.1.1.1 | +3 EXTENSION ( 0.751 MT) - 14Nos. | MT | 10.514
1.1.1.2 | +6 EXTENSION ( 1.497 MT) - 11Nos. | MT | 16.467
1.1.2 | OB TYPE (30 deg ANGLE ) TOWERS ( 6.343 MT) - 22Nos. | MT | 139.546
1.1.2.1 | +3 EXTENSION ( 1.336 MT) - 13Nos. | MT | 17.368
1.1.2.2 | +6 MTR EXTENSION to OB ( 2.321 MT)- 4Nos. | MT | 9.284
1.1.3 | OC TYPE (60 deg ANGLE ) TOWERS ( 9.014) - 28Nos. | MT | 252.392
1.1.3.1 | +3 EXTENSION ( 1.468 MT) - 11NOS. | MT | 16.148
1.1.3.2 | +6 EXTENSION ( 2.618 MT) - 7NOS. | MT | 18.326
1.1.4 | +15 EXTENSION ( 2.618 MT) - 3NOS. | MT | 7.854
1.1.4.1 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 4 NOS. | MT | 49.752
| +6 EXTENSION ( 4.161MT) - 4 NOS. | MT | 16.644
1.2 | DD Type(Composit) Tower (Nominal unit weight- 7.690MT+0.592MT)-1 No | MT | 8.282
1.3 | STUBS & CLEATS
1.3.1 | OA TYPE( 0.230 MT)- 30 | MT | 6.9
1.3.2 | OB TYPE ( 0.436 MT)-22 | MT | 9.592
1.3.3 | OC TYPE ( 0.774 MT)-28 | MT | 21.672
1.3.4 | OC+15 TYPE ( 0.697 MT)- 3 | MT | 2.091
1.3.5 | UR TYPE ( 0.697 MT)- 4 | MT | 2.788
1.3.6 | DD TYPE ( 0.592 MT)- 1 |  | 0.592
1.4 | TEMPLATES
1.4.1 | OA ( 0.580 MT)- 4Nos. | MT | 17.4
1.4.2 | OB ( 0.794 MT) -4Nos. | MT | 17.468
1.4.3 | OC ( 0.962 MT) - 4Nos. | MT | 29.822
1.4.4 | UR+6 ( 1.476 MT)- 01Nos. | MT | 5.904
1.4.5 | DD ( 0.757 MT)- 01Nos. | MT | 0.757
1.5 | Erection of Super structures | MT | 690.077 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 6014466.2927 | RC25-27 TL 9.(i)
1.6 | Fixing of stub and Template (MS enamel painted templates and stubs, cleats) | MT | 114.986 | 5738.91 | 516.5019 | 516.5019 | 6771.9138 | 778675.2802 | RC25-27 TL .6.1
1.6 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 37.2645 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 324783.7248 | RC25-27 TL 9.(i)
2 | Erection of the following tower accessories as per technical specification. | [6 empty] | 0
2.1 | EARTHING OF TOWER: Pipe type earthing including cost of bentonate compound and good borrowed earth where necessary in accordance with IS:3043-1966 and with supply of all T&P and Labour, with excavation of Morrum and laterite layer and back filling with good borrowed earth.- i)Without cost of earthing pipe (50mm Dia 3050mm length medium gauge) and GI flat | Nos. | 170 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 616197.062 | RC25-27 TL 8.1.(i)
2.2 | DANGER BOARD | Nos. | 85 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 15994.841 | RC25-27 TL H.11.(ii)
2.3 | NUMBER PLATE | Nos. | 170 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 31989.682 | RC25-27 TL H.11.(i)
2.4 | PHASE PLATE | Nos. | 510 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 95969.046 | RC25-27 TL H.11.(iii)
2.5 | BIRD GUARD | Nos. | 180 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 33871.428 | RC25-27 TL H.11.(iv)
2.6 | ANTICLIMBING DEVICE | Nos. | 85 | 3441.28 | 309.7152 | 309.7152 | 4060.7104 | 345160.384 | RC25-27 TL H.11.(v)
2.7 | CIRCUIT PLATE | Nos. | 170 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 31989.682 | RC25-27 TL H.11.(iii)
3 | Hoisting and fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire & OPGW in the proposed lines with all required accessories including scaffolding/other required arrangements for 33 KV,11 KV, LT , P&T lines, NH/roads, railway line, river etc and using own required T&P and compression jointing machines etc. as per the direction of Engineer in charge. | [6 empty] | 0
3.1 | ACSR ZEBRA | RKM | 25 | 95684.03 | 8611.5627 | 8611.5627 | 112907.1554 | 2822678.885 | RC25-27 TL-10.10.I.b
| Additional charges for stringing EHT line crossing/railway/ National highway crossing | RKM | 0 | 33489.42 | 3014.0478 | 3014.0478 | 39517.5156 | 0 | RC25-27 TL-10.10.I.b(i)
4 | ERECTION OF OPGW CABLE | [6 empty] | 0
4.1 | 24F/48F OPGW stringing without supply of required HWF, tension assembly set, suspension assembly set, vibration damper set etc.(Under offline condition) | KM | 25 | 45000 | 4050 | 4050 | 53100 | 1327500 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
| TOTAL OF ELECTRICAL WORKS (PART-A) | [6 empty] | 12439276.3077
CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey - Making walkover survey ascertaining feasibile route and marking on TOposheet, preparation of route alignment | KM. | 25 | 5036 | 453.24 | 453.24 | 5942.48 | 148562 | RC25-27 TL 1.1
1.1 | Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 25 | 14268.67 | 1284.1803 | 1284.1803 | 16837.0306 | 420925.765 | RC25-27 TL 1.2
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 25 | 6714.67 | 604.3203 | 604.3203 | 7923.3106 | 198082.765 | RC25-27 TL 1.4
1.3 | Preparation of land schedule on revenue (if required)maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval.Detail GIS (Geographical Information System) of towers to be included. | KM. | 25 | 10911.34 | 982.0206 | 982.0206 | 12875.3812 | 321884.53 | RC25-27 TL 1.3
1.4 | Soil Testing in complete shape along with submission of report etc. | [6 empty] | 0
1.4.1 | Normal foundation (Boring up to 7.0m depth) | Per Loc. | 45 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 1515332.754 | RC25-27 TL 1.5(a)
1.4.2 | Under ream pilee foundation (boring up to 15.0m depth) | Per Loc. | 10 | 38609.34 | 3474.8406 | 3474.8406 | 45559.0212 | 455590.212 | RC25-27 TL 1.5(b)
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS | [6 empty] | 0
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposal of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge ( Total 14300 CUM) | [6 empty] | 0
2.1.1 | Soft/Loose soil | CUM | 1430 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 394800.978 | RC25-27 TL 2.(i)
2.1.2 | Dense / compact soil | CUM | 2860 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 1236999.192 | RC25-27 TL 2.(ii)
2.1.3 | Partially submerged soil | CUM | 2860 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 1421229.524 | RC25-27 TL 2.(vi)
2.1.3 | Fully submerged soil | CUM | 715 | 421.13 | 37.9017 | 37.9017 | 496.9334 | 355307.381 | RC25-27 TL 2.(v)
2.1.4 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 2145 | 701.88 | 63.1692 | 63.1692 | 828.2184 | 1776528.468 | RC25-27 TL 2.(iii)
2.1.5 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 4290 | 1403.75 | 126.3375 | 126.3375 | 1656.425 | 7106063.25 | RC25-27 TL 2.(iv)
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. This includes the open cast foundations, Piles, Pile cappings, risers, chimney, rivetment works etc. | [6 empty] | 0
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 300 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 2257613.76 | RC25-27 TL 6.2.(iii)
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation, 500mm under ream piles, pile caps, chimney, risers (if any) with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 4000 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 42969558.4 | RC25-27 TL 6.4.(i)
3.4 | Supply of all materials like cement, coarse aggregates (Nominal size 12mm to 20mm), fine aggregates and making 1000mm river bed pile foundations (after pile boring as per required depth, basing on design) as per requirement, including supply of all equipment with labours, head loading of all type of Civil materials , proper curing of the foundations and T&P as per specification in the concrete ratio 1:1:2 and disposal of excess earth as per the direction of Engineer In Charge. | MT | 60 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 4530096.936 | RC25-27 TL 6.5.(i)
4 | WELDING OF TOWER MEMBERS
4.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 80000 | 10.24 | 0.9216 | 0.9216 | 12.0832 | 966656 | RC25-27 TL 16.2.(i)
5 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | [6 empty] | 0
5.1 | Excavation and Back filling (as per approved drawing) | [6 empty] | 0
5.1.1 | Soft/loose soil | CUM | 1500 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 414126.9 | RC25-27 TL 2.(i)
5.1.2 | Dense/compact soil | CUM | 500 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 216258.6 | RC25-27 TL 2.(ii)
5.1.3 | Soft/Dis intigrated rock (not required blasting) | CUM | 500 | 701.88 | 63.1692 | 63.1692 | 828.2184 | 414109.2 | RC25-27 TL 2.(iii)
5.2 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply of sand chips etc. | CUM | 400 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 3010151.68 | RC25-27 TL 6.2.(iii)
5.3 | PCC in the ratio 1:2:4 as above Design, Engineering, Providing and laying of plain cement concrete (PCC 1:2:4) with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 350 | 7723.79 | 695.1411 | 695.1411 | 9114.0722 | 3189925.27 | RC25-27 TL 6.3.(i)
5.4 | RR masonary work in the ratio 1:5 including supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | CUM | 2500 | 3805.47 | 342.4923 | 342.4923 | 4490.4546 | 11226136.5 | RC25-27 TL 15.10.(i)
6 | PTCC approval, railway crossing has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 226644.96 | 20398.0464 | 20398.0464 | 267441.0528 | 267441.0528 | LOA NO.137,Dt.16.02.2023 (Turumunga -Dhenkikote)
7 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hecter | 5 | 135360 | 12182.4 | 12182.4 | 159724.8 | 798624 | R/C FOR Forest Clearance vide No.1268, Dt.03.11.25 of Sr.GM, CPC
8 | Barbed wire fencing with spike to avoid wild animals, elephants from electrocution in Reserve Forest area including supply of barbed wire and all other materials as per approved TS and drawings ans as per recommendation of site Engineer-In -Charge as per condition of MOEF. GOI | Per Loc. | 15 | 115000 | 10350 | 10350 | 135700 | 2035500 | Tentative Market Price
9 | Supply & Installation of Dynamic Bird Flight Diverter LED type for installation in Top conductor & Earth wire under Forest stretch as per condition of MOEF. GOI | Nos. | 400 | 2475 | 222.75 | 222.75 | 2920.5 | 1168200 | Wor Order No.ED-NZ-BLS-1040,Dt.23.05.2025
10 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line. | [6 empty] | 0
10.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per Loc. | 50 | 400000 | 36000 | 36000 | 472000 | 23600000 | Average bench mark value of concerned area
10.2 | Compensation for acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | Per Km | 10 | 2500000 | 225000 | 225000 | 2950000 | 29500000
TOTAL CIVIL WORKS | [7 empty] | 141915705.1178
TOTAL SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (220KV 220 KV TURUMUNGA-BASUDEVPUR D/C LINE ) | [7 empty] | 154354981.4255

## LINE CIVIL
0 |  | CALCULATION SHEET
SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
1 | PA+0 | 0 | 63.36 | 0 | 0.968 | 0 | 8.76 | 0 | 0.201 | 0
2 | PA+3 | 0 | 70 | 0 | 0.968 | 0 | 9.72 | 0 | 0.201 | 0
3 | PA+6 | 0 | 70 | 0 | 0.968 | 0 | 9.72 | 0 | 0.201 | 0
4 | PB+0 | 0 | 104.43 | 0 | 1.5125 | 0 | 15.49 | 0 | 0.272 | 0
5 | PB+3 | 0 | 113.49 | 0 | 1.5125 | 0 | 17 | 0 | 0.272 | 0
6 | PB+6 | 0 | 113.49 | 0 | 1.5125 | 0 | 17 | 0 | 0.272 | 0
7 | PC+0 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
8 | PC+3 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
9 | PC+6 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
10 | OB+3 | 0 | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
11 | OB+6 | 0 | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
1 | OA+0(WET) | 5 | 64.512 | 322.56 | 0.968 | 4.84 | 8.796 | 43.98 | 0.194 | 0.97
2 | OA+3(WET) | 14 | 71.25 | 997.5 | 0.968 | 13.552 | 9.764 | 136.696 | 0.194 | 2.716
3 | OA+6 (WET) | 11 | 71.25 | 783.75 | 0.968 | 10.648 | 9.764 | 107.404 | 0.194 | 2.134
4 | OB+0(WET) | 5 | 119.16 | 595.8 | 1.682 | 8.41 | 17.9 | 89.5 | 0.292 | 1.46
5 | OB+3(WET) | 13 | 129.02 | 1677.26 | 1.682 | 21.866 | 19.59 | 254.67 | 0.292 | 3.796
6 | OB+6 (WET) | 4 | 129.02 | 516.08 | 1.682 | 6.728 | 19.59 | 78.36 | 0.292 | 1.168
7 | OC+0(WET) | 7 | 212.94 | 1490.58 | 2.738 | 19.166 | 35.397 | 247.779 | 0.432 | 3.024
8 | OC+3(WET) | 11 | 212.94 | 2342.34 | 2.738 | 30.118 | 35.397 | 389.367 | 0.432 | 4.752
9 | OC+6 (WET) | 7 | 212.94 | 1490.58 | 2.738 | 19.166 | 35.397 | 247.779 | 0.432 | 3.024
10 | OC+15(WET/P.S) | 3 | 360 | 1080 | 10 | 30 | 59 | 177 | 5.6 | 16.8
11 | OC+24(WET/P.S) | 0 | 390 | 0 | 11 | 0 | 65 | 0 | 5.9 | 0
12 | UR+0 (P.S) | 0 | 276.48 | 0 | 8.836 | 0 | 73.632 | 0 | 0.721 | 0
13 | UR+6 (P.S) | 4 | 276.48 | 1105.92 | 8.836 | 35.344 | 73.632 | 294.528 | 0.721 | 2.884
14 | DD+0 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
15 | DD+3 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
16 | MB+0 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
17 | MB+6 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
18 | MB+9 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
19 | MC+0 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
20 | MC+6 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
21 | MC+9 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
22 | MC+15 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
23 | QD+9 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
24 | QD+15 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
25 | MA+0(WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
26 | MA+3(WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
27 | MA+6 (WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
28 | MB+0(WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
29 | MB+3(WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
30 | MB+6 (WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
31 | MC+0(WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
32 | MC+3(WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
33 | MC+6 (WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
14 | DD type composite tower | 1 | 461.28 | 461.28 | 6.96 | 6.96 | 45.67 | 45.67 | 4.398 | 4.398
34 |  | 85 |  | 12402.37 |  | 199.838 |  | 2067.063 |  | 42.728
[7 empty] | M20 | 2067.063
[7 empty] | M25 | 0
|  |  |  | 14262.7255 |  | 229.8137 |  | 2377.1224 |  | 49.1372
0

## LINE SUMMERY
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
SUMMARY (PART-B)
Name of of Works: Construction of 220 KV UNCHABALI-PALASPANGA D/C LINE
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (SCHEDULE-VIIA (FOR 220 KV UNCHABALI-PALASPANGA D/C LINE)) | 185603450.4337
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 5568103.513
3 | Sub-Total (sl no. 1+2) | 191171553.9467
4 | Contigency 3% on Sl.No.3 | 5735146.6184
5 | T&P cost @ 2% on Sl.No. 3 | 3823431.0789
6 | Transportation @5% on Sl.No.3 | 9558577.6973
7 | Total erection Chages (SCHEDULE-VIIB & VIIC (FOR 220 KV UNCHABALI-PALASPANGA D/C LINE) | 154354981.4255
8 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection,obtaining clearance from PTCC Auhtority etc. | 500000
9 | Tree cutting @20000/- per Kms | 700000
10 | Grand Total (3+4+5+6+7+8) | 365843690.7669
Deputy General Manager (Elect.),
E.H.T (Const.) Division,
OPTCL, Keonjhar

## VIIA CABLE
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Name of of Works: Construction of 220 KV Transmission line from proposed 400/220KV Unchabali GSS to Palaspanga GSS along with 2Nos. 220KV Bays extension at proposed 400/220kV Unchabali GSS
PART-C: VII-A (SUPPLY PART FOR LAYING OF 220 KV UG CABLE )
| DESCRIPTION OF ITEMS | UNITS | Total Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | Escalation (UNIT PO PRICE/ COST DATA RATE + 5% ESCALATION PER YEAR) | TOTAL PRICE OF QUANTITY in Rs | Price Reference
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification)
1 | 2 | 3 | 4 | 5 | 6 | 7=4X6 | 8
1 | Type tested EHV XLPE Power Copper conductor cable as per IEC60840 & IS7098 for the (220 KV class) as per TS
1.1 | 220KV XLPE cable, 1000 sqmm single core annealed Copper cable with corrugated aluminium sheath as per TS.(for interconnection from 220KV Dead end tower to 220kV SY at Palaspanga) | MTR | 7000 | 18369.8 |  | 128588600 | Cost Data 24-25-ss-151
1.2 | Supply of 200mm PE 80-PN8 HDPE pipe for laying of individual run of UG cable at main road/drain crossing/ railway crossing unaccesseble place as per instruction of Engineeer-in-charge | MTR | 300 | 1200 |  | 360000 | Tentative
1.3 | Straight through jointing kits hit shrinkable type suitable for 220KV,1000 sq. mm UG cable with all accessories as per TS | Nos. | 8 | 134541.58 | 155748.6965 | 1245989.5724 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.4 | Supply of 220 KV Outdoor type cable termination oil type-1000sqmm | No | 0 | 1086005.79 |  | 0 | Cost Data 24-25-ss-153
1.5 | Supply of earthing materials 3Mtr, 100mm ID heavy gauge type pipe with provision of with GI clamp fixtures welded all around the pipe & connecting separately to main equipment for grounding (single electrode with accessories) with GI flat 75X10mm size | No. | 8 | 11790.51 | 13648.9891 | 109191.9131 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.6 | Supply of Earth Flat (75mmX 10mm) for laying of earth mat at cable termination end as per approved drawing & specifications. | MT | 5 | 93451.89 |  | 467259.45 | CD 24-25-Line-4
1.7 | Supply of single phase Link box with SVL with clamps and connectors with acessories | No. | 8 | 38675.29 |  | 309402.32 | Cost Data 24-25-ss-146
1.8 | Supply of single phase Link box without SVL with clamps and connectors with acessories | No. | 8 | 21301.16 |  | 170409.28 | Cost Data 24-25-ss-147
1.9 | Supply of 6.6 KV,300sqmm Single core bonding copper cable | Mtr | 300 | 3171.9 |  | 951570 | Cost Data 24-25-ss-152
1.1 | Supply of Earthing cable of size 1.1KV 1CX300sqmm Cu Cable below ground including connection/termination as required to make the system complete in all respect | Mtr | 1600 | 2232.46 |  | 3571936 | Cost Data 24-25-ss-143
1.11 | Supply of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 200000 |  | 200000 | Tentative
1.12 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS (For composite tower) | No. | 8 | 71489.05 |  | 571912.4 | Cost Data 24-25-ss-30
1.13 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type (31mm/kV)) and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply with IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with tubular type HDG support structure. - SF6 to air bushing shall be placed as close to the GIS building (for both feeder and TRF bays) as practicable to reduce length of Bus Duct used which shall be as per the approved drawing. | No. | 8 | 716720.234 |  | 5733761.8716 | Gopalpur SS 1.8
2 | Supply of 24F OPGW (DWSM) fibre optic cable, laid along 220 KV UG Cable
2.1 | Supply of 24F OPGW (DWSM) fibre optic cable, laid along 220 KV UG Cable | Km. | 0.8 | 190400 |  | 152320 | Cost Data 24-25-Tel-23
2.2 | Supply of joint box(Splice enclosure),24F | No. | 1 | 4525.2 |  | 4525.2 | Cost Data 24-25-Tel-27
2.3 | Supply of end Connectors and acessories for OFC connection at GRID substations | Set | 1 | 5158.005 | 5971.0355 | 5971.0355 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
2.4 | Supply of HDPE PLB duct of size 40 mm for laying of 24 OFC cable . | Km. | 0.8 | 66320.955 | 76774.7955 | 61419.8364 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
| TOTAL PART-C, SCHEDULE-VIIA (SUPPLY COMPONENT OF THE WORKS FOR 220KV UG CABLE) |  |  |  |  | 142504268.8791
| GST @ 18% |  |  |  |  | 25650768.3982
| TOTAL PART-C, SCHEDULE-VIIA (SUPPLY COMPONENT OF THE WORKS FOR 220KV UG CABLE) including GST |  |  |  |  | 168155037.2773
| Manager (Fin.) |  |  | Deputy General Manager (El)
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## VIIB VIIC CABLE
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Name of of Works: Construction of 220 KV Transmission line from proposed 400/220KV Unchabali GSS to Palaspanga GSS along with 2Nos. 220KV Bays extension at proposed 400/220kV Unchabali GSS
PART-C: VIIB & VIIC (ERECTION & CIVIL PART FOR LAYING OF 220 KV UG CABLE)
| DESCRIPTION OF ITEMS | UNIT | Total Qty | Price per unit in Rs | Total price | Remarks
SL. No. | ERECTION,TESTING & COMMISSIONING INCLUDING CIVIL WORKS OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS
1 | 2 | 3 | 4 | 5 | 6=4X5 | 7
ELECTRICAL WORKS
1 | Erection, Comissioning & Testing of 220 kV, 1 Core,6-Runs, 1000mm² Copper, XLPE insulation UG Cable
1.1 | Laying , Comissioning & Testing of 220 kV, 1 Core,1 X 4-Runs, 1000 mm² Copper, XLPE insulation UG Cable. | MTR | 7000 | 2250 | 15750000 | LoA No.2238,Dt.31.03.2016 of Sr.GM,CPC
1.1 | Laying, commissioning & testing of 220KV XLPE cable, 1000 sqmm single core annealed Copper cable with corrugated aluminium sheath cable by HDD method with 200mm PE 80-PN8 HDPE pipe for laying of individual run of UG cable at main road/drain crossing/ railway crossing unaccesseble place as per instruction of Engineeer-in-charge | MTR | 300 | 1500 | 450000 | Tentative
1.2 | Straight through jointing kits hit shrinkable type suitable for 220 KV, 1000 sq. mm UG cable (mandatory spare-3Nos.) with all accessories as per TS | Nos. | 8 | 38157 | 305256 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.3 | Erection, Comissioning & Testing of Outdoor terminating kit Heat shrinkablre type uitable for 220 kV class, 1Core, 1000 mm², copper UG Cable connection of 300sqmm bonding cable | Nos. | 0 | 50000 | 0 | LoA No.2238,Dt.31.03.2016 of Sr.GM,CPC
1.4 | Erection of earthing materials 3Mtr, 100mm ID heavy gauge type pipe with provision of with GI clamp fixtures welded all around the pipe & connecting separately to main equipment for grounding (single electrode with accessories) with GI flat 75X10mm size as per approved drawing & specifications | Nos. | 8 | 5723.55 | 45788.4 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.5 | Erection, Comissioning & Testing of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 8 | 7631.4 | 61051.2 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.6 | Erection, Comissioning & Testing single phase Link box with SVL with clamps and connectors with acessories | Nos. | 8 | 9539.25 | 76314 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.8 | Erection, Comissioning & Testing of Single core, 6.6 KV,300sqmm Single core bonding copper cable | Mtr | 300 | 28.16 | 8448 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.9 | Erection, Comissioning & Testing of Single core, 300 sqmm XLPE Earthing cable | Mtr | 1600 | 28.16 | 45056 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
1.1 | Erection of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 20000 | 20000 | Tentative
1.11 | laying of Earth Flat (75mmX 10mm) for laying of earth mat at cable termination end(composite tower)as per approved drawing & specifications. | Mtr | 400 | 108.47 | 43388 | RC24-25-SS-I.1.1.vi(b)
1.12 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS (For composite tower) | No. | 8 | 5203.87 | 41630.96 | RC 25-27 SS-10.10.i.(i)
1.13 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type (31mm/kV)) and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply with IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with tubular type HDG support structure. - SF6 to air bushing shall be placed as close to the GIS building (for both feeder and TRF bays) as practicable to reduce length of Bus Duct used which shall be as per the approved drawing. | No. | 8 | 15000 | 120000 | Ranua estimate
2 | Laying of 24 fibre optic cable, single mode duct type,with fibre armoured Duct pipe of size 40mm and connectors,laid along with 220 kV UG cable..
2.1 | Laying of 24 fibre optic cable, single mode duct type,with fibre armoured Duct pipe of size 40mm and connectors,laid along with 220 kV UG cable.. | Km. | 0.8 | 50081.055 | 40064.844 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
2.2 | Erection of straight connectors for OFC connection | No. | 1 | 8585.325 | 8585.325 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
2.3 | Erection of end Connectors and acessories for OFC connection at GRID subststions | No. | 1 | 21463.305 | 21463.305 | LoA No.785,Dt.23.11.2022 of Sr.GM,CPC
| TOTAL ELECTRICAL WORKS |  |  |  | 17037046.034
CIVIL WORKS
1.1 | Earth work excavation of Hard Soil | Cum | 1950 | 358.41 | 698899.5 | RC25-26 TL-EXC-1(ii)
1.2 | Supply & Filling with fine river sand after/before laying of Cable inside the trench | Cum | 1462.5 | 898.26 | 1313705.25 | RC25-26 SS-FDN-3.2
1.3 | Plain Cement Concrete (1:3:6). | Cum | 182 | 5907.71 | 1075203.22 | RC25-26 SS-FDN-2.i
1.4 | R.C.C M-20(1:1.5:3). | Cum | 539.5 | 8533.36 | 4603747.72 | RC25-26 SS-FDN-3.i
1.5 | Rigid smooth Centering & Shuttering. | SQMTR | 6630 | 442.29 | 2932382.7 | RC25-26 TL-EXC-3
1.6 | SUPPLY OF MS ROD (As per the OPTCL Approved Make) | MT | 20 | 65511.29 | 1310225.8 | RC25-26 SS-FDN-1.1.i
1.7 | Cutting, Bending, Binding Placing in position of steel rod for foundation including cost of binding wire. | MT | 20 | 6508.03 | 130160.6 | RC25-26 SS-FDN-1.1.ii
1.8 | Providing 12mm thick cement plaster (1:6).(With supply of cement) | SQMTR | 5135 | 135.96 | 698154.6 | RC25-26 SS-MASONARY-1.5.i
| TOTAL OF CIVIL WORKS |  |  |  | 12762479.39
| TOTAL PART-C, SCHEDULE-VII B & VII C-ERECTION and CIVIL WORKS (ERECTION PART FOR LAYING OF 132 KV UG CABLE) |  |  |  | 29799525.424
| GST @ 18% |  |  |  | 5363914.5763
| TOTAL PART-C, SCHEDULE-VII B & VII C-ERECTION and CIVIL WORKS (ERECTION PART FOR LAYING OF 132 KV UG CABLE) including GST |  |  |  | 35163440.0003

## CABLE SUMMERY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
SUMMARY
PART-C (220 KV UG CABLE LINE)
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials VII-A (FOR CABLE) | 168155037.2773
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 5044651.1183
3 | Sub-Total (sl no. 1+2) | 173199688.3956
4 | Contigency 3% on Sl.No.3 | 5195990.6519
5 | T&P cost @ 2% on Sl.No. 3 | 3463993.7679
6 | Transportation @5% on Sl.No.3 | 8659984.4198
7 | Total erection Chages VIB & VIIC (FOR CABLE) | 35163440.0003
8 | Grand Total (3+4+5+6+7) | 225683097.2355
Deputy General Manager (Elect.),
E.H.T (Const.) Division,
OPTCL, Keonjhar

## VIIA UNCHABALI SS
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at proposed 400/220KV GSS Unchabali
SUPPLY OF EQUIPMENT / MATERIALS,
PART -A, SCHEDULE-VIIA-SUPPLY (FOR 220 KV SUB-STATION WORK)
Sl. No. | DESCRIPTION OF ITEMS SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT | TOTAL QUANTITY (02No. Bays) | [5 empty] | Price Reference
|  |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price
1 | 2 | 3 | 5 | 6 | 7 | 8 | 9 | 10= 4*9 | 12
1 | 245 KV, 50kA, 1200-600-300A/1A (5 core), SINGLE PHASE CURRENT TRANSFORMER AS PER TS | NOS | 6 | 382298.97 | 34406.9073 | 34406.9073 | 451112.7846 | 2706676.7076 | CD 24-25-SS-21
2 | 245 KV,2000A,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS | 2 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 1408165.1776 | CD 24-25-SS-5
2.2 | WITH SINGLE EARTH SWITCH | NOS | 2 | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 1831043.6656 | CD 24-25-SS-6
2.3 | TANDEM MOUNTED WITHOUT EARTH SWITCH | NOS | 4 | 633063.08 | 56975.6772 | 56975.6772 | 747014.4344 | 2988057.7376 | CD 24-25-SS-7 | Yes
3 | 245 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER AS PER TS | NOS | 6 | 379430 | 34148.7 | 34148.7 | 447727.4 | 2686364.4 | CD 24-25-SS-54
4 | 245KV, SF6 CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 1365681.73 | 122911.3557 | 122911.3557 | 1611504.4414 | 3223008.8828 | CD 24-25-SS-2
5 | 216 KV SURGE ARRESTOR AS PER TS | NOS | 6 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 506142.474 | CD 24-25-SS-30
6 | 220 KV Bus Post Insulators | NOS | 20 | 22424.5697 | 2018.2113 | 2018.2113 | 26460.9923 | 529219.845 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
7 | BUS BAR & CIRCUIT MATERIALS
7.1 | TENSION & SUSPENSION ANTI FOG TYPE INSULATOR STRING
7.2 | 160 kN ANTIFOG PORCELAIN DISC INSULATOR | NOS | 1700 | 726.98 | 65.4282 | 65.4282 | 857.8364 | 1458321.88 | CD 24-25-TL-ACC-58
7.3 | 90 kN ANTIFOG PORCELAIN DISC INSULATOR | NOS | 500 | 599.75 | 53.9775 | 53.9775 | 707.705 | 353852.5 | CD 24-25-TL-ACC-57
7.4 | ACSR MOOSE CONDUCTOR ( 61/3.66 SQMM) | KM | 3 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 1582124.0226 | CD 24-25-TL-ACC-19
7.5 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | MTRS | 300 | 2020.9386 | 181.8845 | 181.8845 | 2384.7075 | 715412.25 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS
8.1 | Double Tension H/W fitting for twin ACSR Moose (2 x 160kN) | NOS | 48 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 286424.5152 | CD 24-25-TL-ACC-10
8.2 | Single Tension H/W fitting for single ACSR Moose (1 x 160kN) | NOS | 6 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 19989.5304 | CD 24-25-TL-ACC-9
8.3 | Single Suspension Hard ware fitting for SINGLE ACSR Moose (1x 90kN) | NOS | 30 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 122672.682 | CD 24-25-TL-ACC-7
8.4 | 'T' Clamp for single moose run with single moose ACSR drop | NOS | 22 | 849.579 | 76.4621 | 76.4621 | 1002.5033 | 22055.0715 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8.5 | 'T' Clamp for twin moose run with single moose ACSR drop | NOS | 12 | 1459.7847 | 131.3806 | 131.3806 | 1722.546 | 20670.552
8.6 | 'T' Clamp for single Zebra run with single moose ACSR drop | NOS | 12 | 849.579 | 76.4621 | 76.4621 | 1002.5033 | 12030.039
8.7 | 220 KV PI Clamp | NOS | 26 | 738.7217 | 66.485 | 66.485 | 871.6916 | 22663.9823
8.8 | 220 KV LA Clamp | NOS | 6 | 649.4472 | 58.4503 | 58.4503 | 766.3478 | 4598.0865
8.9 | 220 KV IVT Clamp | NOS | 6 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 5924.7248
8.1 | 220 KV CT Clamp | NOS | 12 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 11849.4495
8.11 | 220 KV CB Clamp | NOS | 12 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 11849.4495
8.12 | 220 KV Isolator pad clamp | NOS | 60 | 649.4472 | 58.4503 | 58.4503 | 766.3478 | 45980.865
8.13 | PG Clamp for ACSR Moose | NOS | 30 | 600.3953 | 54.0356 | 54.0356 | 708.4665 | 21253.995
8.14 | Spacer for Twin bus ACSR Moose 220 KV bus | NOS | 36 | 1769.39 | 159.2451 | 159.2451 | 2087.8802 | 75163.6872 | CD 24-25-TL-ACC-51
9 | SUBSTATION EARTHING SYSTEMS
9.1 | 75X10 mm GI Flat | MT | 10 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1102732.302 | CD 24-25-Line-4
9.2 | 50X6 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MT | 4 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 441092.9208 | CD 24-25-Line-4
9.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 140 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 376817.896 | CD 24-25-TL-8
10 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1, 2-2,3-3 & 4-4 along with its accessories as per TS.
10.2 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 1300 | 1067.3695 | 96.0633 | 96.0633 | 1259.496 | 1637344.8 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
10.3 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 900 | 712.2337 | 64.101 | 64.101 | 840.4358 | 756392.175
10.4 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 600 | 498.3674 | 44.8531 | 44.8531 | 588.0735 | 352844.1
10.5 | support GI angle suitable for different sections G.I Cable Trays including i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. | MT | 10 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1102732.302 | CD 24-25-Line-4
11 | SUB STATION SWITCYARD BMK,AC CONSOLE & OTHER MARSHALLING BOXES
11.1 | BAY MARSHALLING KIOSK | NOS | 2 | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 354854.4144 | CD 24-25-SS-76
11.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.11.2
11.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659
11.4 | CT & IVT Out Door Console Boxes | NOS | 4 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 212912.0256 | CD 24-25-SS-75
11.5 | APEX Energy Meter Panel | NOS | 2 | 82637.47 | 7437.3723 | 7437.3723 | 97512.2146 | 195024.4292 | CD 24-25-SS-104
12 | 0.2 Class ABT Complaint Apex energy Audit meter - 2 Nos (1 Nos Main & 1 Nos Check) | NOS | 4 | 87655.56 | 7889.0004 | 7889.0004 | 103433.5608 | 413734.2432 | CD 24-25-SS-105
13 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220KV CLASS
13.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
13.1.1 | P1S - COLUMN ( 4.76KG) Including the earth spikes | NOS | 8
13.1.2 | Q1 BEAM (1.598KG) | NOS | 6
13.1.3 | Q3 BEAM (2.484MT) | NOS | 2
13.2 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220kV CLASS (column & Beam) | MT | 52.636 | 85000 | 7650 | 7650 | 100300 | 5279390.8 | Anticipated price
13.3 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.1 | 95000 | 8550 | 8550 | 112100 | 235410 | Anticipated price
13.4 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
13.4.1 | SINGLE ISOLATORS without ES-220KV ( 1.271 MT) | SET | 2
13.4.2 | Single isolator with ES- 220 KV (1.271MT) | SET | 2
13.4.3 | Tandem isolator without ES 220 KV (1.271MT) | SET | 4
13.4.4 | CTs-220 KV (0.225 MT)) | SET | 6
13.4.5 | IVTs-220 KV (0.287MT) | SET | 6
13.4.6 | Surge Arrester-220 kV (0.292MT) | SET | 6
13.4.7 | BPI-220 KV (0.292MT) | SET | 20
13.4.8 | TOTAL WEIGHT OF EQUIPMENT STRUCTURES | MT | 22.584 | 85000 | 7650 | 7650 | 100300 | 2265175.2 | Anticipated price
13.4.9 | Total weight of GI Nuts and bolts for the above structures | MT | 2.2584 | 95000 | 8550 | 8550 | 112100 | 253166.64 | Anticipated price
14 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
14.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
14.1.1 | PVC 3.5 CX70 mm2 | KM | 3 | 265690.44 | 23912.1396 | 23912.1396 | 313514.7192 | 940544.1576 | CD 24-25-SS-129
14.1.2 | PVC-3.5 CX35 mm2 | KM | 5 | 147505.32 | 13275.4788 | 13275.4788 | 174056.2776 | 870281.388 | CD 24-25-SS-127
14.1.3 | PVC-4 CX 16 mm2 | KM | 3 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 409880.4222 | CD 24-25-SS-125
14.1.4 | PVC-4 CX 6 mm2 | MTRS | 2000 | 131.1821 | 11.8064 | 11.8064 | 154.7948 | 309589.6734 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.16.1.5
14.1.5 | PVC 4CX 4 mm2 | MTRS | 3000 | 104.9503 | 9.4455 | 9.4455 | 123.8413 | 371524.0001 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.16.1.6
14.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
14.2.1 | 2 CX 2.5 mm2 | KM | 3 | 78413.59 | 7057.2231 | 7057.2231 | 92528.0362 | 277584.1086 | CD 24-25-SS-107
14.2.2 | 4 CX 2.5 mm2 | KM | 14 | 123673.44 | 11130.6096 | 11130.6096 | 145934.6592 | 2043085.2288 | CD 24-25-SS-109
14.2.3 | 7CX 2.5 mm2 | KM | 7 | 187201.82 | 16848.1638 | 16848.1638 | 220898.1476 | 1546287.0332 | CD 24-25-SS-110
14.2.4 | 10 CX 2.5 mm2 | KM | 12 | 254413.65 | 22897.2285 | 22897.2285 | 300208.107 | 3602497.284 | CD 24-25-SS-111
14.2.5 | 12 CX 2.5 mm2 | KM | 6 | 393557.7713 | 35420.1994 | 35420.1994 | 464398.1701 | 2786389.0205 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.17.5
14.2.6 | 16 CX 2.5 mm2 | KM | 4 | 387033.75 | 34833.0375 | 34833.0375 | 456699.825 | 1826799.3 | CD 24-25-SS-112
14.2.7 | 19 CX 2.5 mm2 | KM | 2 | 448832.3 | 40394.907 | 40394.907 | 529622.114 | 1059244.228 | CD 24-25-SS-113
14.2.8 | 3.5CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | KM | 1 | 459114.77 | 41320.3293 | 41320.3293 | 541755.4286 | 541755.4286 | CD 24-25-SS-131
15 | ACCESSORIES FOR PLCC SYSTEM With OPGW cable
15.1 | 24 Fibre Optic Approach cable (DWSM) | KM | 1 | 159579.27 | 14362.1343 | 14362.1343 | 188303.5386 | 188303.5386 | CD 24-25-TELC-31
15.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be compatible with existing OPTCL system. | No | 2 | 393554.8077 | 35419.9327 | 35419.9327 | 464394.6731 | 928789.3462 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Tel sl.4
15.3 | Digital Teleprotection Equipment and accessories to be suitable for interfacing with SDHMUX | No. | 1 | 562958.9237 | 50666.3031 | 50666.3031 | 664291.53 | 664291.53 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
15.3 | Supply of FODP(Fibre Optic Distribution Panel)48 F: Indoor type,rack mounted with FCPC coupling and pig tails(DWSm Fibre) | No | 2 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 128046.402 | CD24-25-TEL-29
15.4 | Remote Terminal Unit (RTU) with MFT/MFM module designed for Power Utility SCADA operation. RTU should report in IEC 870-5-104 protocols to both main & backup control centre. RTU should have ports for interfacing with relay control panels,MFT/MFMs and port for LDMS facility. Laptop should be part of the supply contract of RTU for monitoring, local data aquisition & configuration of RTU. | No | 1 | 1165622.5 | 104906.025 | 104906.025 | 1375434.55 | 1375434.55 | CD24-25-TEL-55
15.5 | 48 V,300 AH,maintenance free VRLA Battery set | Set | 1 | 119332.12 | 10739.8908 | 10739.8908 | 140811.9016 | 140811.9016 | CD24-25-TEL-02
15.6 | SMPS based Battery Charger of 48V/75A suitable for 48V VRLA Battery | NO. | 1 | 110881.51 | 9979.3359 | 9979.3359 | 130840.1818 | 130840.1818 | CD24-25-TEL-18
15.7 | 2.5 sq. mm 2 core control cable(power supply,Transducer/MFT PT supply) | Metre | 300 | 44.08 | 3.9672 | 3.9672 | 52.0144 | 15604.32 | CD24-25-TEL-62
15.8 | 2.5 sq. mm multi strand 4 core control cable(Transducer/MFT CT , supply) | Metre | 300 | 61.71 | 5.5539 | 5.5539 | 72.8178 | 21845.34 | CD24-25-TEL-61
15.9 | 1.5 sq. mm 10 core control cable(Digital Input) | Metre | 200 | 125.62 | 11.3058 | 11.3058 | 148.2316 | 29646.32 | CD24-25-TEL-59
15.1 | 10 sq. mm 2 core multi strand control cable(Battery) | Metre | 100 | 183 | 16.47 | 16.47 | 215.94 | 21594 | Local Market rate
15.11 | Earth Flat, Cable Tray, Telephone cable,ACDB, DCDB, Foundation rail, Junction Box. | LS | 2 | 174913.2479 | 15742.1923 | 15742.1923 | 206397.6325 | 412795.265 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Tel. Sl.10
16 | Substation Switchyard Lighting: Installation of fixtures & lamps (LED) of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality) with switch gear, GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | Nos. | 40 | 17085.7602 | 1537.7184 | 1537.7184 | 20161.197 | 806447.88 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
17 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS).
17.1 | STREET LIGHTING: Installation of HDG Tubular street lighting poles 8.5 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. Poles shall be installed on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes installation of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI junction box, GI Conduit etc. & as per technical specification. | Nos. | 40 | 11105.3517 | 999.4817 | 999.4817 | 13104.315 | 524172.6 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, sl.32
17.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB, XLPE cables (305 C*120sqmm) from main ACDB CR to the out door KIOSK. XLPE cable of 4CX16sqmm from outdoor KIOSK to the street light poles & 4CX6sqmm from pole to pole & 2CX6sqmm from pole to lighting fixtures | Nos. | 2 | 74748.2387 | 6727.3415 | 6727.3415 | 88202.9216 | 176405.8433
18 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | Nos. | 16 | 64069.6386 | 5766.2675 | 5766.2675 | 75602.1735 | 1209634.776
19 | 220 KV SIDE PROTECTION & OTHER PANELS
19.1 | 220KV Feeder Protection Panel: DP MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. The panel shall be compatible with the existing panels for the substation for smooth integration with SAS. | Nos. | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | CD 24-25-SS-37
19.2 | 220KV BUS-BAR Protection Sysstem (Shall be compatible with the existing busbar protection of the substation): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. The bus bar protection system shall be integrated with the Automation system. | Nos. | 2 | 3809977.15 | 342897.9435 | 342897.9435 | 4495773.037 | 8991546.074 | CD 24-25-SS-40
20 | BEST QUALITY &APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X10)mm Size | NOS | 30 | 3860.9639 | 347.4867 | 347.4867 | 4555.9374 | 136678.1212 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, Sl.31.4
21 | SUBSTATION AUTOMATION SYSTEM: Supply of the following 132KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of Industrial computer with accessories, PC with accessories, laser printer, UPS, GPS system & numerical Bay Control unit etc.
21.1 | 220KV Level
21.1.1 | BCU for 220KV side: Numerical Bay Control unit:64 Digital Input & 32Nos. Digital output with 4 CT Input,4 VT inputs, IEC 61850 protocol with PRP,power supply 220V DC | No. | 2 | 231021.31 | 20791.9179 | 20791.9179 | 272605.1458 | 545210.2916 | CD 24-25-BCU-02
21.1.2 | Numerical Distance protection with PRP,IEC 61850 protocol.Digital input & output to be provided as per the scheme. | No. | 2 | 213250.44 | 19192.5396 | 19192.5396 | 251635.5192 | 503271.0384 | CD 24-25-BCU-03
21.1.3 | Numerical O/C & E/F relays: IEC 61850protocol with PRP Digital input & outpot to be provided as per the scheme | No. | 2 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 251635.5192 | CD 24-25-BCU-05
21.1.4 | High impedance REF relay. Digital input & output to be provided as per scheme | No. | 2 | 236944.94 | 21325.0446 | 21325.0446 | 279595.0292 | 559190.0584 | CD 24-25-BCU-04
21.1.5 | Auxiliary Relay for DC supervision | No. | 8 | 5331.26 | 479.8134 | 479.8134 | 6290.8868 | 50327.0944 | CD 24-25-BCU-06
21.1.6 | MPG-TEST BLOCK | No. | 16 | 2402.62 | 216.2358 | 216.2358 | 2835.0916 | 45361.4656 | CD 24-25-BCU-08
21.1.7 | High speed Trip relay (Electrical Reset) 86A,86B,96 | No. | 8 | 10070.16 | 906.3144 | 906.3144 | 11882.7888 | 95062.3104 | CD 24-25-BCU-09
21.1.8 | Line interface unit | No. | 4 | 3791.12 | 341.2008 | 341.2008 | 4473.5216 | 17894.0864 | CD 24-25-BCU-10
21.1.9 | Ethernet switch IEEE802.3,IEEE1588,IEC 61850-3, PRP protocol,20% spare to be provided | LOT | 2 | 473889.88 | 42650.0892 | 42650.0892 | 559190.0584 | 1118380.1168 | CD 24-25-BCU-11
21.1.10 | Simplex cubicle type for BCU & protection equipment, swing frame front access (VSG), Dimension 2300mm(H) X 1000mm (D) X 1000mm (W). Earth bar 25X6 sqmm, Copper & panel illumination. Complete wiring of protection & control components,all relay & equipment fitted . One panel for control & protection of two bays, with provision of TCS relay, DC changeover relay & suitable voltage slection relay. | SET | 1 | 118472.47 | 10662.5223 | 10662.5223 | 139797.5146 | 139797.5146 | CD 24-25-BCU-12
21.1.11 | DCDB panel : with Bus Bar switches,with dual source facility of Double Bus system for independent DC supply to each Bay, should have the facility of VTD & CTD for voltage & current montoring. Each MCB/MCCBs should also be given wth Aux contacts. | No. | 1 | 49758.44 | 4478.2596 | 4478.2596 | 58714.9592 | 58714.9592 | CD 24-25-SAS-35
26 | CCTV Surveilance system
26.1 | Outdoor PTZ Camera (with PTZ camera housing, gooseneck stand-wall mount bracket, power supply/ adaptor, camera holder and other accessories) (Range: 100Mtrs) | Nos. | 1 | 92942.62 | 8364.8358 | 8364.8358 | 109672.2916 | 109672.2916 | CD 24-25-SS-173
| TOTAL: PART -A, SCHEDULE-VIIA-SUPPLY (FOR 220 KV SUB-STATION WORK) | [6 empty] | 78612059.7922

## VIIB VIIC UNCHABALI SS
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at proposed 400/220KV GSS Unchabali
ERECTION OF EQUIPMENTS/ MATERIALS AND CIVIL WORKS
PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 132KV SUB-STATION WORK)
SL. NO. | DESCRIPTION OF ITEMS ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS | UNITS | TOTAL QUANTITY (For 02No. 220KV Bays) | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3
PART A | ELECTRICAL WORKS
1 | 245 KV,1200-600-300A/1-1-1-1,SINGLE PHASE CURRENT TRANSFORMER | NOS | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | RC-25-27-SS-10.10.h(i)
2 | 245 KV,2000A,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS | 2 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 70517.4608 | RC-25-27-SS-10.10.b(i)
2.2 | WITH SINGLE EARTH SWITCH | NOS | 2 | 33153.68 | 2983.8312 | 2983.8312 | 39121.3424 | 78242.6848 | RC-25-27-SS-10.10.d(i)
2.3 | TANDEM ISOLATOR | NOS | 4 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 141034.9216 | RC-25-27-SS-10.10.g(i)
3 | 245 KV,3CORE,SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | RC-25-27-SS-10.10.h(i)
4 | 245KV,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 97698.43 | 8792.8587 | 8792.8587 | 115284.1474 | 230568.2948 | RC-25-27-SS-10.10.a(i)
5 | 216 KV SURGE ARRESTOR AS PER TS | NOS | 6 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 36843.3996 | RC-25-27-SS-10.10.i(i)
6 | 220 KV Bus Post Insulators | NOS | 20 | 2853.73 | 256.8357 | 256.8357 | 3367.4014 | 67348.028 | RC-25-27-SS-10.10.j(i)
7 | BUS BAR & CIRCUIT MATERIALS
7.1 | Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors,hoisting of Long Rod/Disc insulator ,Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments,testing,commissioning etc. as per the instruction of Engineer-in charge.
7.1.1 | Busbar stringing (for single moose) wirth fixing of insulator | Mtrs | 1000 | 184.65 | 16.6185 | 16.6185 | 217.887 | 217887 | RC 25-27 SS-14.e.(i)
7.1.2 | Busbar stringing (for twin moose) wirth fixing of insulator | Mtrs | 400 | 252.05 | 22.6845 | 22.6845 | 297.419 | 118967.6 | RC 25-27 SS-14.f.(i)
7.1.3 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side including all clamps and connectors. | Mtrs | 330 | 236.4407 | 21.2797 | 21.2797 | 279 | 92070 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
7.2 | ACSR MOOSE CONDUCTOR JUMPERING
7.2.1 | Jumpering to equipments with fixing of clamps and connectors (for single moose) | Mtrs | 400 | 134.3 | 12.087 | 12.087 | 158.474 | 63389.6 | RC 25-27 SS-15(v)
7.2.2 | Jumpering to equipments with fixing of clamps and connectors (for twin moose) | Mtrs | 400 | 184.65 | 16.6185 | 16.6185 | 217.887 | 87154.8 | RC 25-27 SS-15(vi)
EARTH WIRES & IT'S HARDWARES & FITTING
| Earthing Spikes of 9 mtr long each and Its Fittings in all respect. (220 kv side) | No. | 10 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 69770 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8 | SUBSTATION EARTHING SYSTEMS
8.2 | EARTHING CONDUCTOR FOR BURRIAL : 75x10 mm GI Earth Flat for laying (Spacing maximum 5m both ways) | Mtrs | 1695 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 220551.027 | RC 25-27 SS-21.10.vi(b)
8.3 | EARTHING CONDUCTOR : 50 X 6 mm GI Earth Flat for raiser from the burrial earthmat to equipment, structure etc. | Mtrs | 1674 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 217818.5364 | RC 25-27 SS-21.10.v(b)
8.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 140 | 2993 | 269.37 | 269.37 | 3531.74 | 494443.6 | RC25-27-SS-E.21.30.ii
9 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:2-2,3-3 & 4-4 along with its accessories as per TS. | Lot | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | Local Market Rate
10 | SUB STATION SWITCYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES
10.1 | BAY MARSHALLING KIOSK | NOS | 2 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 23373.7704 | RC-25-27-SS-18.40
10.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 23373.7704 | RC-25-27-SS-18.40
10.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 23373.7704 | RC-25-27-SS-18.40
10.4 | CT & CVT Out Door Console Boxes | NOS | 8 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 28840.8048 | RC-25-27-SS-18.60
10.5 | Installation of APEX meter for Main & Check (Two Nos. each) | LOT | 2 | 10000 | 900 | 900 | 11800 | 23600 | Tentative
11 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
11.1 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220KV CLASS (column & Beam) | MT | 44 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 302614.1624 | RC-25-27-SS-16
11.2 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.1 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 14442.9487 | RC-25-27-SS-16
11.3 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 220KV EQUIPMENTS ALONG WITH 33 KV EQUIPMENT | MT | 22.584 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 155323.5964 | RC-25-27-SS-16
11.4 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.2584 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 15532.3596 | RC-25-27-SS-16
12 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
12.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
12.1.1 | PVC 3.5 CX70 mm2 | MTRS | 3000 | 685.24 | 61.6716 | 61.6716 | 808.5832 | 2425749.6 | RC-25-27-SS-17.20(viiii)
12.1.2 | PVC-3.5 CX35 mm2 | MTRS | 5000 | 519.83 | 46.7847 | 46.7847 | 613.3994 | 3066997 | RC-25-27-SS-17.20(vi)
12.1.3 | PVC-4 CX 16 mm2 | MTRS | 3000 | 275.67 | 24.8103 | 24.8103 | 325.2906 | 975871.8 | RC-25-27-SS-17.20(iv)
12.1.4 | PVC-4 CX 6 mm2 | MTRS | 2000 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 371770.8 | RC-25-27-SS-17.20(ii)
12.1.5 | PVC 4CX 4 mm2 | MTRS | 3000 | 126.02 | 11.3418 | 11.3418 | 148.7036 | 446110.8 | RC-25-27-SS-17.20(i)
12.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
12.2.1 | 2 CX 2.5 mm2 | MTRS | 3000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 195195.6 | RC-25-27-SS-17.10(i)
12.2.2 | 4 CX 2.5 mm2 | MTRS | 14000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 910912.8 | RC-25-27-SS-17.10(ii)
12.2.3 | 7CX 2.5 mm2 | MTRS | 7000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 455456.4 | RC-25-27-SS-17.10(iv)
12.2.4 | 10 CX 2.5 mm2 | MTRS | 12000 | 63 | 5.67 | 5.67 | 74.34 | 892080 | RC-25-27-SS-17.10(vi)
12.2.5 | 12 CX 2.5 mm2 | MTRS | 6000 | 63 | 5.67 | 5.67 | 74.34 | 446040 | RC-25-27-SS-17.10(vii)
12.2.6 | 16 CX 2.5 mm2 | MTRS | 4000 | 63 | 5.67 | 5.67 | 74.34 | 297360 | RC-25-27-SS-17.10(viii)
12.2.7 | 19 CX 2.5 mm2 | MTRS | 2000 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 185897.2 | RC-25-27-SS-17.10(ix)
12.2.8 | 3.5CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTRS | 1000 | 1023.93 | 92.1537 | 92.1537 | 1208.2374 | 1208237.4 | RC-25-27-SS-17.20(x)
13 | Erection for OPGW System
13.1 | Erection / commissioning of SDH/MUX along with termination with FODP | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
13.2 | Erection / commissioning of digital teleprotection coupler | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986
13.3 | 24 Fibre Optic approach cable (DWSM) | Km | 1 | 45000 | 4050 | 4050 | 53100 | 53100 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
13.4 | Erection / commissioning of RTU along with fixing,cabling of MFMs | Set | 1 | 17327.87 | 1559.5083 | 1559.5083 | 20446.8866 | 20446.8866 | RC-25-27-TELC-38.a.i
13.5 | 48V,300AH,VRLA Battery set | Set | 1 | 5892.12 | 530.2908 | 530.2908 | 6952.7016 | 6952.7016 | RC-25-27-TELC-39.ii
13.6 | SMPS based Battery charger of 75A suitable for 48V VRLA Battery | No. | 1 | 5892.12 | 530.2908 | 530.2908 | 6952.7016 | 6952.7016 | RC-25-27-SS-20.ii
13.7 | Earth flat, Cable tray, telephone Cable,ACDB,DCDB,Foundation rail,Junction Box. | Set | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
13.8 | DCDB | NO. | 1 | 3547.46 | 319.2714 | 319.2714 | 4186.0028 | 4186.0028
13.9 | 2.5sqmm 2C/3C control cable laying | Mtr | 400 | 23.73 | 2.1357 | 2.1357 | 28.0014 | 11200.56
14 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).(150 watt each) | LOT | 2 | 30000 | 2700 | 2700 | 35400 | 70800 | Tentative
15.1 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos. | 40 | 4138.9831 | 372.5085 | 372.5085 | 4884 | 195360 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
15.2 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | Nos. | 40 | 431.8584 | 38.8673 | 38.8673 | 509.5929 | 20383.7168
15.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB. | Nos. | 2 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 13954
16 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | Nos. | 16 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 111632
17 | 220 KV SIDE PROTECTION & OTHER PANELS
17.1 | 220KV Feeder Protection Panel: DP MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. The panel shall be compatible with the existing panels for the substation for smooth integration with SAS. | Nos. | 2 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 75271.4448 | RC25-27 SS 18.10(ii)
17.3 | 220KV BUS-BAR Protection Sysstem (Shall be compatible with the existing busbar protection of the substation): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. The bus bar protection system shall be integrated with the Automation system. | Nos. | 2 | 31894.68 | 2870.5212 | 2870.5212 | 37635.7224 | 75271.4448 | RC25-27 SS 18.10(ii)
18 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | NOS | 30 | 200 | 18 | 18 | 236 | 7080 | Local Market Rate
19 | Inspection of Sub-Station by CEI & documentation | LS | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Local Market Rate
20 | SUBSTATION AUTOMATION SYSTEM: Erection of the following 220KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of GPS system & numerical Bay Control unit etc. | set | 1 | 25000 | 2250 | 2250 | 29500 | 29500 | Tentative
21 | AC & DC SYSTEM
21.1 | AC SYSTEM
21.1.1 | ACDB AS PER SPECIFICATION (AC DB-1.AC DB-2 WITH B/C) | SET | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC24-25-SS-H.1.3
21.1.2 | MAIN LIGHTING DISTRIBUTION BOARD (HAVING 250A MCCB AS INCOMER)AS PER SPECIFICATION (WITH DB-1.DB-2 & B/C) | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.3 | INDOOR LIGHTING DISTRIBUTION BOARD AS PER SPECIFICATION (WITH DB-I.DB-2& B/C) | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.4 | EMERGENCY LIGHTING DISTRIBUTION BOARD | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.5 | S/Y RECEPTACLE BOARD | SET | 2 | 2500 | 225 | 225 | 2950 | 5900 | LOA NO.118/22.02.19 GODISAHI GIS
21.2 | DC SYSTEM
21.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). Consider separate source(DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered.Facilities for integration with SAS as per the site requirement. | SET | 2 | 10000 | 900 | 900 | 11800 | 23600 | LOA NO.118/22.02.19 GODISAHI GIS
21.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC24-25-SS-H.1.3
| TOTAL OF ELECTRICAL WORKS (PART-A) | [6 empty] | 17509100.8678
SL. NO. | DESCRIPTION OF ITEMS ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS | UNITS | QUANTITY: For 2Nos. 220KV Bays | Unit Price (RC 14-15) / Market rate |  |  |  |  | Remarks
1 | 2 | 3
PART A | CIVIL WORKS
1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P (120*18) | SQ.MTRS. | 4320 | 5.87 | 0.5283 | 0.5283 | 6.9266 | 29922.912 | RC25-27-SS-1.10(i)
1.2 | Soil investigation : Supply of labour,T&P and other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. (15.00mtrs)
1.4.1 | Normal foundation (Boring up to 7.0m depth) | PER POINT | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.1224 | RC25-27 TL 1.5(a)
3 | CUTTING of substation area
2.1 | Cutting of earth from substation area, filling & compaction of the usable earth in the substation area and disposal of the unusable soil beyond the substation area including all T & P, labour, carriage etc complete in all respect as per the direction of Engineer in Charge. (900sqm*0.3m)
2.1.1 | Soft/loose soil | Cum | 108 | 187.16 | 16.8444 | 16.8444 | 220.8488 | 23851.6704 | RC-25-27-SS-1.20(i)
2.1.2 | Dense/ Compact soil | Cum | 108 | 296.35 | 26.6715 | 26.6715 | 349.693 | 37766.844 | RC-25-27-SS-1.20(ii)
2.1.3 | Soft/Disintegrated rock[not requiring blasting] | Cum | 324 | 608.29 | 54.7461 | 54.7461 | 717.7822 | 232561.4328 | RC-25-27-SS-1.20(iii)
4 | FILLING of substation area with borrowed earth with supply of all labour,T& P. (1050sqm*0.4*2=840cum) | [6 empty] | 0
2.2.1 | Filling with borrowed earth & compaction: beyond the substation area & up to 100mtrs lead as per the direction of Engineer in Charge. | Cum | 336 | 658.65 | 59.2785 | 59.2785 | 777.207 | 261141.552 | RC-25-27-SS-1.30(ii)
2.2..2 | Filling with borrowed earth beyond 100 mtrs lead as per the direction of Engineer in Charge. | Cum | 504 | 1170.92 | 105.3828 | 105.3828 | 1381.6856 | 696369.5424 | RC-25-27-SS-1.30(iii)
5 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod, coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation, concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge.
5.1 | EXCAVATION:
5.1.1 | Normal Soil(SOFT/LOOSE) | Cum | 1000 | 187.17 | 16.8453 | 16.8453 | 220.8606 | 220860.6 | RC-SS-25-27-2.10
5.1.2 | Dence Compact/Muddy/ PS/FS- Soil | Cum | 2000 | 296.35 | 26.6715 | 26.6715 | 349.693 | 699386 | RC-SS-25-27-2.10
| Soft Rock/Disintegrated rock (not requiring blasting) | Cum | 1000 | 662.88 | 59.6592 | 59.6592 | 782.1984 | 782198.4 | RC-SS-25-27-2.10
5.1.3 | Hard Rock required blasting | Cum | 900 | 1091.81 | 98.2629 | 98.2629 | 1288.3358 | 1159502.22 | RC-SS-25-27-2.10
5.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in for the column/equipment/marshalling box foundations column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 100 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 714910.08 | RC-SS-25-27-3.2(i)
5.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 800 | 8751.26 | 787.6134 | 787.6134 | 10326.4868 | 8261189.44 | RC-SS-25-27-3.40(i)
5.4 | Cutting, Bending, Binding Placing in position of steel rod for foundation including cost of binding wire with supply all size of rod (TATA/ RAIL/ Sail Make) | MT | 70 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 5285113.092 | RC-SS-25-27-3.5(i)
6 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Brick ,plastering (1:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}.
6.1 | Section 1-1 | LOT | 2 | 1500000 | 135000 | 135000 | 1770000 | 3540000 | Local Market Rate
6.2 | Section 2- 2
6.3 | Section 3-3
6.4 | Section 4-4
7 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing )
7.1 | Section 1-1 | Nos | 2 | 150000 | 13500 | 13500 | 177000 | 354000 | Local Market Rate
8 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Enginer In charge. Provision of drains on both the side of the roads for easy discharge of rain water. | [6 empty] | 0
8.1 | 3.75 mtrs Concrete road . | MTR | 100 | 14279.661 | 1285.1695 | 1285.1695 | 16850 | 1685000 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, Sl.48
8.2 | 7Mtr RCC Road | MTR | 250 | 20488.9831 | 1844.0085 | 1844.0085 | 24177 | 6044250
9 | Out door bay kiosks : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The internal dimensions of the Bay Kiosks are as mentioned against the switchyards below. Doors shall be heat insulated and hinge type.
9.1 | For 220KV Switchyards (1 Lot for 220KV Bay) Internal Dimensions for the Kiosk - 8m x 5.5m x 3.3m
9.1.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 544858 | 49037.22 | 49037.22 | 642932.44 | 642932.44 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 193401 | 17406.09 | 17406.09 | 228213.18 | 228213.18 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 | 94447 | 8500.23 | 8500.23 | 111447.46 | 111447.46 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 94178 | 8476.02 | 8476.02 | 111130.04 | 111130.04 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 25464 | 2291.76 | 2291.76 | 30047.52 | 30047.52 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 90945 | 8185.05 | 8185.05 | 107315.1 | 107315.1 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 79083 | 7117.47 | 7117.47 | 93317.94 | 93317.94 | LoA No.221,Dt.01.02.25 (Neulpoi)
10 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 420 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 3002622.336 | RC-SS-25-27-3.2(i)
11 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 560 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 2191384.608 | RC25-27-SS-5.10
12 | RCC Retaining (4 mtr height) cum boundary wall : Design, engineering, supply of all labour, material (Supply of Cement, coarse and fine aggregates and construction of PCC (1:3:6) & RCC (1:1.5:3) as per requirement including excavation, concreting, shuttering and back filling of open cast grade beam concreting etc complete for the boundary walls, as per the approved drawings. (140Mtr length) | LOT | 2 | 2500000 | 225000 | 225000 | 2950000 | 5900000 | Local Market Rate
13 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick masonry work with ratio 1:5 and cement pointing of the joints, for the fencing up to a height from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | LOT | 2 | 350000 | 31500 | 31500 | 413000 | 826000 | Local Market Rate
14 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 2 | 150000 | 13500 | 13500 | 177000 | 354000 | Local Market Rate
15 | Anti-Weed Treatment | [6 empty] | 0
15.1 | Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treatment of the switch-yard areas,controlroom etc.- spraying of anti weed chemicals/ pesticides(Burachlora/Glyphoss) for destoying of wild plants, grass, shrubs bushed etc. inside swithyard as per the instruction of Engineer-in-Charge. | Sq.Mtrs | 20000 | 18 | 1.62 | 1.62 | 21.24 | 424800 | Local Market Rate
| TOTAL OF SUBSTATION (Civil Work) | [6 empty] | 44118582.532
| PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 220KV SUB-STATION WORK) | [6 empty] | 61627683.3998
Note on B12: OPTCL: Turumunga is 2 main & transfer bus?

## SUMMERY UNCHABALI SS
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at 220/132/33KV GSS Turumunga
S U M M A R Y PART-A (FOR 220 KV BAY EXTENSION)
Sl.No. | Description | Amount (in Rs.)
1 | Total Cost of materials (PART-I SCHEDULE-VIIA including GST | 78421811.9558
2 | Stock, Storage & Insurance(@3% on Sl.No-1 | 2352654.3587
3 | Sub-Total(1+2) | 80774466.3145
4 | Contingency 3% on Sl.No.3 | 2423233.9894
5 | T&P cost @ 2% on Sl.No. 3 | 1615489.3263
6 | Transportation @ 5% on Sl.No.3 | 4038723.3157
7 | Total Cost of Supply(Sl No.3 to Sl No.6) | 88851912.9459
8 | Total erection Chages (PART-I, SCHEDULE-VIIB & VIIC including GST | 56601825.3078
9 | Total Cost of the Supply & Erection (Sl No.7+Sl No.8) | 145453738.2537
11 | Or Say | 145453738

## N&B (hidden)
SL | TYPE OF TOWER | QNTY | 30MM | TOTAL | 35MM | TOTAL | 40MM | TOTAL | 45MM | TOTAL | 50MM | TOTAL | 55MM | TOTAL | 60MM | TOTAL | 65MM | TOTAL | 70MM | TOTAL | 75MM | TOTAL | 80MM | TOTAL | 150MM | TOTAL | 175MM | TOTAL | N&B PER TOWER | TOTAL OF BOLT & NUT
FOR 220KV LINE |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1 | OC' TYPE STUB | 13 |  | 0 |  | 0 |  | 0 | 3.24 | 42.12 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 3.58 | 46.54
2 | OC' TYPE TEMPLATE | 1 |  | 0 | 15.708 | 15.708 |  | 0 |  | 0 | 3.432 | 3.432 | 1.208 | 1.208 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 25.14 | 25.14
3 | OC+0 TYPE TOWER | 22 | 7.303 | 160.666 | 73.423 | 1615.306 | 50.419 | 1109.218 | 53.73 | 1182.06 | 34.034 | 748.748 | 7.399 | 162.778 | 30.652 | 674.344 | 17.49 | 384.78 |  | 0 |  | 0 |  | 0 | 49.5 | 1089 |  | 0 | 346.25 | 7617.5
4 | OC+3 TYPE TOWER | 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42.35 | 254.1
5 | OC+6 TYPE TOWER | 3 | 3.597 | 10.791 | 25.109 | 75.327 |  | 0 | 8.37 | 25.11 | 4.433 | 13.299 |  | 0 |  | 0 | 17.49 | 52.47 |  | 0 |  | 0 |  | 0 | 6.75 | 20.25 |  | 0 | 71.04 | 213.12
6 | OC+9 TYPE TOWER | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
7 | OC+15,24 TEMPLATE | 1 |  | 0 | 19.04 | 19.04 | 11.684 | 11.684 | 1.08 | 1.08 | 1.144 | 1.144 | 4.832 | 4.832 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41.97 | 41.97
8 | OC+15 TYPE STUB | 4 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 18.304 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 20.12
9 | OC+15 TYPE TOWER | 4 |  | 0 | 32.13 | 128.52 | 13.208 | 52.832 | 27 | 108 | 8.58 | 34.32 | 5.436 | 21.744 |  | 0 |  | 0 | 41.28 | 165.12 | 22.912 | 91.648 |  | 0 | 19.5 | 78 |  | 0 | 188.29 | 753.16
10 | OC+24 TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 22.88 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 25.15
11 | OC+24 TYPE TOWER | 5 |  | 0 | 15.232 | 76.16 | 27.94 | 139.7 | 52.38 | 261.9 | 22.88 | 114.4 | 15.704 | 78.52 | 3.14 | 15.7 | 18.368 | 91.84 | 66.736 | 333.68 | 25.92 | 129.6 |  | 0 | 42 | 210 |  | 0 | 304.66 | 1523.3
8 | OC+15 TYPE STUB | 4 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 18.304 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 20.12
9 | OC+15 TYPE TOWER | 4 |  | 0 | 32.13 | 128.52 | 13.208 | 52.832 | 27 | 108 | 8.58 | 34.32 | 5.436 | 21.744 |  | 0 |  | 0 | 41.28 | 165.12 | 22.912 | 91.648 |  | 0 | 19.5 | 78 |  | 0 | 188.29 | 753.16
10 | OC+24 TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 22.88 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 25.15
11 | OC+24 TYPE TOWER | 5 |  | 0 | 15.232 | 76.16 | 27.94 | 139.7 | 52.38 | 261.9 | 22.88 | 114.4 | 15.704 | 78.52 | 3.14 | 15.7 | 18.368 | 91.84 | 66.736 | 333.68 | 25.92 | 129.6 |  | 0 | 42 | 210 |  | 0 | 304.66 | 1523.3
| TOTAL |  |  | 171.457 |  | 2134.741 |  | 1505.966 |  | 1990.17 |  | 1146.431 |  | 369.346 |  | 705.744 |  | 620.93 |  | 997.6 |  | 442.496 |  | 0 |  | 1685.25 |  | 0 |  | 12841.83
1 | UR' TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 2.288 | 11.44 | 2.416 | 12.08 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 9.86 | 49.3
2 | UR' TYPE TEMPLATE | 1 | 1.744 | 1.744 | 22.372 | 22.372 | 2.794 | 2.794 | 1.08 | 1.08 | 4.004 | 4.004 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 35.57 | 35.57
3 | UR+0 TYPE TOWER | 5 | 6.976 | 34.88 | 59.5 | 297.5 | 47.244 | 236.22 | 38.745 | 193.725 | 43.186 | 215.93 | 25.67 | 128.35 | 36.024 | 180.12 | 59.4 | 297 |  | 0 |  | 0 |  | 0 |  | 0 | 35.109 | 175.545 | 401.21 | 2006.05
4 | UR+3 TYPE TOWER | 0 | 0.952 | 0 | 11.176 | 0 | 8.636 | 0 | 3.24 | 0 | 4.576 | 0 | 2.416 | 0 | 1.264 | 0 | 18.48 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1.125 | 0 | 26.57 | 0
5 | UR+6 TYPE TOWER | 5 |  | 0 | 7.616 | 38.08 | 5.08 | 25.4 | 23.22 | 116.1 | 4.576 | 22.88 | 6.04 | 30.2 | 1.264 | 6.32 | 36.96 | 184.8 |  | 0 |  | 0 |  | 0 |  | 0 | 3 | 15 | 97.28 | 486.4
| TOTAL |  |  | 36.624 |  | 357.952 |  | 264.414 |  | 310.905 |  | 254.254 |  | 170.63 |  | 186.44 |  | 481.8 |  | 0 |  | 0 |  | 0 |  | 0 |  | 190.545 |  | 2577.32
1 | MONO POLE TOWER(400KV) | 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2 | +25 MTR TO PD TYPE | 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 6500 | 13000
| TOTAL |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 13000
| GRAND TOTAL |  |  | 208.081 |  | 2492.693 |  | 1770.38 |  | 2301.075 |  | 1400.685 |  | 539.976 |  | 892.184 |  | 1102.73 |  | 997.6 |  | 442.496 |  | 0 |  | 1685.25 |  | 190.545 |  | 28419.15
[29 empty] | IN MT | 28.4192