## CALCULATION SHEET (hidden)
0 |  | CALCULATION SHEET
SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
1 | PA+0 | 4 | 63.36 | 253.44 | 0.968 | 3.872 | 8.76 | 35.04 | 0.201 | 0.804
2 | PA+3 | 1 | 70 | 70 | 0.968 | 0.968 | 9.72 | 9.72 | 0.201 | 0.201
3 | PA+6 | 1 | 70 | 70 | 0.968 | 0.968 | 9.72 | 9.72 | 0.201 | 0.201
4 | PB+0 | 1 | 104.43 | 104.43 | 1.5125 | 1.5125 | 15.49 | 15.49 | 0.272 | 0.272
5 | PB+3 | 1 | 113.49 | 113.49 | 1.5125 | 1.5125 | 17 | 17 | 0.272 | 0.272
6 | PB+6 | 1 | 113.49 | 113.49 | 1.5125 | 1.5125 | 17 | 17 | 0.272 | 0.272
7 | PC+0 | 2 | 141.54 | 283.08 | 1.74 | 3.48 | 20.64 | 41.28 | 0.309 | 0.618
8 | PC+3 | 1 | 141.54 | 141.54 | 1.74 | 1.74 | 20.64 | 20.64 | 0.309 | 0.309
9 | PC+6 |  | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
10 | OB+3 |  | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
11 | OB+6 |  | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
12 | OC+0 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
13 | OC+3 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
14 | OC+6 |  | 212.94 | 0 | 5.184 | 0 | 35.397 | 0 | 0.422 | 0
15 | OC+15 |  | 360 | 0 | 10 | 0 | 59 | 0 | 5.6 | 0
16 | OC+24 |  | 390 | 0 | 11 | 0 | 65 | 0 | 5.9 | 0
17 | UR+0 |  | 216.75 | 0 | 7.225 | 0 | 52.04 | 0 | 0.534 | 0
18 | UR+6 |  | 216.75 | 0 | 7.225 | 0 | 52.04 | 0 | 0.534 | 0
19 | DD+0 |  | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
20 | DD+3 |  | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
|  | 12 |  | 1149.47 |  | 15.5655 |  | 165.89 |  | 2.949
SL NO | AP | TOWER | ST FITTING | DT FITTING | SS FITTINg | DS FITTING | VIBRATION DAMPER | EARTHING DEVICE
1 | GANTRY | GANTRY | 3 | 0 | 0 | 0 | 3 | 0
2 | AP 01 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
3 | AP 02 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
4 | AP 03 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
5 | AP 04 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
6 | AP 05 | OC+24 | 0 | 6 | 0 | 0 | 6 | 2
7 | AP 06 | OC+15 | 3 | 3 | 0 | 0 | 6 | 2
8 | AP 07 | OC+15 | 6 | 0 | 0 | 0 | 6 | 1
9 | AP 08 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
10 | AP 09 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
11 | AP 10 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
12 | AP 11 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
13 | AP 12 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
14 | AP12/1 | PA+6 | 0 | 0 | 3 | 0 | 6 | 1
15 | AP 13 | PB+3 | 3 | 3 | 0 | 0 | 6 | 1
16 | AP 14 | PC+3 | 3 | 3 | 0 | 0 | 6 | 1
17 | AP 15 | PB+03 | 3 | 3 | 0 | 0 | 6 | 1
18 | AP 16 | PB+0 | 3 | 3 | 0 | 0 | 6 | 1
19 | AP 17 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
20 | AP 18 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
21 | AP 19 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
22 | AP 20 | PB+03 | 3 | 3 | 0 | 0 | 6 | 1
23 | AP 21 | PC+0 | 3 | 3 | 0 | 0 | 6 | 1
24 | AP 22 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
25 | AP 23 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
26 | AP 23/1 | PA+0 | 0 | 0 | 3 | 0 | 6 | 1
27 | AP 24 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
28 | AP 25 | PC+0 | 6 | 0 | 0 | 0 | 6 | 1
29 | AP 26 | DD+0 | 0 | 3 | 0 | 0 | 3 | 9
30 | AP 27 | DD+3 | 3 | 0 | 0 | 0 | 3 | 9
31 | AP 28 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
32 | AP 29 | OC+6 | 6 | 0 | 0 | 0 | 6 | 1
33 | AP 30 | OC+3 | 6 | 0 | 0 | 0 | 6 | 1
34 | AP 31 | OC+0 | 6 | 0 | 0 | 0 | 6 | 1
35 | AP 32 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
36 | AP 33 | OC+3 | 6 | 0 | 0 | 0 | 6 | 1
37 | AP 34 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
38 | AP34/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
39 | AP 35 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
40 | AP 36 | OC+15 | 6 | 0 | 0 | 0 | 6 | 1
41 | AP 37 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
42 | AP 38 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
43 | AP 39 | OC+6 | 6 | 0 | 0 | 0 | 6 | 1
44 | AP 40 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
45 | AP 41 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
46 | AP 42 | OC+6 | 3 | 3 | 0 | 0 | 6 | 2
47 | AP 43 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
48 | AP43/1 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
49 | AP 44 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
50 | AP 45 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
51 | AP 45/1 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
52 | AP 45/2 | PB+0 | 6 | 0 | 0 | 0 | 6 | 1
53 | AP 46 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
54 | AP 47 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
55 | AP 48 | OC+24 | 3 | 3 | 0 | 0 | 6 | 2
56 | AP 49 | OC+24 | 0 | 6 | 0 | 0 | 6 | 2
57 | AP 50 | OC+15 | 3 | 3 | 0 | 0 | 6 | 2
58 | AP 51 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
59 | AP 51/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
60 | AP 52 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
61 | AP 53 | OB+3 | 6 | 0 | 0 | 0 | 6 | 1
62 | AP 54 | PC+6 | 6 | 0 | 0 | 0 | 6 | 1
63 | AP 54/1 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
64 | AP 55 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
65 | AP 55/1 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
66 | AP 56 | OC+24 | 6 | 0 | 0 | 0 | 6 | 1
67 | AP 57 | UR+0 | 6 | 0 | 0 | 0 | 6 | 1
68 | AP 57/1 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
69 | AP 57/2 | OB+6 | 6 | 0 | 0 | 0 | 6 | 1
70 | AP 57/3 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
71 | AP 57/4 | PB+3 | 6 | 0 | 0 | 0 | 6 | 1
72 | AP 58 | OC+3 | 3 | 3 | 0 | 0 | 6 | 1
73 | AP 58/1 | OB+3 | 3 | 3 | 0 | 0 | 6 | 1
74 | AP 58/2 | UR+6 | 6 | 0 | 0 | 0 | 6 | 1
75 | AP 59 | PC+0 | 3 | 3 | 0 | 0 | 6 | 1
76 | AP 60 | PC+3 | 0 | 6 | 0 | 0 | 6 | 1
77 | AP 60/1 | PA+3 | 0 | 0 | 0 | 3 | 6 | 1
78 | AP 61 | PC+3 | 6 | 0 | 0 | 0 | 6 | 1
79 | AP 62 | DD+0 | 3 | 0 | 0 | 0 | 3 | 9
80 | GANTRY | GANTRY | 3 | 0 | 0 | 0 | 3 | 0
|  |  | 381 | 66 | 6 | 3 | 465 | 110

## LINE SUPPLY
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 220 KV TURUMUNGA-BASUDEVPUR D/C Line along with 2Nos. 220KV Bays extension at Turumunga GSS
Conductor- ACSR ZEBRA |  | Total length of over head line- 49.968 RKM.
Earth wire- OPGW |  | Total towers- 225
No. of Ciruit- DC line on DC tower |  | Angle towers- 60Nos.
SCHEDULE-VIIA-SUPPLY (FOR 220 KV TURUMUNGA-BASUDEVPUR D/C LINE)
Sl. No. |  | Unit | Qnty | IN INR
| DESCRIPTION OF ITEMS |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3 | 4 | 5 |  |  |  | 7=4*6
1 | SUPPLY of following type tested Lattice type Galvanized steel Tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification.
1.1 | TOWER SUPER STRUCTURES
1.1.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.250 MT) - 165Nos. | MT | 701.25
1.1.1.1 | +3 EXTENSION ( 0.751 MT) - 35Nos. | MT | 26.285
1.1.1.2 | +6 EXTENSION ( 1.497 MT) - 20Nos. | MT | 29.94
1.1.2 | OB TYPE (30 deg ANGLE ) TOWERS ( 6.343 MT) - 20Nos. | MT | 126.86
1.1.2.1 | +3 EXTENSION ( 1.336 MT) - 6Nos. | MT | 8.016
1.1.2.2 | +6 MTR EXTENSION to OB ( 2.321 MT)- 4Nos. | MT | 9.284
1.1.3 | OC TYPE (60 deg ANGLE ) TOWERS ( 9.014) - 20Nos. | MT | 180.28
1.1.3.1 | +3 EXTENSION ( 1.468 MT) - 6 NOS. | MT | 8.808
1.1.3.2 | +6 EXTENSION ( 2.618 MT) - 4 NOS. | MT | 10.472
1.1.4 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 20 NOS. | MT | 248.76
1.1.4.1 | +6 EXTENSION ( 4.161MT) - 20 NOS. | MT | 83.22
1.5 | MA TYPE MULTI CIRCUIT ( HT-6.303+MS-7.981= 23.001 MT +STUB 1.309 MT) - 20 NOS. | MT
1.5.1 | HT materials for 0 mtr Extension | MT
1.5.2 | MS materials for 0 mtr extension | MT
1.5.3 | +3 EXTENSION ( HT-0.723+ MS-0.944 MT) - 6NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.3 | +6 EXTENSION ( HT-1.186+ MS-1.711 MT) - 4NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5 | MB TYPE ( ANGLE TOWERS) MULTI CIRCUIT ( HT-10.654+MS-12.347= 23.001 MT +STUB 1.309 MT) - 0No. | MT
1.5.1 | HT materials for 0 mtr Extension | MT
1.5.2 | MS materials for 0 mtr extension | MT
1.5.3 | +3 EXTENSION ( HT-1.002+ MS-1.769 MT) -NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.3 | +6 EXTENSION ( HT-1.729+ MS-2.874 MT) -NO. | MT
1.5.4 | HT materials for +6 extension | MT
1.5.5 | MS materials for +6 extension | MT
1.5.6 | +9 EXTENSION ( 6.488 MT) - 1 NO. | MT
1.5.7 | HT materials for +9 extension (2.402MT) | MT
1.5.8 | MS materials for +9 extension (4.086MT) | MT
1.6 | MC TYPE ( ANGLE TOWERS) MULTI CIRCUIT - (HT-15.658+MS-13.341=28.999MT)- 10Nos. | MT
1.6.2 | HT materials for +0 extension 15.658 MT | MT
1.6.3 | MS materials for +0 extension 13.341 MT | MT
1.6.4 | +3 EXTENSION ( HT-1.559+ MS-2.037 MT) - 3 Nos. | MT
1.6.5 | HT materials for +6 extension 1.559 MT | MT
1.6.6 | MS materials for +6 extension 2.037 MT | MT
1.6.4 | +6 EXTENSION ( HT-2.707+ MS-3.233 MT) - 02 NO. | MT
1.6.5 | HT materials for +6 extension 2.707 MT | MT
1.6.6 | MS materials for +6 extension 3.233 MT | MT
1.2 | STUBS & CLEATS
1.2.1 | OA TYPE( 0.230 MT)- 165 | MT | 37.95
1.2.2 | OB TYPE ( 0.436 MT)-20 | MT | 8.72
1.2.3 | OC TYPE ( 0.774 MT)-20 | MT | 15.48
1.2.4 | UR TYPE ( 0.697 MT)- 20 | MT | 13.94
1.3 | TEMPLATES
1.3.1 | OA ( 0.580 MT)- 10Nos. | MT | 5.8
1.3.2 | OB ( 0.794 MT) - 3Nos. | MT | 2.382
1.3.3 | OC ( 0.962 MT) - 3Nos. | MT | 2.886
1.3.4 | UR+6 ( 1.476 MT)- 04Nos. | MT | 5.904
1.4 | WEIGHT OF THE STRUCTURES (including Towers, stubs, cleats & templates) | MT | 1509.265 | 90371.05 | 8133.3945 | 8133.3945 | 106637.839 | 160944758.0783 | CD 24-25 Line sl.2
1.5 | MS enamel painted templates | MT | 16.972 | 69832.18 | 6284.8962 | 6284.8962 | 82401.9724 | 1398526.2756 | CD 24-25 Line sl.6
1.6 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 76.3119 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 10676148.2961 | CD 24-25 Line sl.5
2 | Supply of the following tower accessories as per technical specification.
2.1 | EARTHING DEVICE | Nos. | 450 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 1211200.38 | CD 24-25 Line sl.8
2.2 | DANGER BOARD | Nos. | 225 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 62862.435 | CD 24-25 Line sl.9
2.3 | NUMBER PLATE | Nos. | 450 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 68700.78 | CD 24-25 Line sl.10
2.4 | PHASE PLATE | Nos. | 1350 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 160765.56 | CD 24-25 Line sl.11
2.5 | BIRD GUARD | Nos. | 990 | 524.7398 | 47.2266 | 47.2266 | 619.193 | 613001.0767 | LOA NO.137,Dt.16.02.23 (Turumunga -Dhenkikote), Line 2.5
2.6 | ANTICLIMBING DEVICE | Nos. | 225 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 1168261.065 | CD 24-25 Line sl.13
2.7 | CIRCUIT PLATE | Nos. | 450 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 53588.52 | CD 24-25 Line sl.12
2.8 | 75X10 MM GI FLAT | MT | 20 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 2205464.604 | CD 24-25-Line-4
3 | Supply of following POWER CONDUCTORS as per the technical specification
3.1 | ACSR ZEBRA | Kms. | 304.3051 | 363162.06 | 32684.5854 | 32684.5854 | 428531.2308 | 130404247.6123 | CD 24-25 Line sl.18
4 | POWER CONDUCTOR ACESSORIES (For ACSR ZEBRA)
4.1 | VIBRATION DAMPER | Nos. | 2700 | 756.44 | 68.0796 | 68.0796 | 892.5992 | 2410017.84 | CD 24-25 Line sl.29
4.2 | MID SPAN JOINT | Nos. | 300 | 797.33 | 71.7597 | 71.7597 | 940.8494 | 282254.82 | CD 24-25 Line sl.34
4.3 | Repair Sleeve | Nos. | 200 | 324.04 | 29.1636 | 29.1636 | 382.3672 | 76473.44 | CD 24-25 Line sl.40
4.4 | Performed Armoured Rod | Set | 990 | 1167.1 | 105.039 | 105.039 | 1377.178 | 1363406.22 | CD 24-25 Line sl.26
5 | Supply of the following Porcelain Antifog Disc Insulators as per the technical specification and as per the instruction of the Engineer in charge.
5.1 | 160 KN Porcelain Antifog Disc Insulators | Nos. | 13230 | 807.9 | 72.711 | 72.711 | 953.322 | 12612450.06 | CD 24-25 Line sl.64 | 198450
5.2 | 120 KN Porcelain Antifog Disc Insulators | Nos. | 14560 | 720.04 | 64.8036 | 64.8036 | 849.6472 | 12370863.232 | CD 24-25 Line sl.65 | 203840
6 | Supply of the following hard ware fittings suitable for ACSR Zebra conductors as per the technical specification.
6.1 | Single Suspension Hard wares fittings (AGS Type, Including Armoured Rod) (1x120kN) | Nos. | 990 | 2698.67 | 242.8803 | 242.8803 | 3184.4306 | 3152586.294 | CD 24-25 Line sl.15
6.2 | Double suspension Hard wares fittings (2x120kN) | Nos. | 0 | 4566.27 | 410.9643 | 410.9643 | 5388.1986 | 0 | CD 24-25 Line sl.16
6.3 | Single Tension Hardware fittings (1 x160kN) | Nos. | 600 | 2076.13 | 186.8517 | 186.8517 | 2449.8334 | 1469900.04 | CD 24-25 Line sl.17
6.4 | Double tension Hardware fittings (2x160kN) | Nos. | 120 | 4735.96 | 426.2364 | 426.2364 | 5588.4328 | 670611.936 | CD 24-25 Line sl.18
6.5 | “D” Shackle | Nos. | 720 | 310 | 27.9 | 27.9 | 365.8 | 263376
6.6 | Hanger | Nos. | 990 | 592 | 53.28 | 53.28 | 698.56 | 691574.4
6.7 | U'-Bolt. | Nos. | 165 | 137 | 12.33 | 12.33 | 161.66 | 26673.9
7 | Supply of OPGW Cable & Hardware fittings
7.1 | Supply of OPGW(DWSM) Fibre Optic Cable 24F | KM | 50.7175 | 190400 | 17136 | 17136 | 224672 | 11394806.6534 | CD24-25-TEL-23
7.2 | Hardware set for 24F OPGW as per the list below required per Km. like suspension Assembly,Tensin Assembly(Dead end assembly, Pass through assembly) ,Vibration Damper,Down Lead Clamp Assemblies for 24/48 Fibre(DWSM) OPGW,Earth bond,Link plates | KM | 49.968 | 22597.72 | 2033.7948 | 2033.7948 | 26665.3096 | 1332412.1901 | CD 24-25-TEL-24
7.3 | Joint Box (splice enclosure),24F | NO. | 20 | 4525.2 | 407.268 | 407.268 | 5339.736 | 106794.72 | CD 24-25-TEL-27
| TOTAL SCHEDULE-VII A (FOR 220 KV TURUMUNGA-BASUDEVPUR D/C LINE) | [6 empty] | 357191726.4286
| Estimator |  |  | Deputy General Manager (Elect.),
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar
Weight of different type G.I Nuts and Bolts for the above structures (1.13*3+170.28*3+25062+50.02+1.19*16+212.37*16+43.4*10+1.34*25+301.55*25+50.5*13+98.34*4+3.88*7+346.25*7+42.35*3+71.04*3+9.86*9+401.21*9+97.28*8+5.03*10+346.25*10+188.29*4+304.66*6+14.65*3+984.84*3+113.8+19.74+18.84+23.28+35.57+35.04+25.14+41.97*2+35=29,814.63kg)

## LINE SERVICE
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
Name of of Works: Construction of 220 KV TURUMUNGA-BASUDEVPUR D/C Line along with 2Nos. 220KV Bays extension at Turumunga GSS
Conductor- ACSR ZEBRA |  | Total length of over head line- 49.968 RKM.
Earth wire- OPGW |  | Total towers- 225
No. of Ciruit- DC line on DC tower |  | Angle towers- 60Nos.
PART SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (220KV 220 KV TURUMUNGA-BASUDEVPUR D/C LINE ) | [9 empty] | 49.4
Sl. No. | DESCRIPTION OF ITEMS | Unit | QTY | IN INR
| DESCRIPTION OF ITEMS |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=5+6+7 | 9=4X8 | 10
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. This includes supply of all labourers, T&P, head loading of all type of structures, & other materials required for erection. All Erection should confirm to the Technical Specification laid there in the Tender Specification.
1.1 | TOWER SUPER STRUCTURES
1.1.1 | OA TYPE (SUSPENSION) TOWERS ( 4.250 MT) - 165Nos. | MT | 701.25
1.1.1.1 | +3 EXTENSION ( 0.751 MT) - 35Nos. | MT | 26.285
1.1.1.2 | +6 EXTENSION ( 1.497 MT) - 20Nos. | MT | 29.94
1.1.2 | OB TYPE (30 deg ANGLE ) TOWERS ( 6.343 MT) - 20Nos. | MT | 126.86
1.1.2.1 | +3 EXTENSION ( 1.336 MT) - 6Nos. | MT | 8.016
1.1.2.2 | +6 MTR EXTENSION to OB ( 2.321 MT)- 4Nos. | MT | 9.284
1.1.3 | OC TYPE (60 deg ANGLE ) TOWERS ( 9.014) - 20Nos. | MT | 180.28
1.1.3.1 | +3 EXTENSION ( 1.468 MT) - 6 NOS. | MT | 198.308
1.1.3.2 | +6 EXTENSION ( 2.618 MT) - 4 NOS. | MT | 10.472
1.1.4 | UR TYPE (60 deg ANGLE ) TOWERS ( 12.438) - 20 NOS. | MT | 248.76
1.1.4.1 | +6 EXTENSION ( 4.161MT) - 20 NOS. | MT | 83.22
1.2 | STUBS & CLEATS
1.2.1 | OA TYPE( 0.230 MT)- 165 | MT | 37.95
1.2.2 | OB TYPE ( 0.436 MT)-20 | MT | 8.72
1.2.3 | OC TYPE ( 0.774 MT)-20 | MT | 15.48
1.2.4 | UR TYPE ( 0.697 MT)- 20 | MT | 13.94
1.3 | TEMPLATES
1.3.1 | OA ( 0.580 MT)- 165Nos. | MT | 95.7
1.3.2 | OB ( 0.794 MT) - 20Nos. | MT | 15.88
1.3.3 | OC ( 0.962 MT) - 20Nos. | MT | 19.24
1.3.4 | UR+6 ( 1.476 MT)- 20Nos. | MT | 29.52
1.4 | WEIGHT OF THE STRUCTURES (including Towers, stubs, cleats) | MT | 1622.675 | 7265.49 | 653.8941 | 653.8941 | 8573.2782 | 13911644.2032 | RC25-26 TL 1.1(i)
1.5 | WEIGHT OF THE STRUCTURES (templates) | MT | 236.43 | 5596.02 | 503.6418 | 503.6418 | 6603.3036 | 1561219.0701 | RC25-26 TL 1.1
1.6 | Weight of different type G.I Nuts and Bolts for the above structures | MT | 76.3119 | 7265.49 | 653.8941 | 653.8941 | 8573.2782 | 654242.72 | RC25-26 TL 1.1(i)
2 | Erection of the following tower accessories as per technical specification. | [6 empty] | 0
2.1 | EARTHING OF TOWER: Pipe type earthing including cost of bentonate compound and good borrowed earth where necessary in accordance with IS:3043-1966 and with supply of all T&P and Labour, with excavation of Morrum and laterite layer and back filling with good borrowed earth.- i)Without cost of earthing pipe (50mm Dia 3050mm length medium gauge) and GI flat | Nos. | 450 | 3021.59 | 271.9431 | 271.9431 | 3565.4762 | 1604464.29 | RC25-26 TL EARTHING 1.1(i)
2.2 | DANGER BOARD | Nos. | 225 | 156.86 | 14.1174 | 14.1174 | 185.0948 | 41646.33 | RC25-26 TL-H-11(ii)
2.3 | NUMBER PLATE | Nos. | 450 | 156.86 | 14.1174 | 14.1174 | 185.0948 | 83292.66 | RC25-26 TL-H-11(ii)
2.4 | PHASE PLATE | Nos. | 1350 | 156.86 | 14.1174 | 14.1174 | 185.0948 | 249877.98 | RC25-26 TL-H-11(ii)
2.5 | BIRD GUARD | Nos. | 990 | 156.86 | 14.1174 | 14.1174 | 185.0948 | 183243.852 | RC25-26 TL-H-11(ii)
2.6 | ANTICLIMBING DEVICE | Nos. | 225 | 3385.07 | 304.6563 | 304.6563 | 3994.3826 | 898736.085 | RC25-26 TL-H-11(v)
2.7 | CIRCUIT PLATE | Nos. | 450 | 156.86 | 14.1174 | 14.1174 | 185.0948 | 83292.66 | RC25-26 TL-H-11(ii)
3 | Hoisting and fixing of insulators with required accessories, paying out of conductor, jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire & OPGW in the proposed lines with all required accessories including scaffolding/other required arrangements for 33 KV,11 KV, LT , P&T lines, NH/roads, railway line, river etc and using own required T&P and compression jointing machines etc. as per the direction of Engineer in charge. | [6 empty] | 0
3.1 | ACSR ZEBRA | RKM | 49.968 | 94121.17 | 8470.9053 | 8470.9053 | 111062.9806 | 5549595.0146 | RC25-26 TL-1.1.1.b.i
| Additional charges for stringing EHT line crossing/railway/ National highway crossing | RKM | 6.5 | 21383.68 | 1924.5312 | 1924.5312 | 25232.7424 | 164012.8256 | RC25-26 TL-10.10.(III)b(i)
4 | ERECTION OF OPGW CABLE | [6 empty] | 0
4.1 | 24F/48F OPGW stringing without supply of required HWF, tension assembly set, suspension assembly set, vibration damper set etc.(Under offline condition) | KM | 49.968 | 45000 | 4050 | 4050 | 53100 | 2653300.8 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
| TOTAL OF ELECTRICAL WORKS (PART-A) | [6 empty] | 27638568.4906
CIVIL WORKS
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | Preliminary survey - Making walkover survey ascertaining feasibile route and marking on TOposheet, preparation of route alignment | KM. | 49.968 | 4953.75 | 445.8375 | 445.8375 | 5845.425 | 292084.1964 | RC25-26 TL-Survey-1.1
1.1 | Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 49.968 | 14035.61 | 1263.2049 | 1263.2049 | 16562.0198 | 827571.0054 | RC25-26 TL-Survey-1.2
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 49.968 | 6604.99 | 594.4491 | 594.4491 | 7793.8882 | 389445.0056 | RC25-26 TL-Survey-1.4
1.3 | Preparation of land schedule on revenue (if required)maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 132 KV line. Final route to be plotted on 1:50000 topo sheet for approval.Detail GIS (Geographical Information System) of towers to be included. | KM. | 49.968 | 10733.12 | 965.9808 | 965.9808 | 12665.0816 | 632848.7974 | RC25-26 TL-Survey-1.3
1.4 | Soil Testing in complete shape along with submission of report etc. | [6 empty] | 0
1.4.1 | Normal foundation (Boring up to 7.0m depth) | Per Loc. | 75 | 28071.23 | 2526.4107 | 2526.4107 | 33124.0514 | 2484303.855 | RC25-26 TL-Survey-1.5(a)
1.4.2 | Under ream pilee foundation (boring up to 15.0m depth) | Per Loc. | 7 | 37978.72 | 3418.0848 | 3418.0848 | 44814.8896 | 313704.2272 | RC25-26 TL-Survey-1.5(b)
2 | EXCAVATION WORKS FOR OPEN CAST/SHALLOW TYPE FOUNDATIONS | [6 empty] | 0
2.1 | Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposal of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge ( Total 27000 CUM) | [6 empty] | 0
2.1.1 | Soft/Loose soil | CUM | 2700 | 228.78 | 20.5902 | 20.5902 | 269.9604 | 728893.08 | RC25-26 TL-EXC-1(i)
2.1.2 | Dense / compact soil | CUM | 5400 | 358.41 | 32.2569 | 32.2569 | 422.9238 | 2283788.52 | RC25-26 TL-EXC-1(ii)
2.1.3 | Partially submerged soil | CUM | 5400 | 411.79 | 37.0611 | 37.0611 | 485.9122 | 2623925.88 | RC25-26 TL-EXC-1(vi)
2.1.3 | Fully submerged soil | CUM | 1350 | 411.79 | 37.0611 | 37.0611 | 485.9122 | 655981.47 | RC25-26 TL-EXC-1(v)
2.1.4 | Soft/Disintegrated rock(Not requiring Blasting) | CUM | 4050 | 686.31 | 61.7679 | 61.7679 | 809.8458 | 3279875.49 | RC25-26 TL-EXC-1(iii)
2.1.5 | Hard Rock(Requiring Blasting/Using breaker machinery) | CUM | 8100 | 1372.61 | 123.5349 | 123.5349 | 1619.6798 | 13119406.38 | RC25-26 TL-EXC-1(iv)
3 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. This includes the open cast foundations, Piles, Pile cappings, risers, chimney, rivetment works etc. | [6 empty] | 0
3.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower open foundations, pile cappings and rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 550 | 6218.65 | 559.6785 | 559.6785 | 7338.007 | 4035903.85 | RC25-26 TL-FDN-1.2(iii)
3.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation, 500mm under ream piles, pile caps, chimney, risers (if any) with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement for tower open foundations, 500mm Under-reamed piles, all pile cappings risers, chimey etc. and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, dewatering, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The height of the coping shall be 350mm above the finished concrete level. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P, head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 5500 | 8877.05 | 798.9345 | 798.9345 | 10474.919 | 57612054.5 | RC25-26 TL-FDN-1.4(i)
3.4 | Supply of all materials like cement, coarse aggregates (Nominal size 12mm to 20mm), fine aggregates and making 1000mm river bed pile foundations (after pile boring as per required depth, basing on design) as per requirement, including supply of all equipment with labours, head loading of all type of Civil materials , proper curing of the foundations and T&P as per specification in the concrete ratio 1:1:2 and disposal of excess earth as per the direction of Engineer In Charge. | MT | 85 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 6570782.387 | RC25-26 TL-FDN-1.1
4 | WELDING OF TOWER MEMBERS |  |  |  | 0 | 0 | 0 | 0
4.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator.), application of required zinc rich paints around the welding portion after welding (two coats),fuel,lubricants,T&P and labours and other arrangements etc. | Nos. | 400000 | 10.01 | 0.9009 | 0.9009 | 11.8118 | 4724720 | RC25-26 TL-Fabrication-1.1(i)
5 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | [6 empty] | 0
5.1 | Excavation and Back filling (as per approved drawing) | [6 empty] | 0
5.1.1 | Soft/loose soil | CUM | 3000 | 228.78 | 20.5902 | 20.5902 | 269.9604 | 809881.2 | RC25-26 TL-EXC-1(i)
5.1.2 | Dense/compact soil | CUM | 350 | 358.41 | 32.2569 | 32.2569 | 422.9238 | 148023.33 | RC25-26 TL-EXC-1(ii)
5.1.3 | Soft/Dis intigrated rock (not required blasting) | CUM | 350 | 686.31 | 61.7679 | 61.7679 | 809.8458 | 283446.03 | RC25-26 TL-EXC-1(iii)
5.2 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply of sand chips etc. | CUM | 300 | 6218.65 | 559.6785 | 559.6785 | 7338.007 | 2201402.1 | RC25-26 TL-FDN-1.2(iii)
5.3 | PCC in the ratio 1:2:4 as above Design, Engineering, Providing and laying of plain cement concrete (PCC 1:2:4) with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in rivetments works etc. as blind layer inclusive of labour charges for concrete mixing, shoring, shuttering & curing. This includes supply of all labourers, T&P , head loading of all type of Civil materials and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc.) as per Technical specification, approved drawings and instruction of Engineer In charge. | CUM | 400 | 8877.05 | 798.9345 | 798.9345 | 10474.919 | 4189967.6 | RC25-26 TL-FDN-1.4(i)
5.4 | RR masonary work in the ratio 1:5 including supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. | CUM | 3000 | 3721.06 | 334.8954 | 334.8954 | 4390.8508 | 13172552.4 | RC25-26 TL-D-1.1(i)
6 | PTCC approval, railway crossing has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 226644.96 | 20398.0464 | 20398.0464 | 267441.0528 | 267441.0528 | LOA NO.137,Dt.16.02.2023 (Turumunga -Dhenkikote)
7 | Forest Clearance work including preparation of Land Schedule (as per requirement ), DGPS Survey, authentication by concerned offices, preparation of complete Forest Diversion Proposal, obtaining Stage-I clearance, grant of working premission, submission of Stage-I compliances and obtaining Stahge-II clearance etc. Any other requirement of documents as per the prevailing norms of Forest department from time to time shall also be complied. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 06 months of award of contract. The contractor have to pay the DGPS authnetication & base point fees and all other payments to ORSAC. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hecter | 6.5 | 302193.28 | 27197.3952 | 27197.3952 | 356588.0704 | 2317822.4576 | LOA NO.137,Dt.16.02.2023 (Turumunga -Dhenkikote)
8 | Barbed wire fencing with spike to avoid wild animals, elephants from electrocution in Reserve Forest area including supply of barbed wire and all other materials as per approved TS and drawings ans as per recommendation of site Engineer-In -Charge as per condition of MOEF. GOI | Per Loc. | 15 | 115000 | 10350 | 10350 | 135700 | 2035500 | Tentative Market Price
9 | Supply & Installation of Dynamic Bird Flight Diverter LED type for installation in Top conductor & Earth wire under Forest stretch as per condition of MOEF. GOI | Nos. | 500 | 2475 | 222.75 | 222.75 | 2920.5 | 1460250 | Wor Order No.ED-NZ-BLS-1040,Dt.23.05.2025
10 | ROW (Right Of Way):- The agency shall pay the compensation @100% of the bench mark value of the land for construction of tower foundation and erection and 15% of bench mark value for acquisition of ROW in the land required for transmission line corridor as per the required width as per the letter no-RDM-LRGEA-POLICY-0003/43341/R&DM Dated 21.12.2022 of Additional Chief Secretary to Govt, R&DM Department, Govt. of Odisha. The agency shall also pay the crops compensation if any during the construction of transmission line in the own cost. The agency is sole responsible for obtaining ROW clearance. The agency shall pay all the cost for obtaining the ROW clearance for construction of Tower foundation, Erection and stringing of said line. | [6 empty] | 0
10.1 | Compensation for construction of Tower foudation & erection of transmission line including crops compensation & etc. (100% Bench mark cost plus other compensation) | Per Loc. | 200 | 180000 | 16200 | 16200 | 212400 | 42480000 | Average bench mark value of concerned area
10.2 | Compensation for or acquisition of ROW in the land required & trees & crops compensation to owners for transmission line corridor as per the required width (15% Bench mark cost plus other compensation if any) | Per Km | 45 | 100000 | 9000 | 9000 | 118000 | 5310000
TOTAL CIVIL WORKS | [7 empty] | 175251574.8143
TOTAL SCHEDULE-VIIB & VIIC-ERECTION AND CIVIL WORKS (220KV 220 KV TURUMUNGA-BASUDEVPUR D/C LINE ) | [7 empty] | 202890143.3049

## CABLE SUPPLY (hidden)
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Construction of 132KV S/C line from existing 132/33KV Grid Sub-Station, Barbil to proposed MRSS of AM/NS INDIA LTD at Sagasahi and 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil.
PART-C, SCHEDULE-2A (SUPPLY PART FOR LAYING OF 132 KV UG CABLE 8.276 RKM & OFC cable 9 RKM)
| DESCRIPTION OF ITEMS | UNITS | Total Quantity | BASIC PRICE PER UNIT (Taxable Value) In Rs | Escalation (UNIT PO PRICE/ COST DATA RATE + 5% ESCALATION PER YEAR) | TOTAL PRICE OF QUANTITY in Rs | Ref
SL. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification)
1 | 2 | 3 | 4 | 5 | 6 | 7=4X6 | 8
1 | Type tested EHV XLPE Power Copper conductor cable as per IEC60840 & IS7098 for the (145 KV class) as per TS
1.1 | Supply of 132 KV, 1 Core, 4 run 630 mm² Copper, XLPE insulation (Extruded semi-conducting screen and extruded or seam welded corrugated Aluminium Sheath type) UG Cable inchuding loop, rise etc.. (Composite tower 1 to Composite tower 2=1.507 KM, Composite tower 3 to Composite Tower 4=6.769 KM), (6.769*4)+(1.507*4)=33.104 Kms extra 2 KM for Spare and termination at Tower and loop in cable joint chamber | Km. | 35 | 6300000 | 6615000 | 231525000 | Rungta Kamanda | 33.104
1.2 | Supply of Outdoor terminating kit Heat shrinkable type suitable for 132 kV class, 1Core, 630 mm², copper UG Cable connection of 300sqmm bonding cable (OET) | No | 12 | 400436.4 | 420458.22 | 5045498.64 | Rungta Kamanda
| Supply of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 16 | 102900 | 108045 | 1728720 | Rungta Kamanda
1.4 | Supply of 6.6 KV,Single core, 300 sqmm XLPE bonding cable | mtr | 8500 | 1995 | 2094.75 | 17805375 | Rungta Kamanda
1.6 | Straight through joint kit for 630 sq. mm UG cable | No. | 66 | 157500 | 165375 | 10914750 | Rungta Kamanda
1.8 | Supply of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 21000 | 22050 | 22050 | Rungta Kamanda
1.9 | Supply of HDPE PLB duct of size 160 mm for laying of 630mm2 UG Cables for NH, road crossing & inside AM/NS premises . (8.276-1.5)*4=27.104 or say 27.5 Kms | Km. | 27.5 | 945000 | 992250 | 27286875 | Rungta Kamanda
2 | Supply of 24 OFC cable,3 | Km. | 9 | 157500 | 165375 | 1488375 | Rungta Kamanda
2.1 | Supply of end Connectors and acessories for OFC connection at GRID subststions | No. | 4 | 15750 | 16537.5 | 66150 | Rungta Kamanda
2.2 | Supply of HDPE PLB duct of size 40 mm for laying of 24 OFC cable .(Composite tower 1 to Composite tower 2=3.550 KM, Composite tower 3 to Kamanda MRSS=6.200 KM), 6.15+3.55=9.70 kms. | Km. | 7 | 64050 | 67252.5 | 470767.5 | Rungta Kamanda
3 | Supply of 120 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No | 12 | 25000 | 38783.2054 | 465398.4648 | Cost data -ss-24
| TOTAL OF SUPPLY PART-E, SCHEDULE 2-A(FOR LINE) ,SUPPLY COMPONENT OF THE WORKS FOR 132KV UG CABLE |  |  |  |  | 296818959.6048
| GST @ 18% on TOTAL OF PART-E |  |  |  |  | 53427412.7289
| TOTAL SUPPLY PART-E, SCHEDULE-2A(LAYING OF 132 KV UG CABLE) including GST |  |  |  |  | 350246372.3337
| Manager (Fin.) |  |  | Deputy General Manager (El)
| E.H.T (Const.) Division, |  |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  |  | OPTCL, Keonjhar

## CABLE SERVICE (hidden)
0
NAME OF THE WORK:- Construction of 132KV S/C line from existing 132/33KV Grid Sub-Station, Barbil to proposed MRSS of AM/NS INDIA LTD at Sagasahi and 1 No. 132KV Feeder Bay Extension at 132/33KV Grid Sub-station, Barbil.
PART-C, SCHEDULE-2A (ERECTION PART FOR LAYING OF 132 KV UG CABLE 8.276 RKM & OFC cable 9 RKM)
| DESCRIPTION OF ITEMS | unit | Total Qty | Price per unit in Rs | Total price | Remarks
SL. No. | ERECTION,TESTING & COMMISSIONING INCLUDING CIVIL WORKS OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | [5 empty] | RC Ref
1 | 2 | 3 | 4 | 5 | 6=4X5 | 7
ELECTRICAL WORKS
1 | Erection, Comissioning & Testing of 132 kV, 1 Core,6-Runs, 630 mm² Copper, XLPE insulation UG Cable
1.1 | Laying , Comissioning & Testing of 132 kV, 1 Core,1X4-Runs, 630 mm² Copper, XLPE insulation UG Cable by RCC trench method in trefoil formation inside precast RCC trench. | Km. | 35 | 531300 | 18595500 | Rungta Kamanda price with 5% escalation
1.1 | Erection, Comissioning & Testing of Outdoor terminating kit Heat shrinkablre type uitable for 132 kV class, 1Core, 630 mm², copper UG Cable connection of 300sqmm bonding cable (OET) | Nos. | 12 | 51975 | 623700 | Rungta Kamanda
1.3 | Erection, Comissioning & Testing of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 16 | 3465 | 55440 | Rungta Kamanda
1.4 | Erection, Comissioning & Testing of Single core, 300 sqmm XLPE bonding cable | Mtr | 8500 | 75.075 | 638137.5 | Rungta Kamanda
1.5 | UG Cable straight jointing through jointing kits Pre Mould type suitable for 132 kV, 1 Core, 630 mm², copper UG Cable | No. | 66 | 210000 | 13860000 | Rungta Kamanda
1.6 | Erection of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 21000 | 21000 | Rungta Kamanda
2.2 | Erection of end Connectors and acessories for OFC connection at GRID subststions | No. | 4 | 5250 | 21000 | Rungta Kamanda
3 | Erection, Comissioning & Testing of 120 KV. METAL OXIDE SURGE ARRESTOR.10 K.A. class III (AIS) | No | 12 | 3525.24 | 42302.88 | RC 3121 Dt.03.12.2020 | 10.2.g.i
6 | Erection and supply of Earthing materials 3050 mm ,50mm ID Heavy gauge type pipe with GI clamp fixtures welded all around the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories)with 75mmX10mm GI flat as per approved drawing & specifications. | Nos. | 20 | 6003.56 | 120071.2 | RC 3121 Dt.03.12.2020 | 21.3.i
7 | laying of Earth Flat (75mmX 10mm) for laying of earth mat at cable termination end(composite tower)as per approved drawing & specifications. | Mtr | 800 | 612.61 | 490088 | RC 3121 Dt.03.12.2020 | 21.1.vi.a
| TOTAL ELECTRICAL WORKS |  |  |  | 34467239.58
CIVIL WORKS
2 | Cable joint chamber: for laying of 132 kV cables Width : 2000mm, Depth : 1500mm, Length: 14000mm, 18 location | CUM
2.1 | Earth work excavation of Hard Soil Trench Dimension : (2.2mtr w x 1.5mtr x14 mtr.X18) | Cum | 831.6 | 293.78 | 244307.448 | RC 3121 Dt.03.12.2020 | 2.2.ii
2.2 | Dispose of excavated soil(after back filling)at site. | per Cum/Mtr | 20790 | 1.31 | 27234.9 |  | 2.3
2.3 | Supply & Filling with fine river sand after/before laying of Cable inside the trench | Cum | 207.9 | 796.4 | 165571.56 |  | 5.2
2.4 | PCC for construction of kiln brick cable joint chamber for Width : 2200mm, Depth : 100mm, Length: 14000mm (M-10 grade/1:3:6 ration PCC) | Cum | 41.58 | 5237.8 | 217787.724 |  | 3.2.i
2.5 | Construction of prefabricated RCC partition slab for kiln brick cable joint chamber. Width :2000mm, Depth : 1500mm, Length: 14000mm (M-20 grade/1:1.5:3 ration RCC) | Cum | 50.4 | 7565.71 | 381311.784 |  | 3.4.i
2.6 | Supply and erection of kiln brick masonary with supply of cement for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Cum | 163.8 | 4093.64 | 670538.232 |  | 6.2.i
2.7 | Supply and erection of plastering the brick wall for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Sqm | 1310.4 | 116.39 | 152517.456 |  | 6.5.i
2.8 | Supply and erection of punning the brick wall for cable joint chamber with man hole including all T&P. Width : 2000mm, Depth : 1500mm, Length: 14000Mtr, 18 location | Sqm | 1310.4 | 98.02 | 128445.408 |  | 6.6.i
2.9 | Supply of rod(TATA/RINL/SAIL), bending ,cutting and binding for prefabricated RCC slabs for cable joint chamber. | MT | 5 | 68623.36 | 343116.8 |  | 3.5.1
3 | Laying of HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS.
3.1 | Laying of 160mm Dia. HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS. | Kms. | 27.5 | 2850000 | 78375000
3.2 | Laying of 40mm Dia. HDPE pipe using HDD method for NH crossing, nala crossing, village road crossing & inside MRSS. | Kms. | 7.5 | 50000 | 375000
4 | UG cable Trench: RCC Trench fo laying of 132 kV Cables Width: 950 mm, Depth; 1400 mm, Length : 1500 mtr
4.1 | Earth work excavation of Hard Soil Trench Dimension : (1.15 mtr w x 1.4mtr x1500 mtr) | Cum | 2415 | 293.78 | 709478.7
4.2 | Dispose of excavated soil(after back filling)at site. | per Cum/Mtr | 60375 | 1.31 | 79091.25
4.3 | Supply & Filling with fine river sand after/before laying of Cable inside the trench | Cum | 313.5 | 796.4 | 249671.4
4.4 | PCC for Construction of RCC Cable trench (M-10 grade/1:3:6 ratio PCC) | CUM | 142.5 | 5237.8 | 746386.5
4.5 | Construction of RCC cable trench & prefabricated RCC partition slab for Width: 950 mm, Depth: 1400 mm, Length : 1500 Mtr (M-20 grade/1:1.5:3 ratio TCC) | CUM | 615 | 7565.71 | 4652911.65
4.6 | Supply of rod(TATA/RINL/SAIL), bending ,cutting and binding for prefabricated RCC slabs for cable joint chamber. | MT | 40 | 68623.36 | 2744934.4
| Supply and Erection of Route Marker along the Cable routes at an interval of 30 Mtrs as per the drawing with civil works | No | 51 | 1000 | 51000
| TOTAL OF CIVIL WORKS |  |  |  | 90314305.212
| PART-E, SCHEDULE-2C (ERECTION PART FOR LAYING OF 132 KV UG CABLE)=TOTAL ELECTRICAL WORKS+TOTAL CIVIL WORKS |  |  |  | 124781544.792
| GST @ 18% on PART-E SCHEDULE-2C (FOR LAYING OF 132 KV UG CABLE) |  |  |  | 22460678.0626
| PART-E, SCHEDULE-2C (ERECTION & CIVILWORKS PART FOR LAYING OF 132 KV UG CABLE) including GST |  |  |  | 147242222.8546
| Manager (Fin.) |  | Deputy General Manager (El)
| E.H.T (Const.) Division, |  | E.H.T (Const.) Division,
| OPTCL, Keonjhar. |  | OPTCL, Keonjhar

## line summery
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
SUMMARY (PART-B)
Name of of Works: Construction of 220 KV TURUMUNGA-BASUDEVPUR D/C Line along with 2Nos. 220KV Bays extension at Turumunga GSS
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (SCHEDULE-VIIA (FOR 220 KV TURUMUNGA-BASUDEVPUR D/C LINE)) | 357191726.4286
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 10715751.7929
3 | Sub-Total (sl no. 1+2) | 367907478.2215
4 | Contigency 3% on Sl.No.3 | 11037224.3466
5 | T&P cost @ 2% on Sl.No. 3 | 7358149.5644
6 | Transportation @5% on Sl.No.3 | 18395373.9111
7 | Total erection Chages (SCHEDULE-VIIB & VIIC (FOR220 KV TURUMUNGA-BASUDEVPUR D/C LINE) | 202890143.3049
8 | Arrangement for obtaining of the Project License for the project from ELBO office,by arranging EHT Licence holder,HT License,Lineman A & other etc,OPTCL drawing preparation, submission,estimate preparation & approval from the competent Authority of CEI &OPTCL,Arrangement of CEI Inspection,obtaining clearance from PTCC Auhtority etc. | 500000
9 | Tree cutting @20000/- per Kms | 700000
10 | Grand Total (3+4+5+6+7+8) | 608788369.3485
Deputy General Manager (Elect.),
E.H.T (Const.) Division,
OPTCL, Keonjhar

## abstract
0
ODISHA POWER TRANSMISSION CORPORATION LIMITED
ABSTRACT
Name of of Works: Construction of 220 KV TURUMUNGA-BASUDEVPUR D/C Line along with 2Nos. 220KV Bays extension at Turumunga GSS
Sl. No. | DESCRIPTION |  | AMOUNT IN INR
1 | PART- A : Construction of 2Nos 220KV Bays Extension at TurumungaG rid S/s |  | 142806152
2 | PART-B : Construction of 220 KV TURUMUNGA-BASUDEVPUR D/C Line . |  | 608788369.3485
| Total Cost of Project (Sl. No. 1+2) |  | 751594521.3485
Or say |  |  | 751594521
Estimator |  | Deputy General Manager (Elect.),
E.H.T (Const.) Division, |  | E.H.T (Const.) Division,
OPTCL, Keonjhar. |  | OPTCL, Keonjhar.

## Line Calculation sheet
0 |  | CALCULATION SHEET
SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
1 | PA+0 | 0 | 63.36 | 0 | 0.968 | 0 | 8.76 | 0 | 0.201 | 0
2 | PA+3 | 0 | 70 | 0 | 0.968 | 0 | 9.72 | 0 | 0.201 | 0
3 | PA+6 | 0 | 70 | 0 | 0.968 | 0 | 9.72 | 0 | 0.201 | 0
4 | PB+0 | 0 | 104.43 | 0 | 1.5125 | 0 | 15.49 | 0 | 0.272 | 0
5 | PB+3 | 0 | 113.49 | 0 | 1.5125 | 0 | 17 | 0 | 0.272 | 0
6 | PB+6 | 0 | 113.49 | 0 | 1.5125 | 0 | 17 | 0 | 0.272 | 0
7 | PC+0 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
8 | PC+3 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
9 | PC+6 | 0 | 141.54 | 0 | 1.74 | 0 | 20.64 | 0 | 0.309 | 0
10 | OB+3 | 0 | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
11 | OB+6 | 0 | 129.02 | 0 | 3.364 | 0 | 19.59 | 0 | 0.365 | 0
1 | OA+0(WET) | 110 | 64.512 | 7096.32 | 0.968 | 106.48 | 8.796 | 967.56 | 0.194 | 21.34
2 | OA+3(WET) | 35 | 71.25 | 2493.75 | 0.968 | 33.88 | 9.764 | 341.74 | 0.194 | 6.79
3 | OA+6 (WET) | 20 | 71.25 | 1425 | 0.968 | 19.36 | 9.764 | 195.28 | 0.194 | 3.88
4 | OB+0(WET) | 10 | 119.16 | 1191.6 | 1.682 | 16.82 | 17.9 | 179 | 0.292 | 2.92
5 | OB+3(WET) | 6 | 129.02 | 774.12 | 1.682 | 10.092 | 19.59 | 117.54 | 0.292 | 1.752
6 | OB+6 (WET) | 4 | 129.02 | 516.08 | 1.682 | 6.728 | 19.59 | 78.36 | 0.292 | 1.168
7 | OC+0(WET) | 10 | 212.94 | 2129.4 | 2.738 | 27.38 | 35.397 | 353.97 | 0.432 | 4.32
8 | OC+3(WET) | 6 | 212.94 | 1277.64 | 2.738 | 16.428 | 35.397 | 212.382 | 0.432 | 2.592
9 | OC+6 (WET) | 4 | 212.94 | 851.76 | 2.738 | 10.952 | 35.397 | 141.588 | 0.432 | 1.728
10 | OC+15(WET/P.S) |  | 360 | 0 | 10 | 0 | 59 | 0 | 5.6 | 0
11 | OC+24(WET/P.S) |  | 390 | 0 | 11 | 0 | 65 | 0 | 5.9 | 0
12 | UR+0 (P.S) |  | 276.48 | 0 | 8.836 | 0 | 73.632 | 0 | 0.721 | 0
13 | UR+6 (P.S) | 20 | 276.48 | 5529.6 | 8.836 | 176.72 | 73.632 | 1472.64 | 0.721 | 14.42
14 | DD+0 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
15 | DD+3 | 0 | 461.28 | 0 | 6.96 | 0 | 45.67 | 0 | 4.398 | 0
16 | MB+0 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
17 | MB+6 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
18 | MB+9 | 0 | 746 | 0 | 19.6 | 0 | 111.34 | 0 | 7.763 | 0
19 | MC+0 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
20 | MC+6 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
21 | MC+9 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
22 | MC+15 | 0 | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
23 | QD+9 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
24 | QD+15 | 0 | 1953 | 0 | 52.99 | 0 | 397.36 | 0 | 32.08 | 0
25 | MA+0(WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
26 | MA+3(WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
27 | MA+6 (WET) |  | 424 | 0 | 10.82 | 0 | 54.47 | 0 | 3.942 | 0
28 | MB+0(WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
29 | MB+3(WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
30 | MB+6 (WET) |  | 746 | 0 | 19.6 | 0 | 113.34 | 0 | 7.763 | 0
31 | MC+0(WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
32 | MC+3(WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
33 | MC+6 (WET) |  | 907 | 0 | 24.03 | 0 | 137.74 | 0 | 9.194 | 0
34 |  | 225 |  | 23285.27 |  | 424.84 |  | 4060.06 |  | 60.91
[7 empty] | M20 | 4060.06
[7 empty] | M25 | 0
|  |  |  | 26778.0605 |  | 488.566 |  | 4669.069 |  | 70.0465
0
Sl. No | Tower No. | Tower Type | HARDWARE FITTINGS
|  |  | SINGLE TENSION | DOUBLE TENSION | SINGLE SUSPENSION | VIBRATION DAMPER | 120 KN DISC INSULATOR (For Suspension/ pilot) | 160 KN DISC INSULATOR (For Tension)
1 | GANTRY | GANTRY |  | 3 |  | 3 |  | 90
2 | 1 | OC+3 | 3 | 3 |  | 6 |  | 135
3 | 2 | OC+3 | 6 |  | 3 | 6 | 42 | 90
4 | 3 | OC+3 | 6 |  | 3 | 6 | 42 | 90
5 | 4 | UR+6 | 6 |  |  | 6 |  | 90
6 | 5 | OC+15 | 6 |  |  | 6 |  | 90
7 | 6 | OC+24 | 6 |  | 3 | 6 | 42 | 90
8 | 7 | OC+3 | 6 |  |  | 6 |  | 90
9 | 8 | OC+24 | 6 |  |  | 6 |  | 90
10 | 9 | UR+6 | 6 |  |  | 6 |  | 90
11 | 10 | OC+3 | 6 |  |  | 6 |  | 90
12 | 11 | OC+6 | 6 |  |  | 6 |  | 90
13 | 12 | OC+15 | 6 |  |  | 6 |  | 90
14 | 13 | OC+0 | 6 |  |  | 6 |  | 90
15 | 14 | OC+24 | 6 |  |  | 6 |  | 90
16 | 15 | OC+15 | 6 |  |  | 6 |  | 90
17 | 16 | OC+24 | 3 | 3 |  | 6 |  | 135
18 | 17 | MDD+25 |  | 6 | 3 | 6 | 42 | 180
19 | 18 | MDD+25 |  | 6 | 3 | 6 | 42 | 180
20 | 19 | OC+24 |  | 6 | 3 | 6 | 42 | 180
21 | 20 | OC+15 | 3 | 3 |  | 6 |  | 135
22 | 21 | UR+6 | 6 |  |  | 6 |  | 90
23 | 22 | UR+6 | 6 |  |  | 6 |  | 90
24 | 23 | UR+6 | 6 |  |  | 6 |  | 90
25 | 24 | OC+6 | 6 |  |  | 6 |  | 90
26 | 25 | OC+6 | 6 |  |  | 6 |  | 90
27 | 26 | OC+3 | 6 |  |  | 6 |  | 90
28 | 27 | OC+0 | 6 |  |  | 6 |  | 90
29 | 28 | OC+0 | 6 |  | 3 | 6 | 42 | 90
30 | 29 | OC+0 | 6 |  |  | 6 |  | 90
109 | AP108 | GANTRY | 3 |  |  | 3 |  | 45
|  |  | 150 | 30 | 21 | 180 | 294 | 3150 |  |  | 405 | 240 | 66 | 642 | 66 | 885

## N&B (hidden)
SL | TYPE OF TOWER | QNTY | 30MM | TOTAL | 35MM | TOTAL | 40MM | TOTAL | 45MM | TOTAL | 50MM | TOTAL | 55MM | TOTAL | 60MM | TOTAL | 65MM | TOTAL | 70MM | TOTAL | 75MM | TOTAL | 80MM | TOTAL | 150MM | TOTAL | 175MM | TOTAL | N&B PER TOWER | TOTAL OF BOLT & NUT
FOR 220KV LINE |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
1 | OC' TYPE STUB | 13 |  | 0 |  | 0 |  | 0 | 3.24 | 42.12 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 3.58 | 46.54
2 | OC' TYPE TEMPLATE | 1 |  | 0 | 15.708 | 15.708 |  | 0 |  | 0 | 3.432 | 3.432 | 1.208 | 1.208 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 25.14 | 25.14
3 | OC+0 TYPE TOWER | 22 | 7.303 | 160.666 | 73.423 | 1615.306 | 50.419 | 1109.218 | 53.73 | 1182.06 | 34.034 | 748.748 | 7.399 | 162.778 | 30.652 | 674.344 | 17.49 | 384.78 |  | 0 |  | 0 |  | 0 | 49.5 | 1089 |  | 0 | 346.25 | 7617.5
4 | OC+3 TYPE TOWER | 6 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 42.35 | 254.1
5 | OC+6 TYPE TOWER | 3 | 3.597 | 10.791 | 25.109 | 75.327 |  | 0 | 8.37 | 25.11 | 4.433 | 13.299 |  | 0 |  | 0 | 17.49 | 52.47 |  | 0 |  | 0 |  | 0 | 6.75 | 20.25 |  | 0 | 71.04 | 213.12
6 | OC+9 TYPE TOWER | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
7 | OC+15,24 TEMPLATE | 1 |  | 0 | 19.04 | 19.04 | 11.684 | 11.684 | 1.08 | 1.08 | 1.144 | 1.144 | 4.832 | 4.832 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 41.97 | 41.97
8 | OC+15 TYPE STUB | 4 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 18.304 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 20.12
9 | OC+15 TYPE TOWER | 4 |  | 0 | 32.13 | 128.52 | 13.208 | 52.832 | 27 | 108 | 8.58 | 34.32 | 5.436 | 21.744 |  | 0 |  | 0 | 41.28 | 165.12 | 22.912 | 91.648 |  | 0 | 19.5 | 78 |  | 0 | 188.29 | 753.16
10 | OC+24 TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 22.88 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 25.15
11 | OC+24 TYPE TOWER | 5 |  | 0 | 15.232 | 76.16 | 27.94 | 139.7 | 52.38 | 261.9 | 22.88 | 114.4 | 15.704 | 78.52 | 3.14 | 15.7 | 18.368 | 91.84 | 66.736 | 333.68 | 25.92 | 129.6 |  | 0 | 42 | 210 |  | 0 | 304.66 | 1523.3
8 | OC+15 TYPE STUB | 4 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 18.304 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 20.12
9 | OC+15 TYPE TOWER | 4 |  | 0 | 32.13 | 128.52 | 13.208 | 52.832 | 27 | 108 | 8.58 | 34.32 | 5.436 | 21.744 |  | 0 |  | 0 | 41.28 | 165.12 | 22.912 | 91.648 |  | 0 | 19.5 | 78 |  | 0 | 188.29 | 753.16
10 | OC+24 TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 4.576 | 22.88 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 5.03 | 25.15
11 | OC+24 TYPE TOWER | 5 |  | 0 | 15.232 | 76.16 | 27.94 | 139.7 | 52.38 | 261.9 | 22.88 | 114.4 | 15.704 | 78.52 | 3.14 | 15.7 | 18.368 | 91.84 | 66.736 | 333.68 | 25.92 | 129.6 |  | 0 | 42 | 210 |  | 0 | 304.66 | 1523.3
| TOTAL |  |  | 171.457 |  | 2134.741 |  | 1505.966 |  | 1990.17 |  | 1146.431 |  | 369.346 |  | 705.744 |  | 620.93 |  | 997.6 |  | 442.496 |  | 0 |  | 1685.25 |  | 0 |  | 12841.83
1 | UR' TYPE STUB | 5 |  | 0 |  | 0 |  | 0 |  | 0 | 2.288 | 11.44 | 2.416 | 12.08 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 9.86 | 49.3
2 | UR' TYPE TEMPLATE | 1 | 1.744 | 1.744 | 22.372 | 22.372 | 2.794 | 2.794 | 1.08 | 1.08 | 4.004 | 4.004 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 35.57 | 35.57
3 | UR+0 TYPE TOWER | 5 | 6.976 | 34.88 | 59.5 | 297.5 | 47.244 | 236.22 | 38.745 | 193.725 | 43.186 | 215.93 | 25.67 | 128.35 | 36.024 | 180.12 | 59.4 | 297 |  | 0 |  | 0 |  | 0 |  | 0 | 35.109 | 175.545 | 401.21 | 2006.05
4 | UR+3 TYPE TOWER | 0 | 0.952 | 0 | 11.176 | 0 | 8.636 | 0 | 3.24 | 0 | 4.576 | 0 | 2.416 | 0 | 1.264 | 0 | 18.48 | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 1.125 | 0 | 26.57 | 0
5 | UR+6 TYPE TOWER | 5 |  | 0 | 7.616 | 38.08 | 5.08 | 25.4 | 23.22 | 116.1 | 4.576 | 22.88 | 6.04 | 30.2 | 1.264 | 6.32 | 36.96 | 184.8 |  | 0 |  | 0 |  | 0 |  | 0 | 3 | 15 | 97.28 | 486.4
| TOTAL |  |  | 36.624 |  | 357.952 |  | 264.414 |  | 310.905 |  | 254.254 |  | 170.63 |  | 186.44 |  | 481.8 |  | 0 |  | 0 |  | 0 |  | 0 |  | 190.545 |  | 2577.32
1 | MONO POLE TOWER(400KV) | 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
2 | +25 MTR TO PD TYPE | 2 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 6500 | 13000
| TOTAL |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 13000
| GRAND TOTAL |  |  | 208.081 |  | 2492.693 |  | 1770.38 |  | 2301.075 |  | 1400.685 |  | 539.976 |  | 892.184 |  | 1102.73 |  | 997.6 |  | 442.496 |  | 0 |  | 1685.25 |  | 190.545 |  | 28419.15
[29 empty] | IN MT | 28.4192

## VIIA 220KV BAY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at 220/132/33KV GSS Turumunga
SUPPLY OF EQUIPMENT / MATERIALS,
PART -A, SCHEDULE-VIIA-SUPPLY (FOR 220 KV SUB-STATION WORK)
Sl. No. | DESCRIPTION OF ITEMS SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT | TOTAL QUANTITY (02No. Bays) | [5 empty] | Price Reference
|  |  |  | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price
1 | 2 | 3 | 5 | 6 | 7 | 8 | 9 | 10= 4*9 | 12
1 | 245 KV, 50kA, 1200-600-300A/1A (5 core), SINGLE PHASE CURRENT TRANSFORMER AS PER TS | NOS | 6 | 382298.97 | 34406.9073 | 34406.9073 | 451112.7846 | 2706676.7076 | CD 24-25-SS-21
2 | 245 KV,2000A,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS | 2 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 1408165.1776 | CD 24-25-SS-5
2.2 | WITH SINGLE EARTH SWITCH | NOS | 2 | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 1831043.6656 | CD 24-25-SS-6
2.3 | TANDEM MOUNTED WITHOUT EARTH SWITCH | NOS | 4 | 633063.08 | 56975.6772 | 56975.6772 | 747014.4344 | 2988057.7376 | CD 24-25-SS-7 | Yes
3 | 245 KV, 3CORE, SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER AS PER TS | NOS | 6 | 379430 | 34148.7 | 34148.7 | 447727.4 | 2686364.4 | CD 24-25-SS-54
4 | 245KV, SF6 CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 1365681.73 | 122911.3557 | 122911.3557 | 1611504.4414 | 3223008.8828 | CD 24-25-SS-2
5 | 216 KV SURGE ARRESTOR AS PER TS | NOS | 6 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 506142.474 | CD 24-25-SS-30
6 | 220 KV Bus Post Insulators | NOS | 20 | 22424.5697 | 2018.2113 | 2018.2113 | 26460.9923 | 529219.845 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
7 | BUS BAR & CIRCUIT MATERIALS
7.1 | TENSION & SUSPENSION ANTI FOG TYPE INSULATOR STRING
7.2 | 160 kN ANTIFOG PORCELAIN DISC INSULATOR | NOS | 1700 | 726.98 | 65.4282 | 65.4282 | 857.8364 | 1458321.88 | CD 24-25-TL-ACC-58
7.3 | 120 kN ANTIFOG PORCELAIN DISC INSULATOR | NOS | 500 | 599.75 | 53.9775 | 53.9775 | 707.705 | 353852.5 | CD 24-25-TL-ACC-57
7.4 | ACSR MOOSE CONDUCTOR ( 61/3.66 SQMM) | KM | 3 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 1582124.0226 | CD 24-25-TL-ACC-19
7.5 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | MTRS | 300 | 2020.9386 | 181.8845 | 181.8845 | 2384.7075 | 715412.25 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS
8.1 | Double Tension H/W fitting for twin ACSR Moose (2 x 160kN) | NOS | 48 | 5056.93 | 455.1237 | 455.1237 | 5967.1774 | 286424.5152 | CD 24-25-TL-ACC-10
8.2 | Single Tension H/W fitting for single ACSR Moose (1 x 160kN) | NOS | 6 | 2823.38 | 254.1042 | 254.1042 | 3331.5884 | 19989.5304 | CD 24-25-TL-ACC-9
8.3 | Single Suspension Hard ware fitting for SINGLE ACSR Moose (1x 90kN) | NOS | 30 | 3465.33 | 311.8797 | 311.8797 | 4089.0894 | 122672.682 | CD 24-25-TL-ACC-7
8.4 | 'T' Clamp for single moose run with single moose ACSR drop | NOS | 22 | 849.579 | 76.4621 | 76.4621 | 1002.5033 | 22055.0715 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8.5 | 'T' Clamp for twin moose run with single moose ACSR drop | NOS | 12 | 1459.7847 | 131.3806 | 131.3806 | 1722.546 | 20670.552
8.6 | 'T' Clamp for single Zebra run with single moose ACSR drop | NOS | 12 | 849.579 | 76.4621 | 76.4621 | 1002.5033 | 12030.039
8.7 | 220 KV PI Clamp | NOS | 26 | 738.7217 | 66.485 | 66.485 | 871.6916 | 22663.9823
8.8 | 220 KV LA Clamp | NOS | 6 | 649.4472 | 58.4503 | 58.4503 | 766.3478 | 4598.0865
8.9 | 220 KV IVT Clamp | NOS | 6 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 5924.7248
8.1 | 220 KV CT Clamp | NOS | 12 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 11849.4495
8.11 | 220 KV CB Clamp | NOS | 12 | 836.8255 | 75.3143 | 75.3143 | 987.4541 | 11849.4495
8.12 | 220 KV Isolator pad clamp | NOS | 60 | 649.4472 | 58.4503 | 58.4503 | 766.3478 | 45980.865
8.13 | PG Clamp for ACSR Moose | NOS | 30 | 600.3953 | 54.0356 | 54.0356 | 708.4665 | 21253.995
8.14 | Spacer for Twin bus ACSR Moose 220 KV bus | NOS | 36 | 1769.39 | 159.2451 | 159.2451 | 2087.8802 | 75163.6872 | CD 24-25-TL-ACC-51
9 | SUBSTATION EARTHING SYSTEMS
9.1 | 75X10 mm GI Flat | MT | 10 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1102732.302 | CD 24-25-Line-4
9.2 | 50X6 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MT | 4 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 441092.9208 | CD 24-25-Line-4
9.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 110 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 296071.204 | CD 24-25-TL-8
9.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 30 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 80746.692 | CD 24-25-TL-8
10 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1, 2-2,3-3 & 4-4 along with its accessories as per TS.
10.2 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 1300 | 1067.3695 | 96.0633 | 96.0633 | 1259.496 | 1637344.8 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
10.3 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 900 | 712.2337 | 64.101 | 64.101 | 840.4358 | 756392.175
10.4 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 600 | 498.3674 | 44.8531 | 44.8531 | 588.0735 | 352844.1
10.5 | support GI angle suitable for different sections G.I Cable Trays including i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. | MT | 10 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 1102732.302 | CD 24-25-Line-4
11 | SUB STATION SWITCYARD BMK,AC CONSOLE & OTHER MARSHALLING BOXES
11.1 | BAY MARSHALLING KIOSK | NOS | 2 | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 354854.4144 | CD 24-25-SS-76
11.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.11.2
11.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 30609.8161 | 2754.8834 | 2754.8834 | 36119.583 | 72239.1659
11.4 | CT & IVT Out Door Console Boxes | NOS | 4 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 212912.0256 | CD 24-25-SS-75
11.5 | APEX Energy Meter Panel | NOS | 2 | 82637.47 | 7437.3723 | 7437.3723 | 97512.2146 | 195024.4292 | CD 24-25-SS-104
12 | 0.2 Class ABT Complaint Apex energy Audit meter - 2 Nos (1 Nos Main & 1 Nos Check) | NOS | 4 | 87655.56 | 7889.0004 | 7889.0004 | 103433.5608 | 413734.2432 | CD 24-25-SS-105
13 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220KV CLASS
13.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
13.1.1 | P1S - COLUMN ( 4.76KG) Including the earth spikes | NOS | 8
13.1.2 | Q1 BEAM (1.598KG) | NOS | 6
13.1.3 | Q3 BEAM (2.484MT) | NOS | 2
13.2 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220kV CLASS (column & Beam) | MT | 52.636 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 5804341.7448 | CD 24-25-Line-4
13.3 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.1 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 293793.3155 | CD 24-25-Line-5
13.4 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
13.4.1 | SINGLE ISOLATORS without ES-220KV ( 1.271 MT) | SET | 2
13.4.2 | Single isolator with ES- 220 KV (1.271MT) | SET | 2
13.4.3 | Tandem isolator without ES 220 KV (1.271MT) | SET | 4
13.4.4 | CTs-220 KV (0.225 MT)) | SET | 6
13.4.5 | IVTs-220 KV (0.287MT) | SET | 6
13.4.6 | Surge Arrester-220 kV (0.292MT) | SET | 6
13.4.7 | BPI-220 KV (0.292MT) | SET | 20
13.4.8 | TOTAL WEIGHT OF EQUIPMENT STRUCTURES | MT | 22.584 | 93451.89 | 8410.6701 | 8410.6701 | 110273.2302 | 2490410.6308 | CD 24-25-Line-4
13.4.9 | Total weight of GI Nuts and bolts for the above structures | MT | 2.2584 | 118560.66 | 10670.4594 | 10670.4594 | 139901.5788 | 315953.7256 | CD 24-25-Line-5
14 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
14.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
14.1.1 | PVC 3.5 CX70 mm2 | KM | 3 | 265690.44 | 23912.1396 | 23912.1396 | 313514.7192 | 940544.1576 | CD 24-25-SS-129
14.1.2 | PVC-3.5 CX35 mm2 | KM | 5 | 147505.32 | 13275.4788 | 13275.4788 | 174056.2776 | 870281.388 | CD 24-25-SS-127
14.1.3 | PVC-4 CX 16 mm2 | KM | 3 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 409880.4222 | CD 24-25-SS-125
14.1.4 | PVC-4 CX 6 mm2 | MTRS | 2000 | 131.1821 | 11.8064 | 11.8064 | 154.7948 | 309589.6734 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.16.1.5
14.1.5 | PVC-2CX 6 mm2 | MTRS | 3000 | 104.9503 | 9.4455 | 9.4455 | 123.8413 | 371524.0001 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.16.1.6
14.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
14.2.1 | 2 CX 2.5 mm2 | KM | 3 | 78413.59 | 7057.2231 | 7057.2231 | 92528.0362 | 277584.1086 | CD 24-25-SS-107
14.2.2 | 4 CX 2.5 mm2 | KM | 14 | 123673.44 | 11130.6096 | 11130.6096 | 145934.6592 | 2043085.2288 | CD 24-25-SS-109
14.2.3 | 7CX 2.5 mm2 | KM | 7 | 187201.82 | 16848.1638 | 16848.1638 | 220898.1476 | 1546287.0332 | CD 24-25-SS-110
14.2.4 | 10 CX 2.5 mm2 | KM | 12 | 254413.65 | 22897.2285 | 22897.2285 | 300208.107 | 3602497.284 | CD 24-25-SS-111
14.2.5 | 12 CX 2.5 mm2 | KM | 6 | 393557.7713 | 35420.1994 | 35420.1994 | 464398.1701 | 2786389.0205 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Sl.17.5
14.2.6 | 16 CX 2.5 mm2 | KM | 4 | 387033.75 | 34833.0375 | 34833.0375 | 456699.825 | 1826799.3 | CD 24-25-SS-112
14.2.7 | 19 CX 2.5 mm2 | KM | 2 | 448832.3 | 40394.907 | 40394.907 | 529622.114 | 1059244.228 | CD 24-25-SS-113
14.2.8 | 3.5CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | KM | 1 | 459114.77 | 41320.3293 | 41320.3293 | 541755.4286 | 541755.4286 | CD 24-25-SS-131
15 | ACCESSORIES FOR PLCC SYSTEM With OPGW cable
15.1 | 24 Fibre Optic Approach cable (DWSM) | KM | 1 | 159579.27 | 14362.1343 | 14362.1343 | 188303.5386 | 188303.5386 | CD 24-25-TELC-31
15.2 | Optical line Terminal Equipment(OLTE) -STM4 type SDH equipment with integrated MUX & tributary cards for speech & data ports for interfacing of Speech & data which should be compatible with existing OPTCL system. | No | 2 | 393554.8077 | 35419.9327 | 35419.9327 | 464394.6731 | 928789.3462 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Tel sl.4
15.3 | Digital Teleprotection Equipment and accessories to be suitable for interfacing with SDHMUX | No. | 1 | 562958.9237 | 50666.3031 | 50666.3031 | 664291.53 | 664291.53 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
15.3 | Supply of FODP(Fibre Optic Distribution Panel)48 F: Indoor type,rack mounted with FCPC coupling and pig tails(DWSm Fibre) | No | 2 | 54256.95 | 4883.1255 | 4883.1255 | 64023.201 | 128046.402 | CD24-25-TEL-29
15.4 | Remote Terminal Unit (RTU) with MFT/MFM module designed for Power Utility SCADA operation. RTU should report in IEC 870-5-104 protocols to both main & backup control centre. RTU should have ports for interfacing with relay control panels,MFT/MFMs and port for LDMS facility. Laptop should be part of the supply contract of RTU for monitoring, local data aquisition & configuration of RTU. | No | 1 | 1165622.5 | 104906.025 | 104906.025 | 1375434.55 | 1375434.55 | CD24-25-TEL-55
15.5 | 48 V,300 AH,maintenance free VRLA Battery set | Set | 1 | 119332.12 | 10739.8908 | 10739.8908 | 140811.9016 | 140811.9016 | CD24-25-TEL-02
15.6 | SMPS based Battery Charger of 48V/75A suitable for 48V VRLA Battery | NO. | 1 | 110881.51 | 9979.3359 | 9979.3359 | 130840.1818 | 130840.1818 | CD24-25-TEL-18
15.7 | 2.5 sq. mm 2 core control cable(power supply,Transducer/MFT PT supply) | Metre | 300 | 44.08 | 3.9672 | 3.9672 | 52.0144 | 15604.32 | CD24-25-TEL-62
15.8 | 2.5 sq. mm multi strand 4 core control cable(Transducer/MFT CT , supply) | Metre | 300 | 61.71 | 5.5539 | 5.5539 | 72.8178 | 21845.34 | CD24-25-TEL-61
15.9 | 1.5 sq. mm 10 core control cable(Digital Input) | Metre | 200 | 125.62 | 11.3058 | 11.3058 | 148.2316 | 29646.32 | CD24-25-TEL-59
15.1 | 10 sq. mm 2 core multi strand control cable(Battery) | Metre | 100 | 183 | 16.47 | 16.47 | 215.94 | 21594 | Local Market rate
15.11 | Earth Flat, Cable Tray, Telephone cable,ACDB, DCDB, Foundation rail, Junction Box. | LS | 2 | 174913.2479 | 15742.1923 | 15742.1923 | 206397.6325 | 412795.265 | TURUMUNGA-DHENKIKOTE LOA (137/16.02.23), Tel. Sl.10
16 | Substation Switchyard Lighting: Installation of fixtures & lamps (LED) of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality) with switch gear, GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | Nos. | 40 | 17085.7602 | 1537.7184 | 1537.7184 | 20161.197 | 806447.88 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
17 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj/Havells/ Osram/ Wipro premium quality).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS).
17.1 | STREET LIGHTING: Installation of HDG Tubular street lighting poles 8.5 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. Poles shall be installed on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes installation of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/ Havells/ Osram/Wipro), with switch gear, GI junction box, GI Conduit etc. & as per technical specification. | Nos. | 40 | 11105.3517 | 999.4817 | 999.4817 | 13104.315 | 524172.6 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, sl.32
17.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB, XLPE cables (305 C*120sqmm) from main ACDB CR to the out door KIOSK. XLPE cable of 4CX16sqmm from outdoor KIOSK to the street light poles & 4CX6sqmm from pole to pole & 2CX6sqmm from pole to lighting fixtures | Nos. | 2 | 74748.2387 | 6727.3415 | 6727.3415 | 88202.9216 | 176405.8433
18 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | Nos. | 16 | 64069.6386 | 5766.2675 | 5766.2675 | 75602.1735 | 1209634.776
19 | 220 KV SIDE PROTECTION & OTHER PANELS
19.1 | 220KV Feeder Protection Panel: DP MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. The panel shall be compatible with the existing panels for the substation for smooth integration with SAS. | Nos. | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | CD 24-25-SS-37
19.2 | 220KV BUS-BAR Protection Sysstem (Shall be compatible with the existing busbar protection of the substation): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. The bus bar protection system shall be integrated with the Automation system. | Nos. | 2 | 3809977.15 | 342897.9435 | 342897.9435 | 4495773.037 | 8991546.074 | CD 24-25-SS-40
20 | BEST QUALITY &APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X10)mm Size | NOS | 30 | 3860.9639 | 347.4867 | 347.4867 | 4555.9374 | 136678.1212 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, Sl.31.4
26 | CCTV Surveilance system
26.1 | Outdoor PTZ Camera (with PTZ camera housing, gooseneck stand-wall mount bracket, power supply/ adaptor, camera holder and other accessories) (Range: 100Mtrs) | Nos. | 1 | 92942.62 | 8364.8358 | 8364.8358 | 109672.2916 | 109672.2916 | CD 24-25-SS-173
| TOTAL: PART -A, SCHEDULE-VIIA-SUPPLY (FOR 220 KV SUB-STATION WORK) | [6 empty] | 76098572.1139

## VIIB & VIIC 220KV BAY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at 220/132/33KV GSS Turumunga
ERECTION OF EQUIPMENTS/ MATERIALS AND CIVIL WORKS
PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 132KV SUB-STATION WORK)
SL. NO. | DESCRIPTION OF ITEMS ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS | UNITS | TOTAL QUANTITY (For 02No. 220KV Bays) | Unit Price | OGST@9% | CGST@9% | Total Unit Price | Total Price | Price Reference
1 | 2 | 3
PART A | ELECTRICAL WORKS
1 | 245 KV,1200-600-300A/1-1-1-1,SINGLE PHASE CURRENT TRANSFORMER | NOS | 6 | 15439.18 | 1389.5262 | 1389.5262 | 18218.2324 | 109309.3944 | RC24-25-SS-E.1.1.h(i)
2 | 245 KV,2000A,ISOLATORS
2.1 | WITH OUT EARTH SWITCH | NOS | 2 | 29392.22 | 2645.2998 | 2645.2998 | 34682.8196 | 69365.6392 | RC24-25-SS-E.1.1.b(i)
2.2 | WITH SINGLE EARTH SWITCH | NOS | 2 | 32612.16 | 2935.0944 | 2935.0944 | 38482.3488 | 76964.6976 | RC24-25-SS-E.1.1.d(i)
2.3 | TANDEM MOUNTED WITHOUT EARTH SWITCH | NOS | 4 | 29392.22 | 2645.2998 | 2645.2998 | 34682.8196 | 138731.2784 | RC24-25-SS-E.1.1.g(i)
3 | 245 KV,3CORE,SINGLE PHASE INDUCTIVE VOLTAGE TRANSFORMER | NOS | 6 | 15439.18 | 1389.5262 | 1389.5262 | 18218.2324 | 109309.3944 | RC24-25-SS-E.1.1.h(i)
4 | 245KV,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 96102.67 | 8649.2403 | 8649.2403 | 113401.1506 | 226802.3012 | RC24-25-SS-E.1.1.a(i)
5 | 216 KV SURGE ARRESTOR AS PER TS | NOS | 6 | 5118.87 | 460.6983 | 460.6983 | 6040.2666 | 36241.5996 | RC24-25-SS-E.1.1.i(i)
6 | 220 KV Bus Post Insulators | NOS | 20 | 2807.13 | 252.6417 | 252.6417 | 3312.4134 | 66248.268 | RC24-25-SS-E.1.1.j(i)
7 | BUS BAR & CIRCUIT MATERIALS
7.1 | Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors,hoisting of Long Rod/Disc insulator ,Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments,testing,commissioning etc. as per the instruction of Engineer-in charge.
7.1.1 | Busbar stringing (for single moose) wirth fixing of insulator | Mtrs | 1000 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 214335.2 | RC24-25-SS-F.1.e(i)
7.1.2 | Busbar stringing (for twin moose) wirth fixing of insulator | Mtrs | 400 | 247.93 | 22.3137 | 22.3137 | 292.5574 | 117022.96 | RC24-25-SS-F.1.f(i)
7.1.3 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side including all clamps and connectors. | Mtrs | 330 | 236.4407 | 21.2797 | 21.2797 | 279 | 92070 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
7.2 | ACSR MOOSE CONDUCTOR JUMPERING
7.2.1 | Jumpering to equipments with fixing of clamps and connectors (for single moose) | Mtrs | 400 | 132.1 | 11.889 | 11.889 | 155.878 | 62351.2 | RC24-25-SS-F.2.(v)
7.2.2 | Jumpering to equipments with fixing of clamps and connectors (for twin moose) | Mtrs | 400 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 85734.08 | RC24-25-SS-F.2.(vi)
EARTH WIRES & IT'S HARDWARES & FITTING
| Earthing Spikes of 9 mtr long each and Its Fittings in all respect. (220 kv side) | No. | 10 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 69770 | Turumunga BOQ after deduction GST- letter no 339/06.06.22,sl.32.1
8 | SUBSTATION EARTHING SYSTEMS
8.1 | 40MM DIA MS ROD FOR EARTHING | Nos. | 100 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 347404.98 | RC24-25-SS-I.1.1.5(ii)
8.2 | EARTHING CONDUCTOR FOR BURRIAL : 75x10 mm GI Earth Flat for laying (Spacing maximum 5m both ways) | Mtrs | 1696 | 108.47 | 9.7623 | 9.7623 | 127.9946 | 217078.8416 | RC24-25-SS-I.1.1.vi(b)
8.3 | EARTHING CONDUCTOR : 50 X 6 mm GI Earth Flat for raiser from the burrial earthmat to equipment, structure etc. | Mtrs | 1674 | 108.47 | 9.7623 | 9.7623 | 127.9946 | 214262.9604 | RC24-25-SS-I.1.1.v(b)
8.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 90 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 312664.482 | RC24-25-SS-I.1.1.3(ii)
8.5 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 50 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 173702.49 | RC24-25-SS-I.1.1.5(ii)
9 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:2-2,3-3 & 4-4 along with its accessories as per TS. | Lot | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | Local Market Rate
10 | SUB STATION SWITCYARD BMK, AC CONSOLE & OTHER MARSHALLING BOXES
10.1 | BAY MARSHALLING KIOSK | NOS | 2 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 22991.9932 | RC24-25-SS-H.1.4
10.2 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 2 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 22991.9932 | RC24-25-SS-H.1.4
10.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 2 | 9742.37 | 876.8133 | 876.8133 | 11495.9966 | 22991.9932 | RC24-25-SS-H.1.4
10.4 | CT & CVT Out Door Console Boxes | NOS | 8 | 3005.27 | 270.4743 | 270.4743 | 3546.2186 | 28369.7488 | RC24-25-SS-H.1.6
10.5 | Installation of APEX meter for Main & Check (Two Nos. each) | LOT | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC24-25-SS-H.1.3
11 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
11.1 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR 220KV CLASS (column & Beam) | MT | 44 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 297671.3784 | RC24-25-SS-F.3.1
11.2 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.1 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 14207.0431 | RC24-25-SS-F.3.1
11.3 | SUPPORT STRUCTURES (LATTICETYPE) FOR ALL 220KV EQUIPMENTS ALONG WITH 33 KV EQUIPMENT | MT | 22.584 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 152786.6002 | RC24-25-SS-F.3.1
11.4 | Structure Nut- Bolts & foundation Nut-Bolts | MT | 2.2584 | 5733.27 | 515.9943 | 515.9943 | 6765.2586 | 15278.66 | RC24-25-SS-F.3.1
12 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES
12.1 | Power Cables-1.1KV, FRLSH XLPE & PVC, Armoured Aluminium Conductor (As Per Specification)
12.1.1 | PVC 3.5 CX70 mm2 | MTRS | 3000 | 674.05 | 60.6645 | 60.6645 | 795.379 | 2386137 | RC24-25-SS-G.1.2.viii
12.1.2 | PVC-3.5 CX35 mm2 | MTRS | 5000 | 511.34 | 46.0206 | 46.0206 | 603.3812 | 3016906 | RC24-25-SS-G.1.2.vi
12.1.3 | PVC-4 CX 16 mm2 | MTRS | 3000 | 271.16 | 24.4044 | 24.4044 | 319.9688 | 959906.4 | RC24-25-SS-G.1.2.iv
12.1.4 | PVC-4 CX 6 mm2 | MTRS | 2000 | 154.95 | 13.9455 | 13.9455 | 182.841 | 365682 | RC24-25-SS-G.1.2.ii
12.1.5 | PVC-2CX 6 mm2 | MTRS | 3000 | 154.95 | 13.9455 | 13.9455 | 182.841 | 548523 | RC24-25-SS-G.1.2.ii
12.2 | Control Cables- 1.1 KV, FRLSH PVC, Armoured Stranded Copper conductor (As Per Specification)
12.2.1 | 2 CX 2.5 mm2 | MTRS | 3000 | 54.24 | 4.8816 | 4.8816 | 64.0032 | 192009.6 | RC24-25-SS-G.1.1.i
12.2.2 | 4 CX 2.5 mm2 | MTRS | 14000 | 54.24 | 4.8816 | 4.8816 | 64.0032 | 896044.8 | RC24-25-SS-G.1.1.ii
12.2.3 | 7CX 2.5 mm2 | MTRS | 7000 | 54.24 | 4.8816 | 4.8816 | 64.0032 | 448022.4 | RC24-25-SS-G.1.1.iv
12.2.4 | 10 CX 2.5 mm2 | MTRS | 12000 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 877636.8 | RC24-25-SS-G.1.1.vi
12.2.5 | 12 CX 2.5 mm2 | MTRS | 6000 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 438818.4 | RC24-25-SS-G.1.1.vii
12.2.6 | 16 CX 2.5 mm2 | MTRS | 4000 | 61.98 | 5.5782 | 5.5782 | 73.1364 | 292545.6 | RC24-25-SS-G.1.1.viii
12.2.7 | 19 CX 2.5 mm2 | MTRS | 2000 | 77.48 | 6.9732 | 6.9732 | 91.4264 | 182852.8 | RC24-25-SS-G.1.1.ix
12.2.8 | 3.5CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTRS | 1000 | 1007.2 | 90.648 | 90.648 | 1188.496 | 1188496 | RC24-25-SS-G-2.0.X
13 | Erection for OPGW System
13.1 | Erection / commissioning of SDH/MUX along with termination with FODP | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
13.2 | Erection / commissioning of digital teleprotection coupler | SET | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986
13.3 | 24 Fibre Optic approach cable (DWSM) | Km | 1 | 45000 | 4050 | 4050 | 53100 | 53100 | CPC RC Sl.No.4 (OrderNo.171, DT.28.02.2023)
13.4 | Erection / commissioning of RTU along with fixing,cabling of MFMs | Set | 1 | 17044.85 | 1534.0365 | 1534.0365 | 20112.923 | 20112.923 | RC24-25-TEL-1.a(i)
13.5 | 48V,300AH,VRLA Battery set | Set | 1 | 5795.88 | 521.6292 | 521.6292 | 6839.1384 | 6839.1384 | RC24-25-TEL-2.0(ii)
13.6 | SMPS based Battery charger of 75A suitable for 48V VRLA Battery | No. | 1 | 1981.5 | 178.335 | 178.335 | 2338.17 | 2338.17 | RC24-25-TEL-1.1(d)
13.7 | Earth flat, Cable tray, telephone Cable,ACDB,DCDB,Foundation rail,Junction Box. | Set | 1 | 11826.27 | 1064.3643 | 1064.3643 | 13954.9986 | 13954.9986 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
13.8 | DCDB | NO. | 1 | 3547.46 | 319.2714 | 319.2714 | 4186.0028 | 4186.0028
13.9 | 2.5sqmm 2C/3C control cable laying | Mtr | 400 | 23.73 | 2.1357 | 2.1357 | 28.0014 | 11200.56
14 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).(150 watt each) | LOT | 2 | 30000 | 2700 | 2700 | 35400 | 70800 | Tentative
15.1 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos. | 40 | 4138.9831 | 372.5085 | 372.5085 | 4884 | 195360 | Turumunga BOQ after deduction GST- letter no 339/06.06.22
15.2 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | Nos. | 40 | 431.8584 | 38.8673 | 38.8673 | 509.5929 | 20383.7168
15.3 | OUTDOOR KIOSK of 3 mm thick CRCA sheet duly hot dip galvanised FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB. | Nos. | 2 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 13954
16 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS(Dual Inverter, Five star type latest model) with copper condensor having remote temperature & operation control facility with required voltage stabiliser. Receptical indoor Control Board having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (AS PER SPECIFICATION) FOR CONTROL/SAS ROOM, Communication room,office room & Conference room . | Nos. | 16 | 5912.7119 | 532.1441 | 532.1441 | 6977 | 111632
17 | 220 KV SIDE PROTECTION & OTHER PANELS
17.1 | 220KV Feeder Protection Panel: DP MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. The panel shall be compatible with the existing panels for the substation for smooth integration with SAS. | Nos. | 2 | 31373.72 | 2823.6348 | 2823.6348 | 37020.9896 | 74041.9792 | RC24-25-SS-H.1.1(iv)
17.3 | 220KV BUS-BAR Protection Sysstem (Shall be compatible with the existing busbar protection of the substation): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. The bus bar protection system shall be integrated with the Automation system. | Nos. | 2 | 31373.72 | 2823.6348 | 2823.6348 | 37020.9896 | 74041.9792 | RC24-25-SS-H.1.1(iv)
18 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | NOS | 30 | 200 | 18 | 18 | 236 | 7080 | Local Market Rate
19 | Inspection of Sub-Station by CEI & documentation | LS | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Local Market Rate
20 | SUBSTATION AUTOMATION SYSTEM: Erection of the following 220KV level consisting of panels, Bay Control Unit, DP relays, Numerical O/C & E/F relays,DC supervision relays, Trip Circuit supervision, Trip relay, Test block, Differential with REF, Overflux, High impedance REF, Numerical O/C & E/F relay, Transformer trouble relay etc. Station level consisting of Industrial computer with accessories, PC with accessories, laser printer, UPS, GPS system & numerical Bay Control unit etc, BCU. | set | 1 | 24768.73 | 2229.1857 | 2229.1857 | 29227.1014 | 29227.1014 | RC Panel 3
21 | AC & DC SYSTEM
21.1 | AC SYSTEM
21.1.1 | ACDB AS PER SPECIFICATION (AC DB-1.AC DB-2 WITH B/C) | SET | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC24-25-SS-H.1.3
21.1.2 | MAIN LIGHTING DISTRIBUTION BOARD (HAVING 250A MCCB AS INCOMER)AS PER SPECIFICATION (WITH DB-1.DB-2 & B/C) | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.3 | INDOOR LIGHTING DISTRIBUTION BOARD AS PER SPECIFICATION (WITH DB-I.DB-2& B/C) | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.4 | EMERGENCY LIGHTING DISTRIBUTION BOARD | SET | 0 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 0 | RC24-25-SS-H.1.3
21.1.5 | S/Y RECEPTACLE BOARD | SET | 2 | 2500 | 225 | 225 | 2950 | 5900 | LOA NO.118/22.02.19 GODISAHI GIS
21.2 | DC SYSTEM
21.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). Consider separate source(DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered.Facilities for integration with SAS as per the site requirement. | SET | 2 | 10000 | 900 | 900 | 11800 | 23600 | LOA NO.118/22.02.19 GODISAHI GIS
21.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 2 | 10303.79 | 927.3411 | 927.3411 | 12158.4722 | 24316.9444 | RC24-25-SS-H.1.3
| TOTAL OF ELECTRICAL WORKS (PART-A) | [6 empty] | 17718853.3767
SL. NO. | DESCRIPTION OF ITEMS ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS | UNITS | QUANTITY: For 2Nos. 220KV Bays | Unit Price (RC 14-15) / Market rate |  |  |  |  | Remarks
1 | 2 | 3
PART A | CIVIL WORKS
1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P (120*18) | SQ.MTRS. | 4320 | 5.78 | 0.5202 | 0.5202 | 6.8204 | 29464.128 | RC24-25-SS-1.1.10
2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge upto 15 m depth. | PER POINT | 8 | 37978.72 | 3418.0848 | 3418.0848 | 44814.8896 | 358519.1168 | RC24-25-SS-1.1.5(b)
3 | CUTTING of substation area
3.1 | [iii]Soft/Disintegrated rock soil, not requiring blasting (900sqm*0.3m) | CUM | 540 | 594.8 | 53.532 | 53.532 | 701.864 | 379006.56 | RC24-25-SS-B.1.iii
4 | FILLING of substation area with borrowed earth with supply of all labour,T& P. |  |  |  | 0 | 0 | 0 | 0
4.1 | (iii) beyond 100mtr lead (918sqm*0.4) | CUM | 734.4 | 1144.94 | 103.0446 | 103.0446 | 1351.0292 | 992195.8445 | RC24-25-SS-B.2.iii
5 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod, coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation, concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge.
5.1 | EXCAVATION:
5.1.1 | Soft/Loose Soil | Cum | 1000 | 183.02 | 16.4718 | 16.4718 | 215.9636 | 215963.6 | RC24-25-SS-B.1.i
5.1.2 | Hard / Dense Soil | Cum | 3000 | 289.77 | 26.0793 | 26.0793 | 341.9286 | 1025785.8 | RC24-25-SS-B.1.ii
5.1.3 | Hard Rock(Requiring Blasting/Using breaker machinery) | Cum | 900 | 1128.58 | 101.5722 | 101.5722 | 1331.7244 | 1198551.96 | RC24-25-SS-B.1.iv
5.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in for the column/equipment/marshalling box foundations column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 70 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 487976.846 | RC24-25-SS-B.1.2(i)
5.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 630 | 8533.36 | 768.0024 | 768.0024 | 10069.3648 | 6343699.824 | RC24-25-SS-B.1.4(i)
5.4 | Cutting, Bending, Binding Placing in position of steel rod for foundation including cost of binding wire with supply all size of rod (TATA/ RAIL/ Sail Make) | MT | 50 | 65511.29 | 5896.0161 | 5896.0161 | 77303.3222 | 3865166.11 | RC24-25-SS-1.1(i)
6 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash Brickwork with fly ash Brick ,plastering (1:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}.
6.1 | Section 1-1 | LOT | 2 | 1500000 | 135000 | 135000 | 1770000 | 3540000 | Local Market Rate
6.2 | Section 2- 2
6.3 | Section 3-3
6.4 | Section 4-4
7 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing ) |  |  |  | 0 | 0 | 0
7.1 | Section 1-1 | Nos | 2 | 150000 | 13500 | 13500 | 177000 | 354000 | Local Market Rate
8 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Enginer In charge. Provision of drains on both the side of the roads for easy discharge of rain water. |  |  |  | 0 | 0 | 0 | 0
8.1 | 3.75 mtrs Concrete road . | MTR | 80 | 14279.661 | 1285.1695 | 1285.1695 | 16850 | 1348000 | Turumunga BOQ after deduction GST- letter no 339/06.06.22, Sl.48
8.2 | 7Mtr RCC Road | MTR | 200 | 20488.9831 | 1844.0085 | 1844.0085 | 24177 | 4835400
9 | Out door bay kiosks : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The internal dimensions of the Bay Kiosks are as mentioned against the switchyards below. Doors shall be heat insulated and hinge type.
9.1 | For 400KV & 220KV Switchyards (4 Lots for 400KV + 4 Lot for 220KV = 8 Lots) Internal Dimensions for the Kiosk - 8m x 5.5m x 3.3m
9.1.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. ( including for Pile foundation if required with cost of boring, Column ,Beams and roofs etc. ) | Lot | 1 | 544858 | 49037.22 | 49037.22 | 642932.44 | 642932.44 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.2 | Fly Ash Brick masonry work in cement sand mortar 1: 5 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 193401 | 17406.09 | 17406.09 | 228213.18 | 228213.18 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.3 | Flooring shall be with vitrified digital double charged tiles (Kajaria/Johnson/Somany/Varmora/Cera) with dado as per technical spec & approved drawings. | Lot | 1 | 94447 | 8500.23 | 8500.23 | 111447.46 | 111447.46 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 94178 | 8476.02 | 8476.02 | 111130.04 | 111130.04 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.5 | Doors shall be of hinge operated openable and window shall be sliding type with adequate locking facility. The door window frame shall be of UPVC (Fenesta make) heavy sections with double layer toughened glaze of 6mm (min.) & windows shall have anodised aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 25464 | 2291.76 | 2291.76 | 30047.52 | 30047.52 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.6 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 90945 | 8185.05 | 8185.05 | 107315.1 | 107315.1 | LoA No.221,Dt.01.02.25 (Neulpoi)
9.1.7 | Provision of smoke and fire detection & Alarm system of the kiosks - to be integrated with the system in the main CRB. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 79083 | 7117.47 | 7117.47 | 93317.94 | 93317.94 | LoA No.221,Dt.01.02.25 (Neulpoi)
10 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 420 | 5907.71 | 531.6939 | 531.6939 | 6971.0978 | 2927861.076 | RC24-25-SS-B.1.2(i)
11 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 560 | 3233.69 | 291.0321 | 291.0321 | 3815.7542 | 2136822.352 | RC24-25-SS-3.1
12 | RCC Retaining (4 mtr height) cum boundary wall : Design, engineering, supply of all labour, material (Supply of Cement, coarse and fine aggregates and construction of PCC (1:3:6) & RCC (1:1.5:3) as per requirement including excavation, concreting, shuttering and back filling of open cast grade beam concreting etc complete for the boundary walls, as per the approved drawings. (140Mtr length) | LOT | 2 | 2500000 | 225000 | 225000 | 2950000 | 5900000 | Local Market Rate
13 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick masonry work with ratio 1:5 and cement pointing of the joints, for the fencing up to a height from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | LOT | 2 | 350000 | 31500 | 31500 | 413000 | 826000 | Local Market Rate
14 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 2 | 150000 | 13500 | 13500 | 177000 | 354000 | Local Market Rate
15 | Anti-Weed Treatment |  |  |  | 0 | 0 | 0 | 0
15.1 | Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treatment of the switch-yard areas,controlroom etc.- spraying of anti weed chemicals/ pesticides(Burachlora/Glyphoss) for destoying of wild plants, grass, shrubs bushed etc. inside swithyard as per the instruction of Engineer-in-Charge. | Sq.Mtrs | 20000 | 18 | 1.62 | 1.62 | 21.24 | 424800 | Local Market Rate
| TOTAL OF SUBSTATION (Civil Work) | [6 empty] | 38867616.8973
| PART - A, SCHEDULE-VIIB &VIIC-ERECTION & CIVILWORKS (FOR 220KV SUB-STATION WORK) | [6 empty] | 56586470.274
Note on B12: OPTCL: Turumunga is 2 main & transfer bus?

## SS SUMMERY
NAME OF THE WORK: Construction of 2 Nos 220KV Bay Extension at 220/132/33KV GSS Turumunga
S U M M A R Y PART-A (FOR 220 KV BAY EXTENSION)
Sl.No. | Description | Amount (in Rs.)
1 | Total Cost of materials (PART-I SCHEDULE-VIIA including GST | 76098572.1139
2 | Stock, Storage & Insurance(@3% on Sl.No-1 | 2282957.1634
3 | Sub-Total(1+2) | 78381529.2773
4 | Contingency 3% on Sl.No.3 | 2351445.8783
5 | T&P cost @ 2% on Sl.No. 3 | 1567630.5855
6 | Transportation @ 5% on Sl.No.3 | 3919076.4639
7 | Total Cost of Supply(Sl No.3 to Sl No.6) | 86219682.2051
8 | Total erection Chages (PART-I, SCHEDULE-VIIB & VIIC including GST | 56586470.274
9 | Total Cost of the Supply & Erection (Sl No.7+Sl No.8) | 142806152.4791
11 | Or Say | 142806152