## LINE_Summary_Sch VIII
SUMMARY
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
Sl.No. | Description | Amount (inRs.)
1 | Total Cost of materials (a+b+c below) | 703195397.5949
a | 220KV Bay extension at 220/132/33KV GSS, Balasore | 41534445.7984
b | 220KV Balasore-Baisinga DC line (Overhead) | 97860031.79
c | 220Kv UG cable laying | 563800920.0065
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 21095861.9278
3 | Sub-Total(1+2) | 724291259.5227
4 | Contigency 3% on Sl.No.3 | 21728737.7857
5 | T&P cost @ 2% on Sl.No. 3 | 14485825.1905
6 | Transportation @5% on Sl.No.3 | 36214562.9761
7 | Total Supply Cost Sub-Total (Sl. No.3 to Sl. No.6) | 796720385.475
8 | Total Electrical Erection cost (a+b+c below) | 51527655.3843
a | 220KV Bay extension at 220/132/33KV GSS, Balasore | 5593185.5935
b | 220KV Balasore-Baisinga DC line (Overhead) | 6532978.17
c | 220Kv UG cable laying | 39401491.6208
9 | Total Civil work cost (a+b+c below) | 99194867.1449
a | 220KV Bay extension at 220/132/33KV GSS, Balasore | 27219336.59
b | 220KV Balasore-Baisinga DC line (Overhead) | 65717653.4702
c | 220Kv UG cable laying | 6257877.0847
10 | Sub-Total (Sl. No.7 + Sl. No.8 + Sl.no-9) | 947442908.0042
11 | Inspection fees (220KV line & Bay extn.) | 300000
12 | TOTAL COST OF SUPPLY, ERECTION AND CIVIL | 947742908.0042
13 | GRAND TOTAL | 947742908.0042
|  | 947742908 | 3617470352
Rupees (Ninety Five crore Seventy Six Lakh Seventy One thousand Five Hundred Fifty) only

## LINE_SUPPLY_VIIA
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
SCHEDULE - VII-A - PART -I SUPPLY COMPONENT OF THE WORKS CONTRACT
| 220 KV LILO TRANSMISSION LINE EQUIPMENTS / MATERIALS | UNIT OF MEASUREMENT | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | GST |  | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | PRICE REFERENCE
Sl. No. | DESCRIPTION OF ITEMS (SCHEDULE-VIIA- 220KV & 132KV DC TRANSMISSION LINE) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) |  |  |  | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE)
1 | 2 | 3 | 4 | 5 | 6= (5X9%) | 7= (5X9%) | 8= 5+6+7 | 9= 8X4
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats, different type of G.I HT Nuts & Bolts, washer, spring washer for the towers, hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification and designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec. Note: Weight as indicated are tentative
1.1 | STUBS & CLEATS
1.1.1 | OA TYPE(NOMINAL UNIT WEIGHT 0.231 MT) [24NOS] | MT | 5.544
1.1.2 | OB TYPE (NOMINAL UNIT WEIGHT 0.437 MT) [06NO] | MT | 2.622
1.1.3 | OC TYPE (NOMINAL UNIT WEIGHT 0.770 MT) [8NOS] | MT | 6.16
1.1.4 | OC+15 TYPE (NOMINAL UNIT WEIGHT 1.067 MT) [3NOS] | MT | 3.201
1.1.5 | UR TYPE (NOMINAL UNIT WEIGHT 0.692 MT) [01NOS] | MT | 0.692
1.1.6 | PC TYPE (Nominal unit weight 0.252 MT) [02nos] | MT | 0.504
1.1.7 | MC TYPE (NOMINAL UNIT WEIGHT 2.13MT) [03nos] | MT | 6.39
1.2 | TOWER SUPER STRUCTURES
1.2.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.309 MT) | MT | 103.416
1.2.2 | +3 EXTENSION (NOMINAL UNIT WEIGHT 0.759 MT) | MT | 3.0384
1.2.3 | +6 EXTENSION (NOMINAL UNIT WEIGHT 1.513 MT) | MT | 7.565
1.2.4 | OB TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 6.4765 MT) | MT | 38.859
1.2.5 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.336 MT) | MT | 1.336
1.2.6 | +6 MTR EXTENSION to OB (Nominal unit weight 2.321 MT) | MT | 0
1.2.7 | OC TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.2577 MT) | MT | 101.8347
1.2.8 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.49 MT) | MT | 0
1.2.9 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.729 MT) | MT | 10.516
1.2.10 | OC+15 EXTENSION (NOMINAL UNIT WEIGHT 8.743 MT) | MT | 26.229
1.3 | UR TYPE TOWERS (Nominal unit wt- 11.888 MT)-02 Nos | MT | 11.888
1.3.1 | +6 mtr Extension to UR type Tower (Nominal wt- 4.148 MT) -02 Nos | MT | 4.148
1.4 | PC TYPE (60 deg ANGLE ) TOWERS (Nominal unit weight 5.924 MT) [02nos] | MT | 11.848
1.4.1 | MC TYPE (60 deg ANGLE ) MULTICIRCUIT TOWERS (Nominal unit weight 31.088 MT) [03nos] | MT | 32.6424
1.5 | WEIGHT OF THE TOWER SUPER STRUCTURES (MS members) | MT | 378.4335 | 82451 | 7420.59 | 7420.59 | 97292.18 | 36818620.2 | Structure rc 1
1.5A | WEIGHT OF THE TOWER SUPER STRUCTURES (HT members) | MT | 60.6216 | 85000 | 7650 | 7650 | 100300 | 6080346.48 | Structure rc 2
1.6 | Weight of different type G.I Nuts and Bolts for Tower Super structure | MT | 25 | 102000 | 9180 | 9180 | 120360 | 3009000 | Structure rc 4.0
1.7 | TEMPLATES
1.7.1 | OA (NOMINAL UNIT WEIGHT 0.580 MT) [2SETS] | MT | 1.16
1.7.2 | OB (NOMINAL UNIT WEIGHT 0.794 MT) [1SET] | MT | 0.794
1.7.3 | OC (NOMINAL UNIT WEIGHT 0.962 MT) [2SETS] | MT | 0.962
1.7.4 | OC+15/24(NOMINAL UNIT WEIGHT 2.073 MT) [1SET] | MT | 2.073
1.7.5 | UR (Nominal unit weight-1.476 MT)(01SET) | MT | 1.476
1.7.6 | PC (Nominal unit weight 0.876 MT) [1set] | MT | 0.876
1.7.7 | MC (Nominal unit weight 1.308 MT)(01 set) | MT | 1.308
1.7 | Weight of MS enamelled template | MT | 8.649 | 63712 | 5734.08 | 5734.08 | 75180.16 | 650233.2 | Structure rc 3.0
1.8 | Weight of different type G.I Nuts and Bolts for Templates | MT | 0.5 | 102000 | 9180 | 9180 | 120360 | 60180 | Structure rc 4.0
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. | 56 | 2280.98 | 205.29 | 205.29 | 2691.56 | 150727.36 | COST DATA 8
2.2 | DANGER BOARD | Nos. | 47 | 236.77 | 21.31 | 21.31 | 279.39 | 13131.33 | COST DATA 9
2.3 | NUMBER PLATE | Nos. | 47 | 129.38 | 11.64 | 11.64 | 152.66 | 7175.02 | COST DATA 10
2.4 | PHASE PLATE | Nos. | 300 | 100.92 | 9.08 | 9.08 | 119.08 | 35724 | COST DATA 11
2.5 | BIRD GUARD | Nos. | 144 | 375 | 33.75 | 33.75 | 442.5 | 63720
2.6 | ANTICLIMBING DEVICE | Nos. | 47 | 4400.23 | 396.02 | 396.02 | 5192.27 | 244036.69 | COST DATA 13
2.7 | CIRCUIT PLATE | Nos. | 100 | 100.92 | 9.08 | 9.08 | 119.08 | 11908 | COST DATA 12
3 | Supply of following POWER CONDUCTORS in the proposed 220kV lines including 1.5% provision for sag and wastage as per the technical specification and as per the instruction of the engineer in charge.
3.1 | ACSR Zebra | Kms. | 71 | 363162.06 | 32684.59 | 32684.59 | 428531.24 | 30425718.04 | COST DATA 18
3.2 | ACSR Panther | Kms. | 10 | 192279.06 | 17305.12 | 17305.12 | 226889.3 | 2268893 | COST DATA 17
4 | POWER CONDUCTOR ACESSORIES
4.1 | For ACSR ZEBRA
4.1.1 | VIBRATION DAMPER | Nos. | 510 | 756.44 | 68.08 | 68.08 | 892.6 | 455226 | COST DATA 29
4.1.2 | MID SPAN JOINT | Nos. | 30 | 797.33 | 71.76 | 71.76 | 940.85 | 28225.5 | COST DATA 34
4.1.3 | Repair Sleeve | Nos. | 30 | 324.04 | 29.16 | 29.16 | 382.36 | 11470.8 | COST DATA 40
4.2 | For ACSR PANTHER
4.2.1 | VIBRATION DAMPER | Nos. | 96 | 466.13 | 41.95 | 41.95 | 550.03 | 52802.88 | Cost Data 2024-25 TL-SL.No.-31
4.2.2 | Repair Sleeve | Nos. | 12 | 220.8 | 19.87 | 19.87 | 260.54 | 3126.48 | Cost Data 2024-25 TL-SL.No.-42
5 | Supply of the following Type Long Rod Porcelain insulators as per the technical specification and as per the instruction of the Engineer in charge.
5.1 | 220KV LONG ROD 160 KN Porcelain insulatorsR (taking 5% extra towards wastage) | Nos. | 318 | 14593.68 | 1313.43 | 1313.43 | 17220.54 | 5476131.72 | COST DATA 60
5.2 | 220KV LONG ROS 90 KN Porcelain insulators (taking 5% extra towards wastage) | Nos. | 288 | 11187.5 | 1006.88 | 1006.88 | 13201.26 | 3801962.88 | COST DATA 59
5.3 | 132kv 90 KN Porcelain Long Rod Insulator | Nos. | 72 | 6620.18 | 595.82 | 595.82 | 7811.82 | 562451.04 | Cost Data 2024-25 TL-SL.No.-61
5.4 | 132kv 120 KN Porcelain Long Rod Insulator | Nos. | 186 | 7826.07 | 704.35 | 704.35 | 9234.77 | 1717667.22 | Cost Data 2024-25 TL-SL.No.-62
6 | Supply of the following hard ware fittings suitable for following conductors as per the technical specification.
6.1 | For ACSR ZEBRA
6.1.1 | Single suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set | 120 | 2698.67 | 242.88 | 242.88 | 3184.43 | 382131.6 | COST DATA 15
6.1.2 | Double suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set | 30 | 4566.27 | 410.96 | 410.96 | 5388.19 | 161645.7 | COST DATA 16
6.1.3 | Single tension Hard wares fittings, suitable for 160 KN Long Rod insulator. | Set | 126 | 2076.13 | 186.85 | 186.85 | 2449.83 | 308678.58 | COST DATA 17
6.1.4 | Double tension Hard wares fittings, suitable for 160 KN Log Rod insulator. | Set | 96 | 4735.96 | 426.24 | 426.24 | 5588.44 | 536490.24 | COST DATA 18
6.1.5 | Single suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator (Pilot insulator). | Set | 108 | 2698.67 | 242.88 | 242.88 | 3184.43 | 343918.44 | COST DATA 15
6.2 | For ACSR PANTHER
6.2.1 | Single suspension Hard wares fittings.(AGS type) suitable for ACSR Panther 90 KN Long Rod insulator. | Nos. | 0 | 1985.16 | 178.66 | 178.66 | 2342.48 | 0 | Cost Data 2024-25 TL-SL.No.-25
6.2.2 | Double suspension Hard wares fittings.(AGS type) suitable for ACSR Panther 90 KN Long Rod insulator. | Nos. | 0 | 1985.16 | 178.66 | 178.66 | 2342.48 | 0 | Cost Data 2024-25 TL-SL.No.-21
6.2.3 | Single tension Hard wares fittings suitable for ACSR Panther 120 KN Long Rod insulator. | Nos. | 42 | 1759.24 | 158.33 | 158.33 | 2075.9 | 87187.8 | Cost Data 2024-25 TL-SL.No.-22
6.2.4 | Double tension Hard wares fittings suitable for ACSR Panther 120 KN Long rod insulator. | Nos. | 72 | 3929.42 | 353.65 | 353.65 | 4636.72 | 333843.84 | Cost Data 2024-25 TL-SL.No.-23
6.2.5 | Single suspension Hard wares fittings(Through type suspension insulator) suitable for ACSR Panther 90 KN insulator (Pilot insulator). | Nos. | 72 | 1985.16 | 178.66 | 178.66 | 2342.48 | 168658.56 | Cost Data 2024-25 TL-SL.No.-25
7 | “D” Shackle | Nos. | 60 | 326.55 | 29.39 | 29.39 | 385.33 | 23119.8 | RTSS Rrpur BOQ NO.71 DT.24.01.23
8 | Hanger (220KV) | Nos. | 144 | 730.8 | 65.77 | 65.77 | 862.34 | 124176.96 | RTSS Rrpur BOQ NO.71 DT.24.01.23
13 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION)
13.1 | 48 Fibre(DWSM) OPGW fibre Optic cable | KM | 12.25 | 215500 | 19395 | 19395 | 254290 | 3115052.5 | Ranki LILO LOA 411 Dt.03.02.2020
13.2 | OPGW hardwarw set like suspension assembly, Tension assembly(Dead end assembly, Pass through assembly), Vibration damper, Down Lead clamp Assemblies for 24F, 48 fibre(DWSM) OPGW, Joint box | KM | 12.25 | 22597.72 | 2033.79 | 2033.79 | 26665.3 | 326649.93 | Ranki LILO LOA 411 Dt.03.02.2021
A | TOTAL OF PRICE FOR SUPPLY COMPONENT OF THE WORKS CONTRACT EQUIPEMENTS / MATERIALS_SCHEDULE VIIA 220 KV LILO TRANSMISSION LINE) | [6 empty] | 97860031.79
Note on D45: OPTCL: considered extra 06nos for power line crossing points 2*3 FOR MC TOWER TWO EARTHING
Note on D48: OPTCL: 3*12 FOR MC TOWER +02*6 FOR 132KV
Note on D54: OPTCL: doubt
Note on D70: OPTCL: 6NOS EXTRA
Note on D78: OPTCL: 12 FOR BEAM END & 06FOR TOWER OTHER END
Note on D80: OPTCL: only MC TOWER

## LINE_ERECTION_VIIB
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
SCHEDULE - VII-B - PART -II ERECTION COMPONENT OF THE WORKS CONTRACT
| ERECTION,TESTING & COMMISSIONING WORKS _220 KV DC TRANSMISSION LINE |  |  |  | GST
Sl. No. | DESCRIPTION OF ITEMS (SCHEDULE-VIIB- 220KV & 132KV DC TRANSMISSION LINE) ERECTION OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY | PRICE REFERENCE
1 | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
PART-A | ELECTRICAL WORKS
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. All Erection should confirm to the Technical Specification laid there in the Tender Specification and the structures are to be designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec.(As per BIS 802). Note:Weight as indicated are tentative.
1.1 | TOWER SUPER STRUCTURES
1.1.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.309 MT) | Nos | 24
1.1.2 | +3 EXTENSION (NOMINAL UNIT WEIGHT 0.759 MT) | Nos | 4
1.1.3 | +6 EXTENSION (NOMINAL UNIT WEIGHT 1.513 MT) | Nos | 5
1.1.4 | OB TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 6.4765 MT) | Nos | 6
1.1.5 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.336 MT) | Nos | 1
1.2.6 | +6 MTR EXTENSION to OB (Nominal unit weight 2.321 MT) | Nos | 0
1.1.6 | OC TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.2577 MT) | Nos | 11
1.1.7 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.49 MT) | Nos | 0
1.1.8 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.729 MT) | Nos | 4
1.1.9 | OC+15 EXTENSION (NOMINAL UNIT WEIGHT 8.743 MT) | Nos | 3
1.1.10 | UR TYPE TOWERS (Nominal unit wt- 11.888 MT) | Nos | 1
1.1.11 | +6 mtr Extension to UR type Tower (Nominal wt- 4.148 MT) | Nos | 1
1.1.12 | PC TYPE (60 deg ANGLE ) TOWERS (Nominal unit weight 5.924 MT) | Nos | 2
1.1.13 | MC TYPE (60 deg ANGLE ) MULTICIRCUIT TOWERS (Nominal unit weight 31.088 MT) | Nos | 3
1.1.13 | WEIGHT OF THE STRUCTURESWITH (HT & MS) | MT | 413.9421 | 7386.14 | 664.75 | 664.75 | 8715.64 | 3607770.32 | RC2023 line 9.i
1.2 | Weight of different type G.I Nuts and Bolts | MT | 25 | 7386.14 | 664.75 | 664.75 | 8715.64 | 217891 | RC2023 line 9.i
1.3 | Fixing of the Templates,STUBS & CLEATS with N&B
1.3.1 | Fixing of the Templates with N&B
1.3.1.1 | OA (NOMINAL UNIT WEIGHT 0.580 MT) | MT | 13.92
1.3.1.2 | OB (NOMINAL UNIT WEIGHT 0.794 MT) | MT | 4.764
1.3.1.3 | OC (NOMINAL UNIT WEIGHT 0.962 MT) | MT | 7.696
1.3.1.4 | OC+15/24(NOMINAL UNIT WEIGHT 2.073 MT) | MT | 6.219
1.3.1.5 | UR (Nominal unit weight-1.476 MT) | MT | 1.476
1.3.1.6 | PC (Nominal unit weight 0.876 MT) |  | 1.752
1.3.1.7 | MC (Nominal unit weight 1.308 MT)(01 set) |  | 3.924
1.3.2 | Fixing of the STUBS & CLEATS
1.3.2.1 | OA TYPE(NOMINAL UNIT WEIGHT 0.231 MT) | MT | 5.544
1.3.2.2 | OB TYPE (NOMINAL UNIT WEIGHT 0.437 MT) | MT | 2.622
1.3.2.3 | OC TYPE (NOMINAL UNIT WEIGHT 0.770 MT) | MT | 6.16
1.3.2.4 | OC+15 TYPE (NOMINAL UNIT WEIGHT 1.067 MT) | MT | 3.201
1.3.2.5 | UR TYPE (NOMINAL UNIT WEIGHT 0.692 MT) | MT | 0.692
1.3.2.6 | PC TYPE (Nominal unit weight 0.252 MT) | MT | 0.504
1.3.2.7 | MC TYPE (NOMINAL UNIT WEIGHT 2.13MT) | MT | 6.39
1.3.3 | WEIGHT OF THE Fixing of the STUBS & CLEATS |  | 64.864 | 5738.91 | 516.5 | 516.5 | 6771.91 | 439253.17 | RC2023 line 6.i
2 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge.
2.1 | EARTHING DEVICE | Nos. | 56 | 3071.77 | 276.46 | 276.46 | 3624.69 | 202982.64 | RC2023 line 8.2.ii
2.2 | DANGER BOARD | Nos. | 47 | 159.47 | 14.35 | 14.35 | 188.17 | 8843.99 | RC2023 line 11.ii
2.3 | NUMBER PLATE | Nos. | 47 | 159.47 | 14.35 | 14.35 | 188.17 | 8843.99 | RC2023 line 11.i
2.4 | PHASE PLATE | Nos. | 300 | 159.47 | 14.35 | 14.35 | 188.17 | 56451 | RC2023 line 11.iii
2.5 | BIRD GUARD | Nos. | 144 | 159.47 | 14.35 | 14.35 | 188.17 | 27096.48 | RC2023 line 11.iv
2.6 | ANTICLIMBING DEVICE | Nos. | 47 | 3441.28 | 309.72 | 309.72 | 4060.72 | 190853.84 | RC2023 line 11.v
2.7 | CIRCUIT PLATE | Nos. | 100 | 159.47 | 14.35 | 14.35 | 188.17 | 18817 | RC2023 line 11.i
3 | Hoisting and fixing of insulators with required accessories,Hardwares, paying out of conductor ,jointing, stringing, sagging & Jumpering etc. of power conductor with G.I. Earth wire in the proposed lines with all required accessories including scaffolding for 33 KV,11 KV, LT , P&T lines, roads and using own required T&P and compression jointing machines etc. and as per the direction of Engineer in charge.
3.1 | DOUBLE CIRCUIT(ACSR ZEBRA, SIX POWER CONDCTOR) | RKM | 11.5 | 82014.8846 | 7381.34 | 7381.34 | 96777.5646 | 1112941.99 | Ranki LILO LOA 411 Dt.03.02.2020
3.2 | DOUBLE CIRCUIT(ACSR PANTHER, SIX POWER CONDCTOR) | RKM | 0.75 | 71223.4457 | 6410.11 | 6410.11 | 84043.6657 | 63032.75
4 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION)
4.1 | 48 Fibre(DWSM) OPGW fibre Optic cable along with its Hardwares and approach cables | KM | 12.25 | 40000 | 3600 | 3600 | 47200 | 578200 | Ranki LILO LOA 411 Dt.03.02.2020
B | ERECTION COMPONENT OF THE WORKS CONTRACT FOR 220 KV DC TRANSMISSION LINE | [6 empty] | 6532978.17
Note on D24: OPTCL: stub&cleat included need to be removed'
Note on D45: OPTCL: considered extra 06nos for power line crossing points 2*3 FOR MC TOWER TWO EARTHING
Note on D48: OPTCL: 3*12 FOR MC TOWER +02*6 FOR 132KV

## LINE_CIVIL WORKS_VIIC 1
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
SCHEDULE - VII-C - PART -III CIVIL WORK COMPONENT OF THE WORKS CONTRACT
|  | CIVIL WORKS _220 KV & 132KV TRANSMISSION LINE |  |  |  | GST
Sl. No. | Code | DESCRIPTION OF ITEMS (SCHEDULE-VIIC- 220 KV & 132KV TRANSMISSION LINE) CIVIL WORKS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE QUANTITY
1 |  | 2 | 3 | 4 | 5 | 6= {5*9%} | 7= {5*9%} | 8= {5+6+7} | 9= {8*4}
1 |  | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting
1.1 | 30000535 | Preliminary survey :- Making walkover survey for ascertaining threealternative routes and marking on Toposheet, preparation of routealignment map, preparation of kml/kmz file and submission for routeapproval | KM. | 12.25 | 5036 | 453.24 | 453.24 | 5942.48 | 72795.38 | RC2023 line 1.1
1.2 | 30000537 | 220kV & 132KV DC Line: Detailed survey including taking of levels, profile plotting, tower spotting ,showing P&T, Power lines, Railway line , River crossing(RC) ,Roads and submission of profile and survey report. The P&T lines and Railway lines for a minimum distance of 8 KMs. on either side of alignment shall be clearly indicated. per RKM. | KM. | 12.25 | 14268.67 | 1284.18 | 1284.18 | 16837.03 | 206253.62 | RC2023 line 1.2
1.3 | 30000545 | 220KV & 132KV DC Line: Check survey- rough check on detailed survey,marking of tower location , locate and peg mark the tower positions on ground confirming to survey chart, marking of pit centers according to excavation marking chart, preparation of tower schedule, line schedule. per RKM. | KM. | 12.25 | 6714.67 | 604.32 | 604.32 | 7923.31 | 97060.55 | RC2023 line 1.4
1.4 | 30000541 | 220KV & 132KV DC Line: Preparation of land schedule-with HAL <(>&<)> SAVIKclassification on revenue maps plot No, khata No, Mouza on revenue mapsindicating alignment therein duly authenticated by Revenue Inspector andTahasildar, enumeration of trees with the help of Forest Officers andother prominent features required for alignment of line per RKM. | KM. | 12.25 | 10911.34 | 982.02 | 982.02 | 12875.38 | 157723.41
1.5.1 | 30000548 | Soil investigation per location-Normal foundation(boring up to 3.0m, 5.0m, 7.0m depth) per Loc. | Per Loc. | 16 | 28537.34 | 2568.36 | 2568.36 | 33674.06 | 538784.96 | RC2023 line 1.5.b
1.5.2 | 30000549 | Soil investigation per location-under reamed(UR) plie foundation( boring to 15.0m depth) per Loc. | Per Loc. | 2 | 38609.34 | 3474.84 | 3474.84 | 45559.02 | 91118.04
2.1.1 | 40000237 | Soft/Loose soil:Excavation of Soft/Loose soil (including shoring where required) andback filling (back filling shall be done in layers of 500mm; sprinklingof water and compaction thereafter followed by disposal of excessquantity of excavated soil at suitable place after back filling),<(>&<)> if required for filling the foundation, borrowedearth/morrum/sand shall be brought for filling and compaction, includingsupply of sand, all T<(>&<)>P, labour as required as per instruction ofEngineer-in-charge | CUM | 1810 | 233.97 | 21.06 | 21.06 | 276.09 | 499722.9 | RC2023 line 2.i
2.1.2 | 40000238 | Excavation of Dense/Compact Soil (including shoring where required) and back filling (back filling shall be done in layers of 500mm; sprinklingof water and compaction thereafter followed by disposal of excess quantity of excavated soil at suitable place after back filling),& if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, includingsupply of sand, all T&P, labour as required as per instruction of Engineer-in-charge. | CUM | 2500 | 366.54 | 32.99 | 32.99 | 432.52 | 1081300 | RC2023 line 2.ii
2.1.3 | 40000241 | Excavation of soft/disintegrated rock not requiring blasting and back filling (back filling shall be done in layers of 500mm; sprinkling of water and compaction thereafter followed bydisposal of excess quantity of excavated soil at suitable place afterback filling), & if required for filling the foundation, borrowedearth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer-in-charge. | CUM | 1810 | 701.88 | 63.17 | 63.17 | 828.22 | 1499078.2 | RC2023 line 2.iii
2.1.4 | 40000242 | Excavation of hard rock requiring blasting and back filling (back filling shall be done in layers of 500mm; sprinkling of water and compaction thereafter followed bydisposal of excess quantity of excavated soil at suitable place afterback filling), & if required for filling the foundation, borrowedearth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer-in-charge. | CUM | 905 | 1403.75 | 126.34 | 126.34 | 1656.43 | 1499069.15 | RC2023 line 2.iv
2.1.5 | 40000239 | Excavation of partially sub-merged soil and back filling (back filling shall be done in layers of 500mm; sprinkling of water and compaction thereafter followed bydisposal of excess quantity of excavated soil at suitable place afterback filling), & if required for filling the foundation, borrowedearth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer-in-charge. | CUM | 905 | 421.13 | 37.9 | 37.9 | 496.93 | 449721.65 | RC2023 line 2.v
2.1.6 | 40000240 | Excavation of fully sub-merged soil and back filling (back filling shall be done in layers of 500mm; sprinkling of water and compaction thereafter followed bydisposal of excess quantity of excavated soil at suitable place afterback filling), & if required for filling the foundation, borrowedearth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required as per instruction of Engineer-in-charge. | CUM | 905 | 421.13 | 37.9 | 37.9 | 496.93 | 449721.65 | RC2023 line 2.vi
3.1.1 | 30000566 | Design, Engineering, Providing and laying of plain cement concrete (PCC1:3:6) of grade M10 with approved quality coarse aggregates (Nominalsize 12mm to 20mm) , fine aggregates, cement in tower foundation asblind layer inclusive of labour charges for concrete mixing <(>&<)>curing. This includes supply of all labourers, T<(>&<)>P and dewateringwherever required as per Technical specification and instruction ofEngineer In charge. | CUM | 200 | 6377.44 | 573.97 | 573.97 | 7525.38 | 1505076 | R C Rate 2025 Annexure-I,TL, SL No.1.2(iii)
3.1.2 | 30000570 | Design, Engineering, Providing and laying of reinforced cement concrete(RCC1:1.5:3) of grade M20 with supply of approved quality coarseaggregates(Nominal size 12mm to 20mm), fine aggregates, cement intower foundation and inclusive of labour charges for concrete mixing,supply and fixing of form boxes, curing, shoring, shuttering, testing ofsample cement concrete cubes as per IS. The surrounding area shall beclear from materials. Damage of land if any by the contractor shall berepaired before measurement. This includes supply of all labourers, T<(>&<)>P, head loading of all type of Civil materials and dewatering (including Supply of all T<(>&<)>P, Fuel, Lubricant <(>&<)>electricity etc.) as per Technical specification and instruction ofEngineer In charge. | CUM | 1500 | 9103.72 | 819.33 | 819.33 | 10742.38 | 16113570 | R C Rate 2025 Annexure-I,TL, SL No.1.4(i)
3.1.3 | 30000573 | Cutting bending hooking, fixing and binding in position of MS bars for reinforcement of foundation concrete of towers including supply of wire for binding -Without supply of steel rod. per MT. | MT | 80 | 63984.42 | 5758.6 | 5758.6 | 75501.62 | 6040129.6 | R C Rate 2025 Annexure-I,TL, SL No.1.1
| 30000589 | 1000mm - In Soft/Loose/Muddy soil without under reamed (UR)-Pile foundation (under reamed (UR)/ without under reamed (UR): Boring for under reamed (UR) cast in situ piling with betonite showing for stabilisation of bore per Mtr.length. | Mtr. | 500 | 4535.07 | 408.16 | 408.16 | 5351.39 | 2675695
|  | 500mm - In Soft/Loose/Muddy soil without under reamed (UR)-Pile foundation (under reamed (UR)/ without under reamed (UR): Boring for under reamed (UR) cast in situ piling with betonite showing for stabilisation of bore per Mtr.length. | Mtr. | 1500 | 1700.65 | 153.06 | 153.06 | 2006.77 | 3010155
| 30000606 | Supply and putting of MS liner:Pile foundation (under reemed/ without under reemed: Boring for under reemed cast in situ piling with betonite showing for stabilisation of bore per Per MT. | MT | 10 | 63984.42 | 5758.6 | 5758.6 | 75501.62 | 755016.2
| 40000245 | Pile riser (if required), capping, tie beams etc, required for stub setting including supply of cement, different gradient for concrete ratio 1:1.5:3 (Grade M-20.) including curing of all type of soil and back filling etc. with supply of all labour T & P as per the direction of Engineer-in Charge including construction of approach road to the location and other arrangements. | CUM | 500 | 9103.72 | 819.33 | 819.33 | 10742.38 | 5371190 | R C Rate 2025 Annexure-I,TL, SL No.1.4(i)
4.1 | 30000080 | Bolt and nut welding (continuous welding) around the bolts (including supply of electrodes and zinc rich paints with application after welding) Per bolt | Nos. | 60000 | 10.24 | 0.92 | 0.92 | 12.08 | 724800 | R C Rate 2025 Annexure-I,TL, SL No.-1.1(i)
5 |  | SHORING & SHUTTERING-Required in submerged or special locations of open cast type foundations with supply of all materials,T&P,head loading and Labour. | SQ.MTR. | 5000 | 452.32 | 40.71 | 40.71 | 533.74 | 2668700 | R C Rate 2025 Annexure-I,TL, SL No.-3
6 |  | Head-Loading of all types of tower structures, conductors, Insulators, Hard-wares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of site Engineer-In- Charge and approval of the General Manager of Concerned circle. | Per MT-Mtr | 100000 | 13.26 | 1.19 | 1.19 | 15.64 | 1564000 | R C Rate 2025 Annexure-I,TL, SL No.-1.6
7.1 | 40000243 | REVETMENT: Excavation in all type of soil including rock & back filling including supply of sand with back filling for revetment (includes benching) | CUM | 1000 | 366.54 | 32.99 | 32.99 | 432.52 | 432520 | R C Rate 2025 Annexure-I,TL, SL No.1.0(ii)
7.2 | 30000566 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply all materials cements, sand chips etc. | CUM | 100 | 6235.72 | 561.21 | 561.21 | 7358.14 | 735814 | R C Rate 2025 Annexure-I,TL, SL No.1.2(iii)
7.3 | 30000568 | With cement and without rod - Providing and laying ordinary plain/reinforced concrete work of Grade M- 150(1:2:4)with approved quality stone chips of nominal size 20mm in tower foundation and coping inclusive of cost of mixing,laying curing etc.and cost of all materials (Form Boxes and other consumables to be supplied by the contractor) conforming to relevant IS., for transmission line per Cum. | CUM | 50 | 7723.79 | 695.14 | 695.14 | 9114.07 | 455703.5 | R C Rate 2025 Annexure-I,TL, SL No.1.3(i)
7.4 | 30000069 | Random Rubble Masonary in ratio 1:5 with supply of rubble, good quality river sand, Labour and T&P. per Cum | CUM | 400 | 3805.47 | 342.49 | 342.49 | 4490.45 | 1796180 | R C Rate 2025 Annexure-I,TL, SL No.1.1(i)
7.5 | 30000071 | With supply of cement - Cement Plastering with Mortar of 1:6 ratio with supply of all fine aggregates(good quality river sand), all labour and T&P per Sqm | SQM | 250 | 116.39 | 10.48 | 10.48 | 137.35 | 34337.5 | R C Rate 2025 Annexure-I,SS, SL No.1.5(i)
7.6 | 30000077 | Stone pitching-Laterite stone pitching with supply of Late rite stone, all Labour and T&P per Cum. | CUM | 250 | 2561.38 | 230.52 | 230.52 | 3022.42 | 755605 | R C Rate 2025 Annexure-I,TL, SL No.1.3
8 | 30000857 | Painting of Tower Structures by applying one coat of zinc phosphateprimer of ASIAN / BERGER make, 2 coats of Aluminium paint of ASIAN/BERGER make and applying one coat of black enamel paint over tower legs up to height of 1 mtr. including cost of material,consumables, T<(>&<)>P and as per the instruction of the Engineer inCharge (Scrapping and washing of structures are to be done prior to painting of towers) and applying | SQ.MTR. | 200 | 146.36 | 13.17 | 13.17 | 172.7 | 34540 | RC Rates
9.1 | 30000557 | Up to 30 mtr lead-Supply of borrowed earth(BE)/morrum for back filling(BF) for Revetment works per Cum.. | CUM | 100 | 285.4 | 25.686 | 25.686 | 336.772 | 33677.2 | RC Rates
9.2 | 30000558 | Beyond 30 mtr & up to 100mtr lead-Supply of borrowed earth(BE)/morrum for back filling(BF) for Revetment works per Cum.. | CUM | 500 | 395.19 | 35.5671 | 35.5671 | 466.3242 | 233162.1 | RC Rates
9.3 | 30000559 | Beyond 100mtr lead-Supply of borrowed earth(BE)/morrum for back filling(BF) for Revetment works per Cum.. | CUM | 1000 | 541.55 | 48.7395 | 48.7395 | 639.029 | 639029 | RC Rates
10 | 40000246 | PTCC approval, railway crossing has to be obtained by submitting the required documents to the concerned department through OPTCL. Way-Leave blockade charges and any other charges are to be borne by the bidders. The documents for PTCC clearance & Railway clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Price Taken from RTSS-Bhanjapur order
11.1 | 30000888 | Compensation for construction of Tower foudation <(>&<)> erection oftransmission line including crops compensation <(>&<)> etc. (100% Benchmark cost plus other compensation) | Per Location | 42 | 100000 | 9000 | 9000 | 118000 | 4956000 | Price taken from Lumsum amount on assumption bais.
11.2 | 30000878 | Compensation for or acquisition of ROW in the land required <(>&<)>trees <(>&<)> crops compensation to owners for transmission linecorridor as per the required width (15% Bench mark cost plus othercompensation if any) | RKM | 11.5 | 500000 | 45000 | 45000 | 590000 | 6785000 | Price taken from Lumsum amount on assumption bais.
12 | 30000883 | Forest clearances ( Stage-I <(>&<)> II) (excluding payment of statutoryfees) has to be obtained by submitting the required docuemnts to theconcerned departments through OPTCL. The documents for above clearancesincluding required drawings etc. have to be submitted by the contractorwithin 06 months of award of contract. The contractor have to pay thecompensation towards standing trees in the non-forest land <(>&<)> treefelling cost in the non-forest land. Beyond the above period, L.D isapplicable <(>&<)> the amount shall be deducted as specified in thespecification. | Per Hac | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Price taken from Lumsum amount on assumption bais.
13 | 40000247 | NHAI, Water,Gas/Oil pipeline, Power line and other statutory/government body clearances except Forest clearance (excluding payment of statutory fees) have to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 05 months of award of contract. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | LS | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | LS
14 |  | Dismantling of tower super structure with N&B as per instruction of Engineer incharge,as a percentage(80%) of erection charges. [07 nos tower & other structure, equipments] | MT | 100 | 5908.9 | 531.801 | 531.801 | 6972.502 | 697250.2
15 |  | Dismantling,delivery and stacking of strung ACSR Panther conductor (6 conductor with one earth wire/OPGW nearest OPTCL store as per instruction of Engineer incharge,in % of stringing charges. | RKM | 0.75 | 62320.52 | 5608.8468 | 5608.8468 | 73538.2136 | 55153.6602
B |  | CIVIL COMPONENT OF THE WORKS CONTRACT FOR 220 KV LILO TRANSMISSION LINE | [6 empty] | 65717653.4702

## BAY EXTN
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
Sl. No. | SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY | Basic Price Per Unit (Taxable Value) In Rs | CGST@ 9% PER UNIT (Inter-State) | SGST@9% PER UNIT (Inter-State) | TOTAL PRICE PER UNIT (In Rs) | TOTAL PRICE
1 | 2 | 3 | 4 | 5 | 6=5X9% | 7=5X9% | 8=6+7+5 | 9=8X5
A | SUBSTATION -Supply of Equipments and materials | [7 empty] | cd
1 | 245 KV, 1200-600-300 A, 50 KA, 5 core Single Phase Current Transformer (4 Nos PX Class & 1 No. 0.2s Class) | NOS | 6 | 382298.97 | 34406.9073 | 34406.9073 | 451112.7846 | 2706676.7076 | 21
2 | 245 KV,2000A,40KA,ISOLATORS, S/I WITH OUT EARTH SWITCH | NOS | 6 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 4224495.5328 | 5
3 | 245 KV,2000A,40KA,ISOLATORS, S/I WITH SINGLE EARTH SWITCH | NOS | 2 | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 1831043.6656 | 6
4 | 245 KV,2000A,40KA,ISOLATORS, BEAM MOUNTED S/I WITHOUT EARTH SWITCH | NOS | 2 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 1408165.1776 | 5
5 | 245 KV, 3CORE, SINGLE PHASE VOLTAGE TRANSFORMER | NOS | 6 | 134349.71 | 12091.4739 | 12091.4739 | 158532.6578 | 951195.9468 | 34
6 | 245KV,3150A,50KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 1365681.73 | 122911.3557 | 122911.3557 | 1611504.4414 | 3223008.8828 | 2
7 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). | NOS | 12 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 1012284.948 | 30
8 | 220 KV Bus Post Insulators | NOS | 28 | 22505 | 2025.45 | 2025.45 | 26555.9 | 743565.2
9 | BUS BAR & CIRCUIT MATERIALS
9.1 | ANTI FOG TYPE INSULATOR
9.1.1 | 160 KN Long Rod Porcilain INSULATOR(220KV Side) | NOS | 28 | 14593.68 | 1313.4312 | 1313.4312 | 17220.5424 | 482175.1872 | 60 line
9.1.2 | 90 KN Long Rod Porcilain INSULATOR (220KV Side) | NOS | 12 | 11187.5 | 1006.875 | 1006.875 | 13201.25 | 158415 | 59 line
9.2 | ACSR MOOSE CONDUCTOR | KMS | 1.5 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 791062.0113 | 19 line
9.3 | IPS 4" ALUMINIUM TUBES(OD:114.2 mm & 8.51mm Thickness)( Required for Equipment to equipment connection in 220 KV side only) including welding sleeves,corona bell etc. | MTRS | 200 | 3052.392 | 274.7153 | 274.7153 | 3601.8226 | 720364.512
9.4 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS
9.4.1 | 220 KV Single Tension H/W fitting for twin moose ACSR | NOS | 12 | 6614.245 | 595.282 | 595.282 | 7804.8091 | 93657.7092
9.4.2 | 220 KV Single Tension H/W fitting for single moose ACSR | NOS | 32 | 4264.447 | 383.8002 | 383.8002 | 5032.0475 | 161025.5187
9.4.3 | 220 KV Single Suspension H/W fitting for single mose ACSR | NOS | 14 | 5687.638 | 511.8874 | 511.8874 | 6711.4128 | 93959.7798
9.4.4 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose, Interconnector suitable for IPS tube, equipments for 220KV system for completion of work in all respect. | LOT | 1 | 300000 | 27000 | 27000 | 354000 | 354000
10 | CT Console Box | NO | 2 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 106456.0128 | 75
11 | SUBSTATION EARTHING SYSTEMS
11.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) | MT | 3 | 70000 | 6300 | 6300 | 82600 | 247800 | Badakushasthali SS 13.2
11.2 | EARTHING CONDUCTOR: 50X6 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MT | 2.5 | 70000 | 6300 | 6300 | 82600 | 206500 | Badakushasthali SS 13.3
11.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos. | 65 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 172721.497 | Badakushasthali SS 13.4
12 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS.
12.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 450 | 781.2 | 70.308 | 70.308 | 921.816 | 414817.2 | Autonagar Sl no- 14.1
12.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 300 | 624.75 | 56.2275 | 56.2275 | 737.205 | 221161.5 | Autonagar Sl no- 14.2
12.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 150 | 469.35 | 42.2415 | 42.2415 | 553.833 | 83074.95 | Autonagar Sl no- 14.3
12.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 1 | 93451 | 8410.59 | 8410.59 | 110272.18 | 110272.18 | CD TL 4
13 | SUB STATION SWITCYARD BMK,AC CONSOLE & OTHER MARSHALLING BOXES
13.1 | BAY MARSHALLING KIOSK (02 nos on 220 kV bay) | NOS | 2 | 150362.04 | 13532.5836 | 13532.5836 | 177427.2072 | 354854.4144 | 76
14 | SWITCH YARD STRUCTURES (LATTICE TYPE FOR TOWER COLUMN & BEAMS FOR ALL EQUIPMENT COLUMN) FOR 220KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
14.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
14.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.8 MT) (08 NOS.) | MT | 38.4
14.1.2 | Q1-220KV BEAMS (NOMINAL UNIT WT- 1.628 MT) (6 NOS.) | MT | 9.768
14.1.3 | Q3-220KV BEAMS (NOMINAL UNIT WT-2.5 MT) (4 NOS.) | MT | 10
14.1.4 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 58.168 | 82451 | 7420.59 | 7420.59 | 97292.18 | 5659291.5262 | structure rc
14.2 | EQUIPMENT SUPPORT STRUCTURES (LATTICE TYPE) FOR ALL 220KV EQUIPMENTS INCLUDING FOUNDATION BOLTS & NUTS
14.2.1 | ISOLATORS-220KV ( SI with E/S-2 No.) | MT | 3.049
14.2.2 | ISOLATORS-220KV (SI without E/S -6Nos.) | MT | 9.148
14.2.3 | CTS-220 KV (6 nos.) | MT | 1.565
14.2.4 | CVTS-220 KV (6 nos.) | MT | 1.815
14.2.5 | Surge Arrester-220 Kv( 6 nos.) | MT | 3.208
14.2.6 | BPI-220 KV (28nos.) | MT | 7.945
14.2.7 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE | MT | 26.73 | 82451 | 7420.59 | 7420.59 | 97292.18 | 2600619.9714 | structure rc
14.3 | Total weight of different size of GI Nuts and bolts for structures. | MT | 1.5 | 102000 | 9180 | 9180 | 120360 | 180540 | structure rc
15 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.)
15.1.1 | XLPE 3.5 CX300 mm2 | Kms | 0.1 | 1027095.19 | 92438.5671 | 92438.5671 | 1211972.3242 | 121197.2324 | CD SS 134
15.1.2 | XLPE 3.5 CX185 mm2 | Kms | 0.1 | 488678.88 | 43981.0992 | 43981.0992 | 576641.0784 | 57664.1078 | CD SS 132
15.1.3 | XLPE 3.5 CX120 mm2 | Kms | 0.1 | 459114.77 | 41320.3293 | 41320.3293 | 541755.4286 | 54175.5429 | CD SS 131
15.1.4 | XLPE 3.5 CX70 mm2 | Kms | 0.3 | 265690.44 | 23912.1396 | 23912.1396 | 313514.7192 | 94054.4158 | CD SS 129
15.1.5 | XLPE 3.5 CX35 mm2 | Kms | 0.3 | 147505.32 | 13275.4788 | 13275.4788 | 174056.2776 | 52216.8833 | CD SS 127
15.1.6 | XLPE 4 CX 16 mm2 | Kms | 0.3 | 115785.43 | 10420.6887 | 10420.6887 | 136626.8074 | 40988.0422 | CD SS 125
15.1.7 | XLPE 4CX 6 sqmm | Kms | 0.3 | 114300 | 10287 | 10287 | 134874 | 40462.2 | BADAKUSTHASTHALI 16.1.7
15.1.8 | XLPE 2CX 6 sqmm | Kms | 0.3 | 114300 | 10287 | 10287 | 134874 | 40462.2 | BADAKUSTHASTHALI 16.1.8
15.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
15.2.1 | 2 CX 2.5 mm2 | Kms | 6.5 | 75413.59 | 6787.2231 | 6787.2231 | 88988.0362 | 578422.2353 | 107
15.2.2 | 4 CX 2.5 mm2 | Kms | 5 | 123673.44 | 11130.6096 | 11130.6096 | 145934.6592 | 729673.296 | 109
15.2.3 | 5 CX 2.5 mm2 | Kms | 0.2 | 184820 | 16633.8 | 16633.8 | 218087.6 | 43617.52 | BADAKUSTHASTHALI 16.2.2
15.2.4 | 7CX 2.5 mm2 | Kms | 3 | 187201.82 | 16848.1638 | 16848.1638 | 220898.1476 | 662694.4428 | 110
15.2.5 | 10 CX 2.5 mm2 | Kms | 1.5 | 254413.65 | 22897.2285 | 22897.2285 | 300208.107 | 450312.1605 | 111
15.2.6 | 12 CX 2.5 mm2 | Kms | 1.5 | 289732.51 | 26075.9259 | 26075.9259 | 341884.3618 | 512826.5427 | BADAKUSTHASTHALI 16.2.5
15.2.7 | 16 CX 2.5 mm2 | Kms | 1.5 | 387033.75 | 34833.0375 | 34833.0375 | 456699.825 | 685049.7375 | 112
15.2.8 | 19 CX 2.5 mm2 | Kms | 0.2 | 448832.3 | 40394.907 | 40394.907 | 529622.114 | 105924.4228 | 113
16 | ACCESSORIES FOR PLCC SYSTEM With OPGW cable
16.1 | 48 Fibre Optic Approach cable along with HDPE Pipes | Kmtr | 0.5 | 127089.72 | 11438.0748 | 11438.0748 | 149965.8696 | 74982.9348
17 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area)
17.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).The qty of lighting fixtures shall bs as per the Lighting calculation. | SET | 16 | 12000 | 1080 | 1080 | 14160 | 226560 | BADAKUSHASTHALI 19.1
17.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. N.B.: Actual quantity shall be as per site condition and as per approval of the competent authority considering the Lux standard. | SET | 8 | 30000 | 2700 | 2700 | 35400 | 283200 | BADAKUSHASTHALI 19.2
17.3 | AIR CONDITIONING: Supply of 2T capacity Split Air Conditioning Units (Dual Inverter, five star latest model - LG/Samsung/Hitachi/Carrier/Mitsubishi/Voltas/Daikin Make) with copper condensor having remote temperature & operation control facility with voltage stabilizer. Following item description also includes AC Control Panel made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 15 amp socket & plug for each unit of AC etc to complete (As per specification) for Switchyard Kisok, Transit House. Control Panel shall be one each at different rooms. Supply of Logic controller for Auto Switch ON & OFF of AC units depending on requirement. Also includes supply of all other additional accessories such as copper tubes, copper cable, steel brackets for holding outdoor units and other accessories necessary for completion of the AC system.As per approved drawing and direction of engineer-in-charge. | SET | 4 | 70000 | 6300 | 6300 | 82600 | 330400 | market rate
18 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-INST TO BIDDER BEFORE DESIGN-SL NO 16-ANNEXURE - I)
18.1 | FOAM TYPE-9 LTRS | NOS | 1 | 6430 | 578.7 | 578.7 | 7587.4 | 7587.4 | BADAKUSHASTHALI 21.1
18.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 1 | 49733 | 4475.97 | 4475.97 | 58684.94 | 58684.94 | BADAKUSHASTHALI 21.2
18.3 | DRY POWDER TYPE - 5 KGS | NOS | 1 | 10020 | 901.8 | 901.8 | 11823.6 | 11823.6 | BADAKUSHASTHALI 21.3
18.4 | CO2 - 4.5 KGS | NOS | 1 | 21390 | 1925.1 | 1925.1 | 25240.2 | 25240.2 | BADAKUSHASTHALI 21.4
18.5 | CO2 - 9 KGS | NOS | 1 | 31620 | 2845.8 | 2845.8 | 37311.6 | 37311.6 | BADAKUSHASTHALI 21.5
18.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 1 | 37241 | 3351.69 | 3351.69 | 43944.38 | 43944.38 | BADAKUSHASTHALI 21.6
18.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND | SET | 1 | 5415 | 487.35 | 487.35 | 6389.7 | 6389.7 | BADAKUSHASTHALI 21.7
19 | 220 KV SIDE PROTECTION PANELS (220KV Level):-
19.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, separate Backup Protection relays, Bay control unit (BCU), 2nos DCCO & other protection and aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. Ethernet FIBER switch for augmentation of SAS with existing SAS system. | Nos | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | SS-37
20 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NO | 4 | 2500 | 225 | 225 | 2950 | 11800 | BADAKUSHASTHALI 40
A | TOTAL OF SUPPLY FOR SS-2C | [6 empty] | 41534445.7984
Sl. No. | DESCRIPTION OF ITEMS(SCHEDULE-2C) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT OF MEASUREMENT | QUANTITY | Basic Price Per Unit (Taxable Value) In Rs | CGST@ 9% PER UNIT (Inter-State) | SGST@9% PER UNIT (Inter-State) | TOTAL PRICE PER UNIT (In Rs) | TOTAL PRICE
1 | 2 | 3 | 4 | 5 | 6=5X9% | 7=5X9% | 8=6+7+5 | 9=8X5
B | ELECTRICAL WORKS
1 | 245 KV, 1200-600-300 A, 50 KA, 5 core Single Phase Current Transformer (4 Nos PX Class & 1 No. 0.2s Class) | NOS | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | 10.10.h.(i)
2 | 245 KV,2000A,40KA,ISOLATORS, S/I WITH OUT EARTH SWITCH | NOS | 6 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 211552.3824 | 10.10.b.(i)
3 | 245 KV,2000A,40KA,ISOLATORS, S/I WITH SINGLE EARTH SWITCH | NOS | 2 | 33153.68 | 2983.8312 | 2983.8312 | 39121.3424 | 78242.6848 | 10.10.d.(i)
4 | 245 KV,2000A,40KA,ISOLATORS, BEAM MOUNTED S/I WITHOUT EARTH SWITCH | NOS | 2 | 23501.34 | 2115.1206 | 2115.1206 | 27731.5812 | 55463.1624 | 10.10.c.(i)
5 | 245 KV, 3CORE, SINGLE PHASE VOLTAGE TRANSFORMER | NOS | 6 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 111124.494 | 10.10.h.(i)
6 | 245KV,3150A,50KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 2 | 97698.43 | 8792.8587 | 8792.8587 | 115284.1474 | 230568.2948 | 10.10.a.(i)
7 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). | NOS | 12 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 73686.7992 | 10.10.i.(i)
8 | 220 KV Bus Post Insulators | NOS | 28 | 2853.73 | 256.8357 | 256.8357 | 3367.4014 | 94287.2392 | 10.10.j (i)
10 | SWITCH YARD STRUCTURES (LATTICE TYPE FOR TOWER COLUMN & BEAMS & PIPE TYPE FOR ALL EQUIPMENT COLUMN) FOR 220KV CLASS INCLUDING FOUNDATION BOLTS & NUTS.
10.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS
10.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.8 MT) (08 NOS.) | MT | 38.4
10.1.2 | Q1-220KV BEAMS (NOMINAL UNIT WT- 1.628 MT) (6 NOS.) | MT | 9.768
10.1.3 | Q3-220KV BEAMS (NOMINAL UNIT WT-2.5 MT) (4 NOS.) | MT | 10
10.1.4 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 58.168 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 400055.9227 | 16.1
10.2 | EQUIPMENT SUPPORT STRUCTURES (LATTICE TYPE) FOR ALL 220KV EQUIPMENTS INCLUDING FOUNDATION BOLTS & NUTS
10.2.1 | ISOLATORS-220KV ( SI with E/S-2 No.) | MT | 3.049
10.2.2 | ISOLATORS-220KV (SI without E/S -6Nos.) | MT | 9.148
10.2.3 | CTS-220 KV (6 nos.) | MT | 1.565
10.2.4 | CVTS-220 KV (6 nos.) | MT | 1.815
10.2.5 | Surge Arrester-220 Kv( 6 nos.) | MT | 3.208
10.2.6 | BPI-220 KV (28nos.) | MT | 7.945
10.2.7 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE | MT | 26.73 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 183838.1037 | 16.1
10.3 | Total weight of different size of GI Nuts and bolts for structures. | MT | 1.5 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 10316.3919 | 16.1
11 | BUS-BAR STRINGING:- Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors,hoisting of single or double insulator strings,Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments,testing,commissioning etc. as per the instruction of Engineer-in charge.
11.1 | Single conductor/Phase/Mtr. | KM | 0.75 | 184650 | 16618.5 | 16618.5 | 217887 | 163415.25 | 14.e.i
11.2 | Twin Conductor /Phase/Mtr. | KM | 0.25 | 252050 | 22684.5 | 22684.5 | 297419 | 74354.75 | 14.f.i
11.3 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | MTRS | 200 | 451.647 | 40.6482 | 40.6482 | 532.9435 | 106588.692 | Badakushasthali 24 ( SANCTION ESTIMATE ON DATED 07.02.2025)
12 | SUB-STATION EARTH-MAT:- Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification.
12.1 | (i)75x10 MM GI FLAT | MTRS | 500 | 110.27 | 9.9243 | 9.9243 | 130.1186 | 65059.3
12.2 | (ii)50x6 MM GI FLAT | MTRS | 1064 | 86.64 | 7.7976 | 7.7976 | 102.2352 | 108778.2528
12.4 | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | Nos | 65 | 2993 | 269.37 | 269.37 | 3531.74 | 229563.1
13 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS.
13.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 450 | 200 | 18 | 18 | 236 | 106200
13.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 300 | 200 | 18 | 18 | 236 | 70800
13.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 150 | 200 | 18 | 18 | 236 | 35400
13.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 1 | 10000 | 900 | 900 | 11800 | 11800
14 | BAY MARSHALLING KIOSK (02 Nos on 220 kV bay) | Nos | 2 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 7210.2012
15 | Erection of console box for CT,PT,CVT | Nos | 2 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 7210.2012
16 | Laying of Power and Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs,Ferrules,clamps,connectors,glands,fixing of cable trays, including supply of N&B,Link plates,Cable Markers,PVC pipes Bends,Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements,laying of Earthing Flats,earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor
16.1 | POWER CABLES,1.1KV,XLPE & PVC ARMOURED, ALUMINIUM CONDUCTOR (As per Specification)
16.1.1 | XLPE 3.5 CX300 mm2 | MTR | 100 | 2284.14 | 205.5726 | 205.5726 | 2695.2852 | 269528.52 | RC SS 17.20
16.1.2 | XLPE 3.5 CX185 mm2 | MTR | 100 | 1732.79 | 155.9511 | 155.9511 | 2044.6922 | 204469.22 | RC SS 17.20
16.1.3 | XLPE 3.5 CX120 mm2 | MTR | 100 | 1023.93 | 92.1537 | 92.1537 | 1208.2374 | 120823.74 | RC SS 17.20
16.1.4 | PVC 3.5 CX70 mm2 | MTR | 120 | 685.24 | 61.6716 | 61.6716 | 808.5832 | 97029.984 | RC SS 17.20
16.1.5 | PVC 3.5 CX35 mm2 | MTR | 300 | 519.83 | 46.7847 | 46.7847 | 613.3994 | 184019.82 | RC SS 17.20
16.1.6 | PVC 4 CX 16 mm2 | MTR | 300 | 275.67 | 24.8103 | 24.8103 | 325.2906 | 97587.18 | RC SS 17.20
16.1.7 | PVC 4CX 6 sqmm | MTR | 300 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 55765.62 | RC SS 17.20
16.1.8 | PVC 2CX 6 sqmm | MTR | 300 | 126.02 | 11.3418 | 11.3418 | 148.7036 | 44611.08 | RC SS 17.20
16.2 | CONTROL CABLES,1.1 KV, PVC,STRANDED COPPER(As per specification)
16.2.1 | 2 CX 2.5 mm2 | MTR | 6500 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 422923.8 | RC SS 17.10
16.2.2 | 4 CX 2.5 mm2 | MTR | 12000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 780782.4 | RC SS 17.10
16.2.3 | 5 CX 2.5 mm2 | MTR | 200 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 13013.04 | RC SS 17.10
16.2.4 | 7CX 2.5 mm2 | MTR | 3000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 195195.6 | RC SS 17.10
16.2.5 | 10 CX 2.5 mm2 | MTR | 1500 | 63 | 5.67 | 5.67 | 74.34 | 111510 | RC SS 17.10
16.2.6 | 12 CX 2.5 mm2 | MTR | 1500 | 63 | 5.67 | 5.67 | 74.34 | 111510 | RC SS 17.10
16.2.7 | 16 CX 2.5 mm2 | MTR | 1500 | 63 | 5.67 | 5.67 | 74.34 | 111510 | RC SS 17.10
16.2.8 | 19 CX 2.5 mm2 | MTR | 200 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 18589.72 | RC SS 17.10
17 | Switch yard lighting: Design, engineering, procurement of labour, material including all associated works for construction of switch yard lightings as per technical specification and approved drawings. The fixture shall be of reputed make and fixtures shall be LED and proper cabling from the lighting outdoor distribution boards to the junction boxes and from junction boxes to the fixtures. The lighting fixtures are to be installed on the switch yard structures. The quantity of such fixtures are to be designed and to be ascertained.
17.1 | INSTALLATION OF SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved). | Set | 16 | 2651.53 | 238.6377 | 238.6377 | 3128.8054 | 50060.8864 | RC SS 32.10
17.2 | INSTALLATION OF STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS), COLONY QUARTERS AND OTHER ROADS. ALL MATERIALS AS PER APPROVED DRAWING AND SPECIFICATION TO COMPLETE. THE STREET LIGHTING SYSTEM. PROPER EARTHING AS PER STANDARD PRACTICE. (ALL THE STREET LIGHT POLE SHALL BE OF GI TUBULAR POLE AND PROVISION OF A GI JUNCTION BOX WITH SUITABLE COVERS AT A HEIGHT OF 1 METRE FROM THE GROUND. THE JUNCTION BOX SHALL HAVE PROVISION OF FUSES, BUSES, CONNECTORS FOR CABLE IN AND OUT. | Set | 8 | 2651.53 | 238.6377 | 238.6377 | 3128.8054 | 25030.4432 | RC SS 32.10
18 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR Outdoor bay kiosk (*SUPPLY OF CABLES ARE COVERED IN CABLE ITEMS AS INDICATED ABOVE) | Set | 4 | 3000 | 270 | 270 | 3540 | 14160
19 | 220KV Level
19.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. supply and installation of HDPE pipe for Optical fibre cable routing as per the direction of the engineer in charge. This includes design ,drawing, supervision, installation , testing & commissioning. Supply of documentation, manuals, drawing, software & training. | Nos. | 2 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 59424.8236 | RC SS-H- 18.10- (iii)
44 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Set | 1 | 50000 | 4500 | 4500 | 59000 | 59000
B | TOTAL of ELECTRICAL WORKS SS | [6 empty] | 5593185.5935
C | CIVIL WORKS_TRANSMISSION LINE EQUIPMENT AND MATERIALS | UNIT OF MEASUREMENT | QUANTITY | Basic Price Per Unit (Taxable Value) In Rs | CGST@ 9% PER UNIT (Inter-State) | SGST@9% PER UNIT (Inter-State) | TOTAL PRICE PER UNIT (In Rs) | TOTAL PRICE
1 | 2 | 3 | 4 | 5 | 6=5X9% | 7=5X9% | 8=6+7+5 | 9=8X5
1 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P
1.1 | LEVELLING OF S/S AREA:Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification.
1.1.1 | CUTTING of substation area :- Any type soil (Dense Soil) | CUM | 50 | 296.35 | 26.6715 | 26.6715 | 349.693 | 17484.65 | rc 1.2.ii
1.1.2 | FILLING of substation area with borrowed earth with supply of all labour,T & P. (iii) Beyond 100mtr lead | CUM | 600 | 1170.92 | 105.3828 | 105.3828 | 1381.6856 | 829011.36 | 1.3.iii
2 | Anti-Weed Treatment :- Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treatment of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge. | Sq.Mtrs | 5000 | 17.84 | 1.6056 | 1.6056 | 21.0512 | 105256 | Badakushasthali 24
3 | OPEN CAST FOUNDATIONS WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc: Design, engineering, supply of all labour, T&P, material (Cement-As Per TS,MS Rod ( FE-500 as per BIS-1786), coarse and fine aggregates (Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the 220KV Column &equipment support & others such as Lighting cum lightning mast, LT distribution boards etc as per the technical specification and approved drawings. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
3.1 | EXCAVATION FOR PREPARATION OF FOUNDATION WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc.: This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge.
3.1.1 | Normal/Soft Soil | Cum | 100 | 187.17 | 16.8453 | 16.8453 | 220.8606 | 22086.06 | 2.1.i
3.1.2 | Dense/Compact Soil | Cum | 350 | 296.35 | 26.6715 | 26.6715 | 349.693 | 122392.55 | 2.1.ii
3.1.3 | Soft rock Not required blasting | Cum | 80 | 662.88 | 59.6592 | 59.6592 | 782.1984 | 62575.872 | 2.1.iv
3.1.4 | Hard Rock required Blasting | Cum | 50 | 1091.81 | 98.2629 | 98.2629 | 1288.3358 | 64416.79 | 2.1.v
3.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in for the above column/equipment/marshalling box foundations for column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 50 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 357455.04 | 3.20 i
3.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 350 | 8751.26 | 787.6134 | 787.6134 | 10326.4868 | 3614270.38 | 3.4 i
3.4 | Supply of steel different sizes(TATA/RINL/SAIL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 30 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 2265048.468 | 3.5
4 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Brickwork with KB brick ,plastering (!:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}.
4.1 | Cable trench with covers
4.1.1 | Section 1-1 | Mtrs | 50 | 17788.46 | 1600.9614 | 1600.9614 | 20990.3828 | 1049519.14 | Badakushasthali 4.1.1
4.1.2 | Section 2- 2 | Mtrs | 50 | 17788.46 | 1600.9614 | 1600.9614 | 20990.3828 | 1049519.14 | Badakushasthali 4.1.2
4.1.3 | Section 3-3 | Mtrs | 270 | 12019.23 | 1081.7307 | 1081.7307 | 14182.6914 | 3829326.678 | Badakushasthali 4.1.3
4.1.4 | Section 4-4 | Mtrs | 300 | 7211.54 | 649.0386 | 649.0386 | 8509.6172 | 2552885.16 | Badakushasthali 4.1.4
5 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:3:6 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 395 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 2823894.816 | `
6 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 520 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 2034857.136 | RC SS 5.10
7 | Roads: Design, construction of roads and walkways/ shoulders within sub-station as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. Provision of drains on both the side of the roads for easy discharge of rain water.
7.1 | 3.75 mtrs Concrete road with shoulder at both the side & shall have drain on both side of the road as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | MTRS | 150 | 5000 | 450 | 450 | 5900 | 885000 | Neulapoi 7.3
8 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. All the switcyard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification.
8.1 | Storm water drain | MTRS | 15 | 1000 | 90 | 90 | 1180 | 17700 | Badakusthasthali 11.2
8.2 | Road-culverts, drain crossings, Cable trench crossing | Lots | 1 | 200000 | 18000 | 18000 | 236000 | 236000
9 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing ( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick Masonry work with ratio mortar (cement and sand)1:5 and cement pointing of the joints, for the fencing upto a height of 350 mm from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | MTRS | 200 | 2240 | 201.6 | 201.6 | 2643.2 | 528640 | NEULAPOI 18
10 | Out door bay kiosks (01 for 220 kV Switchyard) : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The plinth area for the 220 kV Bay kiosk are 25 sq. mtrs each (5mx5m) approx. Doors shall be heat insulated and hinge type. The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. | [6 empty] | 0
10.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. | Lot | 1 | 300000 | 27000 | 27000 | 354000 | 354000
10.2 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
10.3 | Flooring of GIS room shall be epoxy paint of adequate thickness & Flooring adjacent panel rooms shall be with vitrified digital double charged tiles with dado as per technical spec & approved drawings. Provision of window blinders in the Panel room. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
10.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000
10.5 | Provision of ceiling in the adjacent panel room area as per specification mentioned in the civil section & approved drawings. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
10.6 | Doors shall be of Hinge type with locking facility and shall be of heat insulated type. As per technical spec & approved drawing. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000
10.7 | Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make),fixing of lighting fixtures & switchgear , Erection of all Lighting FIXTURES & LAMPS (LED), D.C emergency lighting (including supply). Concealed internal wiring for Cable connection for Internet LAN, socket for using Telephone including supply of all materials,board,connectors etc as required should also be considered. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
10.8 | Provision of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000
11 | CIVIL WORKS (DISMANTLING):- Dismantling/breaking of all concrete structures (of all grades) & Brick work in cement mortar by mechanical means using pneumatic tools, breaking to pieces and disposal of dismantled materials up to a lead of 1000 metres, stacking serviceable and unserviceable materials separately as per the instruction of Engineer Incharge including supply of T&P, labour etc for completion of work in all respect. | CUM | 250 | 3589.73 | 323.0757 | 323.0757 | 4235.8814 | 1058970.35
12 | Random Rubble Masonary in ratio 1:5 with supply of rubble, good quality river sand, Labour and T&P. per Cum | CUM | 410 | 3805.47 | 342.49 | 342.49 | 4490.45 | 1841084.5
13 | With supply of cement - Cement Plastering with Mortar of 1:6 ratio with supply of all fine aggregates(good quality river sand), all labour and T&P per Sqm | SQM | 250 | 116.39 | 10.48 | 10.48 | 137.35 | 34337.5
14 | Stone pitching-Laterite stone pitching with supply of Late rite stone, all Labour and T&P per Cum. | CUM | 250 | 2561.38 | 230.52 | 230.52 | 3022.42 | 755605
C | TOTAL OF (Civil Work) SS | [6 empty] | 27219336.59
Note on D15: OPTCL: 06NOS FOR TAKE UP POINT
Note on E22: Author: 400KV ESTIMATE RATE
Note on E24: Author: 10% escal with Chendipada estimate
Note on E25: Author: 10% escal with Chendipada estimate
Note on E26: Author: 10% escal with Chendipada estimate
Note on E62: Author: 400KV ESTIMATE
Note on E67: Author: 400KV ESTIMATE
Note on E70: Author: 400KV
Note on E76: Author: 400KV
Note on E77: Author: 400KV
Note on E78: Author: MARKET RATE
Note on E88: Author: 400KV ESTIMATE
Note on D102: OPTCL: 6nos for cable take up point
Note on E122: Author: 400KV
Note on E154: Author: 400KV
Note on E158: Author: 400KV
Note on E180: Author: 400kv
Note on E181: Author: 400kv
Note on E182: Author: 400kv
Note on E183: Author: 400kv
Note on E190: Author: market
Note on E191: Author: 400kv
Note on E193: Author: 400kv

## LINE CALCULATION (hidden)
CALCULATION SHEET
| SL NO | TYPE OF TOWER | QTY | EXCAVATION |  | PCC |  | RCC |  | MS ROD
|  |  |  | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT VOL | TOTAL VOL | UNIT WT | TOTAL WT
| 1 | OA+0 | 14 | 81.648 | 1143.072 | 1.152 | 16.128 | 11.988 | 167.832 | 0.23 | 3.22
| 2 | OA+3 | 20 | 89.376 | 1787.52 | 1.152 | 23.04 | 13.24 | 264.8 | 0.23 | 4.6
| 3 | OA+6 | 3 | 89.376 | 268.128 | 1.152 | 3.456 | 13.24 | 39.72 | 0.23 | 0.69
| 4 | OB+0 | 5 | 156.27 | 781.35 | 2.1125 | 10.5625 | 26.52 | 132.6 | 0.365 | 1.825
| 5 | OB+3 | 8 | 167.86 | 1342.88 | 2.1125 | 16.9 | 28.76 | 230.08 | 0.365 | 2.92
| 6 | OB+6 | 4 | 167.86 | 671.44 | 2.1125 | 8.45 | 28.76 | 115.04 | 0.365 | 1.46
| 7 | OC+0 | 5 | 271.04 | 1355.2 | 3.362 | 16.81 | 51.357 | 256.785 | 0.487 | 2.435
| 8 | OC+3 | 1 | 271.04 | 271.04 | 3.362 | 3.362 | 51.357 | 51.357 | 0.487 | 0.487
| 9 | OC+6 | 2 | 271.04 | 542.08 | 3.362 | 6.724 | 51.357 | 102.714 | 0.487 | 0.974
|  |  | 62 |  | 8162.71 |  | 105.4325 |  | 1360.928 |  | 18.611
| Pile |  |  | Pile (Unit) |  |  |  | Pile (Total)
SL NO | No of Pile / Tower | Length of each Pile (Mtr) |  | Pile Length | PCC (CUM) | RCC (CUM) | Steel (MT) | Pile Length | PCC (CUM) | RCC (CUM) | Steel (MT)
1 (AP-9) OC+6 | 12 | 12.5 |  | 150 | 0 | 38.7 | 2.115 | 150 | 0 | 38.7 | 2.115
0 | [7 empty] | 150 | 0 | 38.7 | 2.115
| Pile Cap & Beam (Unit) |  |  |  | Pile Cap & Beam (Total)
Type | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT)
OC | 50.832 | 5.31 | 51.952 | 2.7 | 50.832 | 5.31 | 51.952 | 2.7
TOTAL |  |  |  |  | 50.832 | 5.31 | 51.952 | 2.7
| Riser (Unit) |  |  |  | Riser (Total) |  |  |  | TOTAL OF PILE FOUNDATION
Type | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT)
OC | 0 | 0 | 16.128 | 0.763 | 0 | 0 | 16.128 | 0.763
TOTAL |  |  |  |  | 0 | 0 | 16.128 | 0.763 | 50.832 | 5.31 | 106.78 | 5.578
RIVER BED PILE FOUNDATION |  |  |  | Per Unit |  |  |  |  | Total
Type of Tower with Loc no | Pile Total | No of Pile / Tower | Length of each Pile (Mtr) | Pile Length |  | PCC (CUM) | RCC (CUM) | Steel (MT) | Pile Length | PCC (CUM) | RCC (CUM) | STEEL (MT)
OC+15 at Ap-14/0,15/0,16/0 | 3 | 16 | 15 | 240 |  | 0 | 47.143 | 3.74 | 720 | 0 | 141.429 | 11.22
| 3 | [7 empty] | 720 | 0 | 141.429 | 11.22
| Beam (Unit) |  |  |  | Beam (Total)
Type | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT)
OC+15 | 64.752 | 25.31 | 52.272 | 7.095 | 194.256 | 75.93 | 156.816 | 21.285
TOTAL | 64.752 | 25.31 | 52.272 | 7.095 | 194.256 | 75.93 | 156.816 | 21.285
| Pile Cap & Riser (Unit) |  |  |  | TOTAL |  |  |  | TOTAL OF RIVER BED PILE FOUNDATION
Type | Excavation (CUM) | PCC (CUM) | RCC (CUM) | Steel (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | STEEL (MT) | Excavation (CUM) | PCC (CUM) | RCC (CUM) | STEEL (MT)
OC | 0 | 0 | 16.128 | 0.763 | 0 | 0 | 48.384 | 2.289
TOTAL | 0 | 0 | 16.128 | 0.763 | 0 | 0 | 48.384 | 2.289 | 194.256 | 75.93 | 346.629 | 34.794
| TOTAL EXCAVATION | TOTAL PCC | TOTAL RCC (1:1.5:3) | TOTAL RCC (1:1:2) | TOTAL MS ROD
| 8407.798 | 186.6725 | 1467.708 | 346.629 | 58.983
| SL NO | AP | TOWER | ST FITTING | DT FITTING | SS FITTING | DS FITTING | VIBRATION DAMPER | EARTHING DEVICE
| 1 | AP-1A (108) | OC+0 | 12 | 0 | 0 | 0 | 12 | 1
| 2 | AP -1/0 | OC+0 | 12 | 0 | 0 | 0 | 12 | 1 | 03 NOS LR WILL BE USED AS PILOT
| 3 | AP-2/0 | OC+0 | 12 | 0 | 0 | 0 | 12 | 1
| 4 | LOC-2/1 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 5 | AP-3/0 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 6 | AP-4/0 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 7 | LOC-4/1 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 8 | AP-5/0 | OB+0 | 12 | 0 | 0 | 0 | 12 | 1
| 9 | LOC-5/1 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 10 | LOC-5/2 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 11 | AP-6/0 | OB+6 | 6 | 6 | 0 | 0 | 12 | 1
| 12 | AP-7/0 | OB+6 | 0 | 12 | 0 | 0 | 12 | 1
| 13 | AP-8/0 | OB+3 | 6 | 6 | 0 | 0 | 12 | 1
| 14 | LOC-8/1 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 15 | LOC-8/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 16 | LOC-8/3 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 17 | LOC-8/4 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 18 | LOC-8/5 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 19 | AP-9/0 | OC+6 | 6 | 6 | 0 | 0 | 12 | 1
| 20 | LOC-9/1 | OB+6 | 6 | 6 | 0 | 0 | 12 | 1
| 21 | LOC-9/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 22 | LOC-9/3 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 23 | LOC-9/4 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 24 | AP-10/0 | OC+0 | 12 | 0 | 0 | 0 | 12 | 1
| 25 | LOC-10/1 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 26 | LOC-10/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 27 | LOC-10/3 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 28 | AP-11/0 | OC+6 | 12 | 0 | 0 | 0 | 12 | 1
| 29 | LOC-11/1 | OA+6 | 0 | 0 | 6 | 0 | 12 | 1
| 30 | LOC-11/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 31 | LOC-11/3 | OA+3 | 6 | 0 | 6 | 0 | 12 | 1
| 32 | LOC-11/4 | OA+3 | 6 | 0 | 6 | 0 | 12 | 1
| 33 | LOC-11/5 | OA+3 | 6 | 0 | 6 | 0 | 12 | 1
| 34 | LOC-11/6 | OB+0 | 12 | 0 | 0 | 0 | 12 | 1
| 35 | AP-12/0 | OC+3 | 12 | 0 | 0 | 0 | 12 | 1
| 36 | LOC-12/1 | OA+6 | 0 | 0 | 6 | 0 | 12 | 1
| 37 | LOC-12/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 38 | LOC-12/3 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 39 | LOC-12/4 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 40 | LOC-12/5 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 41 | LOC-12/6 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 42 | LOC-12/7 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 43 | LOC-12/8 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 44 | LOC-12/9 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 45 | AP-13/0 | OC+6 | 12 | 0 | 0 | 0 | 12 | 1
| 46 | AP-14/0 | OC+15 | 0 | 12 | 0 | 0 | 12 | 2
| 47 | AP-15/0 | OC+15 | 0 | 12 | 0 | 0 | 12 | 2
| 48 | AP-16/0 | OC+15 | 6 | 6 | 0 | 0 | 12 | 2
| 49 | AP-17/0 | OB+0 | 12 | 0 | 0 | 0 | 12 | 1
| 50 | LOC-17/1 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 51 | LOC-17/2 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 52 | LOC-17/3 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 53 | LOC-17/4 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 54 | LOC-17/5 | OA+6 | 0 | 0 | 6 | 0 | 12 | 1
| 55 | LOC-17/6 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 56 | AP-18/0 | OB+6 | 12 | 0 | 0 | 0 | 12 | 1
| 57 | LOC-18/1 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 58 | LOC-18/2 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 59 | LOC-18/3 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 60 | LOC-18/4 | OA+0 | 0 | 0 | 6 | 0 | 12 | 1
| 61 | AP-19/0 | OB+0 | 12 | 0 | 0 | 0 | 12 | 1
| 62 | LOC-19/1 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 63 | LOC-19/2 | OA+3 | 0 | 0 | 6 | 0 | 12 | 1
| 64 | AP-20/0 | OB+3 | 12 | 0 | 0 | 0 | 12 | 1
| 65 | AP-21/0 | OB+0 | 12 | 0 | 0 | 0 | 12 | 1
| 66 | AP-22/0 | OC+0 | 12 | 0 | 0 | 0 | 12 | 1
| 67 | GANTRY | GANTRY | 6 | 0 | 0 | 0 | 6 | 0
|  |  |  | 306 | 66 | 222 | 0 | 798 | 69

## 220KV UG SUPPLY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
A | 220 KV UG CABLING EQUIPMENTS / MATERIALS
SL. No. | DESCRIPTION OF ITEMS (SCHEDULE-2A)-(220KV UG CABLE LAYING ) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNIT OF MEASUREMENT | QTY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE FOR THE TENDER QUANTITY
1 | 2 | 3 | 4 | 5 | 6= (5x9%) | 7= (5x9%) | 8= (5+6+7) | 9= (8x4)
1 | Type tested EHV XLPE, Extruded (Seamless) / Seam welded Corrugated Power Copper conductor cable as per IEC60840 & IS7098 for the ( 220 KV class) as per TS
1 | Supply of 220 kV, 1 Core, 1000 mm² Copper, XLPE insulation (Extruded semi-conducting screen and Extruded (Seamless) / Seam welded corrugated Aluminium Sheath type) UG Cable [6+1 cable x 3.3=23.10kms] | Km | 23.1 | 18369800 | 1653282 | 1653282 | 21676364 | 500724008.4 | 151 cd | 23.1 | 23.1
2 | Supply of Straight through jointing kits heat shrinkable type suitable for 220 kV, 1Core, 1000 mm², copper UG Cable (Mandatory Spare- 3 nos.) | No | 24 | 386906 | 34821.54 | 34821.54 | 456549.08 | 10957177.92 | As per Technical sanction 406, dated. 01.02.2025 of ED, CZ, BBSR(Diversion of 220kV Paradeep- Essar Line)
3 | Supply of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:2 Nos +Joints with Mid Points Bonding-1Nos ) | No | 3 | 386907 | 34821.63 | 34821.63 | 456550.26 | 1369650.78 | As per Technical sanction 406, dated. 01.02.2025 of ED, CZ, BBSR(Diversion of 220kV Paradeep- Essar Line)
4 | Supply of Outdoor terminating kit (oil filled, composite housed) suitable for 220 kV class, 1Core, 1000 mm² | No | 14 | 1086005.79 | 97740.5211 | 97740.5211 | 1281486.8322 | 17940815.6508 | cost data 24-25
5 | Supply of High Density Polyethylene (HDPE) pipe 200mm dia PE 80- PN8 for laying of 220kV UG cable | Km | 14 | 1470000 | 132300 | 132300 | 1734600 | 24284400 | As per Technical sanction 406, dated. 01.02.2025 of ED, CZ, BBSR(Diversion of 220kV Paradeep- Essar Line)
6 | Supply of Earthing materials 3 Mtr ,100mm ID Heavy gauge type pipe (with provision of with GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x10mm size | Nos. | 7 | 14050 | 1264.5 | 1264.5 | 16579 | 116053 | Rate considered from CPC W.O- 250(14), 14.03.2024
7 | Supply of 1 ph Link box with SVL with clamps and connectors with acessories | Nos. | 7 | 38675.29 | 3480.7761 | 3480.7761 | 45636.8422 | 319457.8954 | cd 146
8 | Supply of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 7 | 38675.29 | 3480.7761 | 3480.7761 | 45636.8422 | 319457.8954 | cd 146
9 | Supply of 3 ph Link box with SVL with clamps and connectors with acessories | Nos. | 2 | 47140 | 4242.6 | 4242.6 | 55625.2 | 111250.4 | Rate considered from CPC W.O- 250(14), 14.03.2024
10 | Supply of Single core, 300 sqmm XLPE bonding cable | Mtr | 200 | 2575.63 | 231.8067 | 231.8067 | 3039.2434 | 607848.68 | cd 144
11 | Supply of GI structure for outdoor end termination including of foundation bolts, nuts and template for line side & GSS side. | MT | 5 | 140183.05 | 12616.4745 | 12616.4745 | 165415.999 | 827079.995 | cd 150
12 | Supply of 48 core fibre optic cables single mode, duct type, fibre armoured with duct pipe, laid along 220kV UG cable.
12.1 | Supply of 48 core fibre optic cables single mode, duct type, fibre armoured laid along 220kV UG cable. | kM | 3.3 | 127089.72 | 11438.0748 | 11438.0748 | 149965.8696 | 494887.3697 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
12.2 | Supply of HDPE PLB duct of size 32/26mm for laying of OFC Cables. | kM | 3.3 | 58722 | 5284.98 | 5284.98 | 69291.96 | 228663.468 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
12.3 | Supply of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Set | 2 | 5142 | 462.78 | 462.78 | 6067.56 | 12135.12 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
12.4 | Supply of end Connectors and acessories for OFC connection at GRID subststions | Set | 2 | 7958 | 716.22 | 716.22 | 9390.44 | 18780.88 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
13 | Design with supply of all materials for modification of UR+6 type D/C tower with cable termination arrangement with cable tray ladder with supply of UR type tower for complete work like fabrication, welding etc. | MT | 25 | 140183.05 | 12616.4745 | 12616.4745 | 165415.999 | 4135399.975 | cd 150
14 | Supply of Clamps and Connectors suitable for connection to the OET,SA and Overhead conductor, Clamps for OET for the overhead conductor | LS | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | market rate
15 | Total wt of nut and bolts for above tower | MT | 1 | 102000 | 9180 | 9180 | 120360 | 120360 | Structure rc 4.0
16 | Earthing device (pipe eathing) | NOS | 10 | 2280.98 | 205.2882 | 205.2882 | 2691.5564 | 26915.564 | cd line 8
17 | Number plate | NOS | 1 | 129.38 | 11.6442 | 11.6442 | 152.6684 | 152.6684 | 10
18 | Danger plate | NOS | 1 | 236.77 | 21.3093 | 21.3093 | 279.3886 | 279.3886 | 9
19 | Phase plate | NOS | 6 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 714.5136 | 11
20 | Circuit plate | NOS | 2 | 100.92 | 9.0828 | 9.0828 | 119.0856 | 238.1712 | 12
21 | Anticlimbing devices/sets | sets | 1 | 4400.23 | 396.0207 | 396.0207 | 5192.2714 | 5192.2714 | 13
22 | 1200mm width cable tray with angle | MTR | 200 | 4500 | 405 | 405 | 5310 | 1062000
A | TOTAL OF SUPPLY COMPONENT OF THE WORKS CONTRACT FOR 220 KV UG CABLE LAYING | [6 empty] | 563800920.0065

## 220KV UG ERE
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
PART -II | DESCRIPTION OF ITEMS
B | ERECTION, INSTALLATION, TESTING & COMMISSIONING OF 220KV UG CABLE
SL. No. | DESCRIPTION OF ITEMS(SCHEDULE-2B-Laying of 220KV UG CABLE LAYING ) ERECTION, INSTALLATION, TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT OF MEASUREMENT | Qty | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL PRICE PER UNIT ( In Rs) | TOTAL PRICE ( In Rs)
1 | 2 | 3 | 4 | 5 | 6= (5x9%) | 7= (5x9%) | 8= (5+6+7) | 9= (8x4)
1 | Erection, Comissioning & Testing of 220kV, 1 Core,2x3-Runs with one spare, 1000 mm² Copper, Extruded (Seamless) / Seam welded Corrugated Aluminium Sheath XLPE insulation UG Cable
1.1 | Laying , Comissioning & Testing of 220kV, 1 Core,2x3-Runs with one spare, 1000mm² Copper, Extruded (Seamless) / Seam welded Corrugated Aluminium SheathXLPE insulation UG Cable by open treanch method in trefoil formation (2X3 in trefoil formation +one spare) in Direct buried or as per instruction of Engg in Charge [7nos cable run] | RKM | 0.5 | 1130365.25 | 101732.8725 | 101732.8725 | 1333830.995 | 666915.4975 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
1.3 | Laying , Comissioning & Testing of 220kV, 1 Core,2x3-Runs with one spare, 1000 mm² Copper, Extruded (Seamless) / Seam welded Corrugated XLPE insulation UG Cable by HDD method with 200 mm dia PE 80- PN8, HDPE pipe for laying of individual run of UG cable at Main Road /Drain crossing / Railway Crossing/unaccessible place as per instruction of Engg in Charge. [7nos cable to be laid per RKM] | RKM | 2.8 | 10550085 | 949507.65 | 949507.65 | 12449100.3 | 34857480.84 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
1.5 | Laying, Testing & Comissioning of 220kV, 1 Core,7-Runs, 1000 mm² Copper, XLPE insulation UG Cable for Sneking,Bending, looping and raising at both the termination end | RKM | 0.2 | 645923 | 51511.95 | 51511.95 | 675378.9 | 135075.78 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
2 | Erection,Commissioning & Tesing of Straight through jointing kits heat shrikable type suitable for 220kV, 1Core, 1000mm², copper UG Cable | No | 21 | 43941 | 3954.69 | 3954.69 | 51850.38 | 1088857.98 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
3 | Erection,Commissioning & Tesing of Shield break type Straight through jointing kits Heat Shrink /cold shrink /premoulded type suitable for 220 kV, 1 Core, 1000 mm², copper UG Cable and Link box connection with Single Core Bonding cables as per approved bonding calculation.(Cross Bonded Joint:2 Nos +Joints with Mid Points Bonding-1Nos ) | No | 3 | 43941 | 3954.69 | 3954.69 | 51850.38 | 155551.14 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
4 | Erection,Commissioning & Tesing of Outdoor terminating kit heat shrikable type suitable for 220 kV class, 1Core, 1000mm², copper UG Cable connection of 300sqmm bonding cable | No | 14 | 64126 | 5771.34 | 5771.34 | 75668.68 | 1059361.52 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
5 | Erection of Earthing materials 3 Mtr ,100mm ID Heavy gauge type pipe with GI clamp fixtures welded allaround the pipe and connecting separately to main equipment for grounding (Single Electrode with accessories) with GI Flat 75x6mm size , as per approved drawing & specifications | Nos. | 10 | 8881 | 799.29 | 799.29 | 10479.58 | 104795.8 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
6 | Erection, Comissioning & Testing of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 7 | 7631.3999 | 686.826 | 686.826 | 9005.0519 | 63035.3635 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
7 | Erection, Comissioning & Testing of 1 ph Link box without SVL with clamps and connectors with acessories | Nos. | 7 | 9539.2499 | 858.5325 | 858.5325 | 11256.3149 | 78794.2044 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
8 | Erection, Comissioning & Testing of 3 ph Link box with SVL with clamps and connectors with acessories | Nos. | 2 | 9539.2499 | 858.5325 | 858.5325 | 11256.3149 | 22512.6298 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
9 | Erection, Comissioning & Testing of Single core, 300 sqmm XLPE bonding cable | Mtr | 200 | 80 | 7.2 | 7.2 | 94.4 | 18880 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
10 | Erection of of GI structure for outdoor end termination including of foundation bolts, nuts and template for line side & GSS side. | MT | 5 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 43578.226 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
11 | Laying of 48 core fibre optic cables single mode, duct type, fibre armoured with duct pipe, laid along 220kV UG cable laying by open treanch method & HDD method . | [7 empty] | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
11.1 | Laying of 48 core single mode fibre optic cables with HDPE PLB duct of size 32/26mm and connectors , laid along 220kV UG cable through open trench method. | Km | 3.3 | 40370 | 3633.3 | 3633.3 | 47636.6 | 157200.78 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
11.2 | Laying of 48 Core single mode Fibre Optic Cables with Duct pipe of size 32/26mm and connectors through HDD method laid along 220kV UG Cable in main road crossing and Railway crossing | Km | 3.3 | 161480 | 14533.2 | 14533.2 | 190546.4 | 628803.12 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
11.3 | Erection of straight through Connectors (Plastic Coupler) and acessories for OFC connection | Sets | 2 | 4709 | 423.81 | 423.81 | 5556.62 | 11113.24 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
11.4 | Erection of end Connectors and acessories for OFC connection at GRID subststions | Sets | 2 | 4709 | 423.81 | 423.81 | 5556.62 | 11113.24 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
12 | Erection of tower super-structure complete with tightening,checking and punching of bolts including step-bolts. | MT | 26 | 7386.14 | 664.7526 | 664.7526 | 8715.6452 | 226606.7752 | Rate considered from CPC W.O- 250(14), 14.03.2024 samanghara-Puri UG cable
13 | Fixing of Number plate | NO | 1 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 188.1746 | RATE 11.00
14 | Fixing Danger plate | NO | 1 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 188.1746 | RATE 11.01
15 | fixing of Phase plate | NO | 6 | 159.47 | 14.3523 | 14.3523 | 188.1746 | 1129.0476 | RATE 11.02
16 | Fixing of Anti climbing device | Sets | 1 | 3441.28 | 309.7152 | 309.7152 | 4060.7104 | 4060.7104 | RATE 11.08
17 | Earthing with chamber (Pipe earthing including cost of bentonate in accordance with IS:3043-1966 with supply of all T&P. | Sets | 2 | 3071.77 | 276.4593 | 276.4593 | 3624.6886 | 7249.3772 | RATE 11.04
18 | Erection of 1200mm width cable tray with angle | MTR | 200 | 250 | 22.5 | 22.5 | 295 | 59000
B | TOTAL OF ERECTION COMPONENT OF THE WORKS CONTRACT FOR LAYING OF 220 KV UG CABLE | [6 empty] | 39401491.6208

## 220KV UG CVL
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Supply, Erection and Commissioning of 220 KV DC Transmission line from Existing 220/132/33KV GSS, Balasore to Proposed 400/ 220KV GSS at Baisinga (Approx Line Length = 11.50 KMs + 3.30KMS 220KV UG cable) [SCOPE OF WORKS:- OA+0 =15NOS, OA+3=04NOS, OA+6=05NOS, OB+0=05NOs, OB+3=01NO, OC+0=4NOS, OC+3=0NO, OC+6=04NOS, OC+15=03NOS, UR+6=01NOS, PC+0=02NOS (132KV Tower) & MC+0 =03NOS (for 132KV lines), TOTAL =47NOS TOWER & 11.50KMS+3.3KMS 220KV UG cable & 07nos 132KV tower to be Dismantled inside 220/132/33KV GSS, Balasore] along with 2 nos. 220KV feeder bay extension at 220/132/33KV substation, Balasore on “EPC/Turnkey CONTRACT BASIS”.
C | CIVIL WORKS FOR 220KV UG CABLING
SL. No. | DESCRIPTION OF ITEMS(SCHEDULE-VIIC-Laying of 220KV UG CABLE LAYING ) CIVIL WORK COMPONENT OF THE WORKS CONTRACT OF FOLLOWING EQUIPMENTS (As per Technical Specification) | UNIT OF MEASUREMENT | QTY | BASIC PRICE PER UNIT (Taxable Value) In Rs | CGST @ 9% PER UNIT (INTRA-STATE) | OGST @ 9% PER UNIT (INTRA-STATE) | TOTAL UNIT PRICE ( In Rs) | TOTAL PRICE FOR THE TENDER QUANTITY ( In Rs)
1 | 2 | 3 | 4 | 5 | 6= (5x9%) | 7= (5x9%) | 8= (5+6+7) | 9= (8x4)
CIVIL Works with supply of all materials like Cement, MS tor rod, Brick, Coarse & Fine Agregrates & Labour,T&P etc For RCC Slabs & Others (PART-B)
1 | Open trench (direct burried) for laying of 220kV cables Width : 1000mm Depth : 1850mm
1.1 | Earth work excavation of soil- This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Trench Dimension : (1mtr w x 1.85mtr d) | Cum | 925 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 400078.41 | rc line 2.ii
1.2 | Filling with fine river sand after laying of Cable inside the trench | Cum | 150 | 921.19 | 82.9071 | 82.9071 | 1087.0042 | 163050.63 | 7.1.ii
2 | Supply and erection of prefabricated RCC partition slab 950x450x75mm (M-20 grade) | Cum | 35.625 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 382697.6295 | 6.4
3 | Supply of rod, bending ,cutting and binding for prefabricated RCC slabs | MT | 3 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 226504.8468 | 6.5
4 | Breaking of all types of roads e.g.Asphalt/Tar/concrete road, concrete footpaths & other utilities (1mtr width) with disposal of same (if any debris) for laying of cable in open trench. | CUM | 100 | 4152.24 | 373.7016 | 373.7016 | 4899.6432 | 489964.32 | 6.6
5 | Reconstructing of Asphalt/Tar road & other utilities to bring its origional shape after laying of cable in open trench (2mtr width) Asphalt : 25 - 50 mm Binder course : 50 - 100 mm Base course : 100 - 300 mm Subgrade : 100 - 300 mm Compacted Subgrade : 150 - 300 mm | Km | 0.1 | 4037023 | 363332.07 | 363332.07 | 4763687.14 | 476368.714 | Rate considered from CPC W.O- 250(14), 14.03.2024
6 | Reconstructing of Concrete road / Concrete Footpath & other utilities to bring its origional shape after laying of cable in open trench (1mtr width) | Km | 0.1 | 2691349 | 242221.41 | 242221.41 | 3175791.82 | 317579.182 | Rate considered from CPC W.O- 250(14), 14.03.2025
7 | Supply of all materials and Erection of 220KV Jointing Bays (2mtrx14Mtr) along trench for straght through joints with RCC protection slab of 150mm thick. With Civil materials like bricks ,cements,sand,Materials for temporary shed,Airconditioners etc | Nos | 6 | 161480 | 14533.2 | 14533.2 | 190546.4 | 1143278.4 | Rate considered from CPC W.O- 250(14), 14.03.2026
8 | Supply and erection of Route Marker along the Cable Routes at an interval of 30 Mtrs as per the drawing with civil works. | No | 110 | 1345 | 121.05 | 121.05 | 1587.1 | 174581 | Rate considered from CPC W.O- 250(14), 14.03.2027
9 | Prefabricated RCC Foundation for 220kV Link Box including supply of all materials | Nos. | 30 | 26913 | 2422.17 | 2422.17 | 31757.34 | 952720.2 | Rate considered from CPC W.O- 250(14), 14.03.2028
10 | Making of earth chamber including excavation, soil treatment with Bentonite powder, supply of charcoal, etc with brick masonary (1:5), PCC (1:4:8) and with RCC cover slab size of the pit 450mmX450mm X600 mm depth as per direction of Engineer in Charge. | Nos | 10 | 740 | 66.6 | 66.6 | 873.2 | 8732 | Rate considered from CPC W.O- 250(14), 14.03.2029
11 | Detailed survey- For ascertaining feasible route,identifying the utilities over the ground, preparation of the detailed marking on topo sheet , preparation of route alignment map, submission of profile and survey report and interaction with the utilities & Govt. bodies for obtaining necessary clearances for laying of cables. (for Final Route only) Survey to be done by making ground penetration method survey. | Kms | 3.3 | 40370 | 3633.3 | 3633.3 | 47636.6 | 157200.78 | Rate considered from CPC W.O- 250(14), 14.03.2030
12 | Soft /loose soil-In first depth[up to 1.5 mtr]-Excavation and back filling: for foundation of equipment and column including supply of all materials, Labour and T& P and as per the instruction of Engineer In charge per Cum | CUM | 50 | 233.97 | 21.0573 | 21.0573 | 276.0846 | 13804.23 | RC-SS-2
13 | Hard / Dense soil-In first depth[up to 1.5 mtr]-Excavation and back filling: for foundation of equipment and column including supply of all materials, Labour and T& P and as per the instruction of Engineer In charge per Cum | CUM | 50 | 366.54 | 32.9886 | 32.9886 | 432.5172 | 21625.86 | RC-SS-2
14 | PCC (1:3:6) | CUM | 5 | 6377.44 | 573.9696 | 573.9696 | 7525.3792 | 37626.896 | RC-SS-3
15 | RCC(1:1.5:3) | CUM | 52 | 9103.72 | 819.3348 | 819.3348 | 10742.3896 | 558604.2592 | RC-SS-3
16 | Cutting, bending, hooking, fixing and binding in poisition of MS barsfor reinforcement of foundation concrete of substation equipment/columnsetc. including supply of wire for binding with supply of steelrod(TATA/RINL/SAIL/JINDAL Make) and head loading. No other make of steelshall be allowed. | MT | 2 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 151003.2312 | RC-SS-5
17 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing ( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick Masonry work with ratio mortar (cement and sand)1:5 and cement pointing of the joints, for the fencing upto a height of 350 mm from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | RMTRS | 80 | 2240 | 201.6 | 201.6 | 2643.2 | 211456 | NEULAPOI 18
18 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:3:6 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 30 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 214473.024 | RC SS 3.20-i
19 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 40 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 156527.472 | RC SS 5.10
C | TOTAL OF CIVIL COMPONENT OF THE WORKS CONTRACT FOR 220 KV CABLE LAYING | [6 empty] | 6257877.0847
Note on E25: Author: 400kv

## FDN (hidden)
Tower Type | Nos. of Towers | Excavation | Excavation Total | Template Including NBs | Stub Including NBs | Total Wt. Stub Fitting(In kg.) | Total Wt. Stub Fitting(In MT) | Lean(PCC) | Total PCC | Concrete(RCC) | Total RCC | Steel(In MT) | Total Steel | Shoring | Total Shoring | Welding | Total Welding
PA+0 | 0 | 63.36 | 0 | 644.155 | 252.97 | 897.125 | 0 | 0.968 | 0 | 8.76 | 0 |  | 0 | 98.56 | 0 | 734 | 0
PA+3 | 0 | 70 | 0 | 644.155 | 252.97 | 897.125 | 0 | 1.936 | 0 | 9.72 | 0 |  | 0 | 98.56 | 0 | 1101 | 0
PA+6 | 0 | 70 | 0 | 644.155 | 252.97 | 897.125 | 0 | 1.936 | 0 | 9.72 | 0 |  | 0 | 98.56 | 0 | 1450 | 0
PB+0 | 0 | 104.43 | 0 | 613.46 | 433.55 | 1047.01 | 0 | 1.51 | 0 | 15.49 | 0 |  | 0 | 134.2 | 0 | 830 | 0
PB+3 | 0 | 113.49 | 0 | 613.46 | 433.55 | 1047.01 | 0 | 3.025 | 0 | 17 | 0 |  | 0 | 134.2 | 0 | 1410 | 0
PB+6 | 0 | 113.49 | 0 | 613.46 | 433.55 | 1047.01 | 0 | 3.025 | 0 | 17 | 0 |  | 0 | 134.2 | 0 | 1981 | 0
PC+0 | 2 | 141.54 | 283.08 | 903.29 | 610.22 | 1513.51 | 3.027 | 1.74 | 3.48 | 20.64 | 41.28 |  | 0 | 158.12 | 316.24 | 1185 | 2370
PC+3 | 0 | 141.54 | 0 | 903.29 | 610.22 | 1513.51 | 0 | 3.481 | 0 | 20.64 | 0 |  | 0 | 158.12 | 0 | 1853 | 0
PC+6 | 0 | 14.54 | 0 | 903.29 | 610.22 | 1513.51 | 0 | 3.481 | 0 | 20.64 | 0 |  | 0 | 158.12 | 0 | 2458 | 0
OA+0 | 15 | 64.512 | 967.68 | 579 | 231.44 | 810.44 | 12.1566 | 0.882 | 13.23 | 8.796 | 131.94 | 0.24 | 3.6 | 112 | 1680 | 839 | 12585 | 240
OA+3 | 4 | 71.25 | 285 | 579 | 231.44 | 810.44 | 3.2418 | 1.25 | 5 | 9.764 | 39.056 | 0.24 | 0.96 | 112 | 448 | 1025 | 4100 | 240
OA+6 | 5 | 71.25 | 356.25 | 579 | 231.44 | 810.44 | 4.0522 | 1.25 | 6.25 | 9.764 | 48.82 | 0.24 | 1.2 | 112 | 560 | 1085 | 5425 | 240
0
OB+0 | 5 | 119.16 | 595.8 | 667 | 437.31 | 1104.31 | 5.5215 | 1.568 | 7.84 | 17.9 | 89.5 | 0.389 | 1.945 | 400 | 2000 | 926 | 4630 | 389
OB+3 | 1 | 129.02 | 129.02 | 667 | 437.31 | 1104.31 | 1.1043 | 1.68 | 1.68 | 19.59 | 19.59 | 0.389 | 0.389 | 166.16 | 166.16 | 2092 | 2092 | 389
OB+6 | 0 | 129.02 | 0 | 667 | 437.31 | 1104.31 | 0 | 1.68 | 0 | 19.59 | 0 | 0.389 | 0 | 166.16 | 0 | 1314 | 0 | 389
0
OC+0 | 4 | 212.94 | 851.76 | 986 | 777.384 | 1763.384 | 7.0535 | 2.592 | 10.368 | 35.397 | 141.588 | 0.44 | 1.76 | 400 | 1600 | 1332 | 5328 | 440
OC+3 | 0 | 212.94 | 0 | 986 | 778.384 | 1764.384 | 0 | 2.592 | 0 | 35.397 | 0 | 0.44 | 0 | 400 | 0 | 1588 | 0 | 440
OC+6 | 4 | 212.94 | 851.76 | 986 | 779.384 | 1765.384 | 7.0615 | 2.592 | 10.368 | 35.397 | 141.588 | 0.44 | 1.76 | 400 | 1600 | 1750 | 7000 | 440
OC+15 | 3 | 322.56 | 967.68 | 2074 | 1071.92 | 3145.92 | 9.4378 | 8.1 | 24.3 | 30.188 | 90.564 | 2.5 | 7.5 | 252 | 756 | 1090 | 3270 | 2500
OC+24 | 0 | 439.04 | 0 | 2074 | 1071.92 | 3145.92 | 0 | 11.24 | 0 | 49.2 | 0 | 3.22 | 0 | 322.24 | 0 | 1760 | 0 | 3220
0
UR+0 | 0 | 216.75 | 0 | 1476 | 696.98 | 2172.98 | 0 | 3.445 | 0 | 52.104 | 0 | 0.526 | 0 | 204 | 0 | 1578 | 0 | 526
UR+6 | 1 | 216.75 | 216.75 | 1476 | 696.98 | 2172.98 | 2.173 | 3.445 | 3.445 | 52.104 | 52.104 | 0.526 | 0.526 | 204 | 204 | 2166 | 2166 | 526
0
MA+0 | 0 | 424 | 0 | 1057.06 | 881.66 | 1938.72 | 0 | 10.82 | 0 | 54.47 | 0 | 3.94 | 0 | 600 | 0 | 3288 | 0 | 3940
MA+3 | 0 | 424 | 0 | 1057.06 | 881.66 | 1938.72 | 0 | 10.82 | 0 | 54.47 | 0 | 3.94 | 0 | 600 | 0 | 1200 | 0 | 3940
MA+6 | 0 | 424 | 0 | 1057.06 | 881.66 | 1938.72 | 0 | 10.82 | 0 | 54.47 | 0 | 3.94 | 0 | 600 | 0 | 1200 | 0 | 3940
0
MB+0 | 0 | 746 | 0 | 1205.13 | 1327.04 | 2532.17 | 0 | 19.6 | 0 | 111.34 | 0 | 7.76 | 0 | 600 | 0 | 4936 | 0 | 7760
MB+3 | 0 | 746 | 0 | 1205.13 | 1327.04 | 2532.17 | 0 | 19.6 | 0 | 111.34 | 0 | 7.76 | 0 | 408.8 | 0 | 1600 | 0 | 7760
MB+6 | 0 | 746 | 0 | 1205.13 | 1327.04 | 2532.17 | 0 | 19.6 | 0 | 111.34 | 0 | 7.76 | 0 | 408.8 | 0 | 1600 | 0 | 7760
0
MC+0 | 3 | 907 | 2721 | 1344.9 | 2126.54 | 3471.44 | 10.4143 | 24.03 | 72.09 | 137.74 | 413.22 | 9.19 | 27.57 | 600 | 1800 | 4792 | 14376 | 9190
MC+3 | 0 | 907 | 0 | 1344.9 | 2126.54 | 3471.44 | 0 | 24.03 | 0 | 137.74 | 0 | 9.19 | 0 | 600 | 0 | 1600 | 0 | 9190
MC+6 | 0 | 907 | 0 | 1344.9 | 2126.54 | 3471.44 | 0 | 24.03 | 0 | 137.74 | 0 | 9.19 | 0 | 600 | 0 | 1600 | 0 | 9190
MC+9 | 0 |  | 0 | 1344.9 | 2126.54 | 3471.44 | 0 | 25.03 | 0 | 138.74 | 0 | 10.19 | 0 | 601 | 0 | 1601 | 0 | 10190
0
MONOPOLE | 0 | 350 | 0 |  |  |  |  | 3.5 | 0 | 30 | 0 | 2.5 | 0 | 603 | 0 | 300 | 0 | 2500
|  |  | 8225.78 |  |  |  | 65.2436 |  | 158.051 |  | 1209.25 |  | 47.21 |  | 11130.4 |  | 63342
|  | with 110% | 9048.358 |  |  |  | 120% |  | 189.6612 |  | 1451.1 |  | 56.652
|  | Round up | 9050 |  |  |  |  | Round up | 190 |  | 1460 |  | 60
Soft/Loose soil | 20% | 1810 | [5 empty] | Pilling | 30 |  | 140 |  | 20
Dense/Compact soil | 30% | 2715 | [6 empty] | 220 |  | 1600 |  | 80
Soft/Disintegrated rock(Not requiring Blasting) | 20% | 1810
Hard Rock(Requiring Blasting/Using breaker machinery) | 10% | 905
Fully submerged soil | 10% | 905
Partial Submerged soil | 10% | 905
| 100% | 9050
|  |  | 469 | 622
|  |  | 938 | 1116
|  |  | 566 | 1256
|  |  | 375 | 1085
|  |  | 550 | 779
|  |  | 360 | 437
|  |  | 324 | 569
|  |  | 168 | 175
|  |  | 64 | 1248
|  |  | 22 | 151
|  |  | 6 | 7438
2
24
100
80
112
128
504

## Tower Mat (hidden)
220KV RAMAKRUSHNAPUR-BHDRAK DC LINE (Structure Supply/Erection/Electrical Work Details)
Sl.No. | Description Of Items |  | Unit | Stub, Template & Super Structure Erection/Electrical Work |  |  | N&B's Of Stub, Template & Super Structure Erection/Electrical Work
|  |  |  | 220KV DC LINE | Unit Wt. In KG As Per OPTCL BOM | Total Wt. In KG As Per OPTCL BOM | Qty. | Unit Wt. In KG As Per OPTCL BOM | Total Wt. In KG As Per OPTCL BOM
1 | 2 |  | 3 | 4 | 5 | 6=4x5 | 7 | 8 | 9=7x8
[A] | Stub & Structure
1 | OA+0-Type Tower | Stub Only | Nos | 31 | 231.8 | 7185.8 | 31 | 1.024 | 31.744
|  | Structure (W/O Stub) | Nos | 31 | 4309.91 | 133607.21 | 31 | 191.31 | 5930.61
2 | OA+3-Extension Portion Only |  | Nos | 19 | 759.64 | 14433.16 | 19 | 25.73 | 488.87
3 | OA+6-Extension Portion Only |  | Nos | 7 | 1512.88 | 10590.16 | 7 | 37.22 | 260.54
4 | OB+0-Type Tower | Stub Only | Nos | 1 | 437.72 | 437.72 | 1 | 1.088 | 1.088
|  | Structure (W/O Stub) | Nos | 1 | 6476.46 | 6476.46 | 1 | 224.38 | 224.38
5 | OB+3-Extension Portion Only |  | Nos | 0 | 1360.44 | 0 | 0 | 35.26 | 0
6 | OB+6-Extension Portion Only |  | Nos | 0 | 2244.56 | 0 | 0 | 58.1 | 0
7 | OC+0-Type Tower | Stub Only | Nos | 8 | 770.56 | 6164.48 | 8 | 3.456 | 27.648
|  | Structure (W/O Stub) | Nos | 16 | 9257.67 | 148122.72 | 16 | 322.92 | 5166.72
8 | OC+3-Extension Portion Only |  | Nos | 1 | 1489.84 | 1489.84 | 1 | 39.5 | 39.5
9 | OC+6-Extension Portion Only |  | Nos | 3 | 2728.52 | 8185.56 | 3 | 63.53 | 190.59
10 | OC+15-Type Tower | Stub Only | Nos | 8 | 1067.28 | 8538.24 | 8 | 4.864 | 38.912
|  | Structure (W/O Stub) | Nos | 8 | 8743.32 | 69946.56 | 8 | 180.756 | 1446.048
11 | UR+0-Type Tower | Stub Only | Nos | 2 | 692.21 | 1384.42 | 2 | 10.33 | 20.66
|  | Structure (W/O Stub) | Nos | 2 | 11887.29 | 23774.58 | 2 | 394.271 | 788.542
12 | UR+6-Extension Portion Only |  | Nos | 2 | 4148.45 | 8296.9 | 2 | 93.36 | 186.72
| PC+0-Type Tower | Stub Only
Structure (W/O Stub)
| MC+0-Type Tower | Stub Only
Structure (W/O Stub)
13 | Sub-Total Weight Of Stub, Structure & Extension including N&B's |  | MT |  |  | 448.6338 |  |  | 14.8426
14 | Total Weight Of Stub, Structure & Extension including N&B's |  | MT | 463.4764
| MULTICIRCUIT TOWER |  |  | MS Total | N&B's Of Stub, Template & Super Structure Unit Wt. In KG
| MA | Set | 1 | #REF! | 450.3 | 450.3
| +3 EXTENSION | Set | 0 | #REF! |  | 0
| +6 EXTENSION | Set | 0 | #REF! |  | 0
| MB | Set | 0 | #REF! |  | 0
| +3 EXTENSION | Set | 0 | #REF! |  | 0
| +6 EXTENSION | Set | 0 | #REF! |  | 0
| MC | Set | 3 | #REF! | 553 | 1659
| +3 EXTENSION | Set | 2 | #REF! | 116.1 | 232.2
| +6 EXTENSION | Set | 0 | #REF! |  | 0
| +9 EXTENSION | Set | 0 |  |  | 0
| +15 EXTENSION | Set | 0 |  |  | 0
|  |  |  | #REF! |  | 2341.5
|  |  |  | #REF! |  | 2.3415