## Sheet4 (2) (hidden)
Tower Type | Nos. of Towers | Excavation | Excavation Total | Template Including NBs | Total Wt. Stub Fitting(In MT) | Lean(PCC) | Total PCC | Concrete(RCC) | Total RCC | Steel(In MT) | Total Steel | Shoring | Total Shoring | Welding | Total Welding | N&B in kg
DA+0 (wet) | 250 | 165.169 | 41292.25 | 2.54 | 635 | 2.328 | 582 | 16.322 | 4080.5 | 1.472 | 368 | 0 | 0 | 2200 | 550000 | 628.182 | 940.182
DA+3 , +6 (PS) | 62 | 223.949 | 13884.838 | 2.54 | 157.48 | 3.232 | 200.384 | 24.453 | 1516.086 | 1.845 | 114.39 | 200 | 12400 | 2800 | 173600 | 149.438 | 16438.18
DB+0 (Wet) | 19 | 312.122 | 5930.318 | 2.654 | 50.426 | 4.068 | 77.292 | 39.138 | 743.622 | 3.587 | 68.153 | 0 | 0 | 2615 | 49685 | 585.728 | 26357.76
DB+3, +6, +9 (PS) | 26 | 426.264 | 11082.864 | 2.654 | 69.004 | 6.407 | 166.582 | 51.897 | 1349.322 | 5.285 | 137.41 | 200 | 5200 | 5655 | 147030 | 171.602 | 4461.652
DC+0 (Wet) | 17 | 413.487 | 7029.279 | 2.654 | 45.118 | 6.205 | 105.485 | 53.645 | 911.965 | 5.437 | 92.429 | 0 | 0 | 3084 | 52428 | 1260.126 | 47884.788
DC+3, +6 (PS) | 19 | 522.728 | 9931.832 | 2.654 | 50.426 | 7.938 | 150.822 | 66.371 | 1261.049 | 7.044 | 133.836 | 200 | 3800 | 3431 | 65189 | 196.792 | 3739.048
DC+18 (wet) | 2 | 523.728 | 1047.456 | 3.654 | 7.308 | 8.938 | 17.876 | 67.371 | 134.742 | 8.044 | 16.088 | 0 | 0 | 3431 | 6862 | 196.792 | 393.584
DD+0 (Wet) | 17 | 532.275 | 9048.675 | 3.7 | 62.9 | 8.09 | 137.53 | 82.062 | 1395.054 | 6.662 | 113.254 | 0 | 0 | 4385 | 74545 | 1154.346 | 114280.254
DD+3, +6,+9 (PS) | 49 | 676.814 | 33163.886 | 3.7 | 181.3 | 10.397 | 509.453 | 102.513 | 5023.137 | 8.73 | 427.77 | 200 | 9800 | 4933 | 241717 | 441.498 | 21633.402
DD+18, +25 (Wet) | 33 | 657.12 | 21684.96 | 4.746 | 156.618 | 10.082 | 332.706 | 130.177 | 4295.841 | 7.094 | 234.102 | 0 | 0 | 8435 | 278355 | 1372.97 | 45308.01
|  |  | 154096.358 |  | 1415.58 |  | 2280.13 |  | 20711.318 |  | 1705.432 |  | 31200 |  | 1639411 |  | 281436.86
Soft/Loose soil | 30 | 154096.358 | 46228.9074 | [6 empty] | for Pile | 340 | MT |  |  |  |  | 281.4369
Dense/Compact soil | 30 | 154096.358 | 46228.9074 | [7 empty] | 2045 | [5 empty] | 337.7242
Soft/Disintegrated rock(Not requiring Blasting) | 10 | 154096.358 | 15409.6358
Hard Rock(Requiring Blasting/Using breaker machinery) | 10 | 154096.358 | 15409.6358
ps soil | 10 | 154096.358 | 15409.6358
fs soil | 10 | 154096.358 | 15409.6358
| 100 |  | 154096.358

## SUMMARY
SUMMARY
NAME OF THE WORK: Construction of 2x500 MVA ICTs, 02 Nos. of 80MVAR line reactors, 2no of 125MVAR bus reactor, 400/220KV AIS Grid Sub-Station With SAS at Balasore along with Tie (One and half breaker scheme) and 220Kv side with 02 Main Bus & 01 Transfer Bus System.
Sl. No. | Description | Amount (inRs.) | GSS | 400 | 220 | bay | total
1 | Total Cost of materials (a below) | 1866553245.2918 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
a | 400KV Substation cost with mandatory spares (Balasore GSS) | 1866553245.2918 | [5 empty] | #REF! | 198
2 | Stock,Storage & Insurance(@3% on Sl.No-1) | 55996597.3588 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | Sub-Total(1+2) | 1922549842.6506 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | Contigency 3% on Sl.No.3 | 57676495.2795 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | T&P cost @ 2% on Sl.No. 3 | 38450996.853 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | Transportation @5% on Sl.No.3 | 96127492.1325 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | Total Supply Cost Sub-Total (Sl. No.3 to Sl. No.6) | 2114804827 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | Total Electrical Erection cost (a below) | 66205869.803 | #REF! | #REF! | #REF! | #REF! |  | #REF!
a | 400KV Substation erection cost (Balasore GSS) | 66205869.803 | #REF! | #REF! | #REF! | #REF! |  | #REF!
9 | Total Civil work cost (below) | 435716747.5746 | [5 empty] | #REF!
a | 400KV Substation Civil works (Balasore GSS) | 435716747.5746 | [5 empty] | #REF!
10 | Sub-Total (Sl. No.7 + Sl. No.8 + Sl.no-9) | 2616727444.3776 | [5 empty] | #REF!
11 | Inspection fees (GSS) | 3000000 | [5 empty] | #REF!
12 | Statutory fees for forest clearance (Substation land i.e. Gramya Jungle of Ac 10.00dec to be aquired) | 50000000 | [5 empty] | #REF!
13 | TOTAL COST OF SUPPLY, ERECTION AND CIVIL | 2669727444.3776
|  |  | 0 | 2669727444.3776 |  |  |  | #REF!
| Or Say | 2669727444
(Rupees Two Hundred Sixty-Seven Crore Sixty-Nine Lakh Fifty-Eight Thousand Six Hundred Eighty-Three only)

## SS SUPPLY
ODISHA POWER TRANSMISSION CORPORATION LIMITED
#REF!
(Supply SUB-STATION) |  |  | 400/220kV Substation at Balasore 400 KV Bays-[10 Nos Bays (2 Fdr+ 2 ICT+ 4 Tie+2 Bus Reactor+2 Line Reactor+ 02 unequipped Spare for line FDR)] In 1 & 1/2 CB System, 220KV Bay-[10 Nos. bays (FDR-6,ICT-2, B/C-1, TB/C-1) & 02nos unequipped Spare Bays] In 02 Main Bus & 01 Transfer Bus System
Sl. No. | SUBSTATION EQUIPMENTS / MATERIALS |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS (SCHEDULE-VIIA-SS) SUPPLY OF FOLLOWING EQUIPMENT & MATERIALS (As per Technical Specification) | UNITS | QTY | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | TOTAL PRICE
[5 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=4X8
A | All Equipment shall have creepage @ 31mm/KV
1 | 420KV, 3000-2000-1000/1A, 63kA, 5 core Single Phase Current Transformer as per TS | NOS | 42 | 564583.56 | 50812.5204 | 50812.5204 | 666208.6008 | 27980761.2336 | SS-20 |  |  | 27980761.2336 | 0
2 | 420 KV, 3000A, 63 KA, HORIZONTAL DOUBLE END BREAK ISOLATORS WITH POST INSULATORS as per TS | [10 empty] | 0 | 0
2.1 | WITH ONE EARTH SWITCH | SET | 30 | 1136282.14 | 102265.3926 | 102265.3926 | 1340812.9252 | 40224387.756 | SS-9 |  |  | 40224387.756 | 0
2.2 | WITH TWO EARTH SWITCH | SET | 2 | 1136282.14 | 102265.3926 | 102265.3926 | 1340812.9252 | 2681625.8504 | SS-9 |  |  | 2681625.8504 | 0
3 | 420 KV, 63 kA, 3 Core Single Phase CVT | NOS | 12 | 231050.72 | 20794.5648 | 20794.5648 | 272639.8496 | 3271678.1952 | SS-33 |  |  | 3271678.1952 | 0
4 | 420KV, 3150A, 63KA,SF6 CIRCUIT BREAKER WITH SUPPORT STRUCTURE AND AS PER TS | [10 empty] | 0 | 0
4.1 | CIRCUIT BREAKER WITHOUT CSD | SET | 2 | 2725573.6 | 245301.624 | 245301.624 | 3216176.848 | 6432353.696 | SS-01 |  |  | 6432353.696 | 0
4.2 | CIRCUIT BREAKER WITH CSD | SET | 10 | 2725573.6 | 245301.624 | 245301.624 | 3216176.848 | 32161768.48 | SS-01 |  |  | 32161768.48 | 0
5 | 336KV Surge Arrester as per TS for 400KV System | NOS | 24 | 162131.12 | 14591.8008 | 14591.8008 | 191314.7216 | 4591553.3184 | SS-29 |  |  | 4591553.3184 | 0
6 | 420KV 1 phase Solid core bus post insulator (8 kN) (AIS) as per technical specification. | NOS | 212 | 67426.2162 | 6068.36 | 6068.36 | 79562.9362 | 16867342.47 | Badakushasthali SS 2.2 |  |  | 16867342.2446 | -0.22541
7 | 245 KV, 1200-600-300 A, 50 KA, 5 core Single Phase Current Transformer (4 Nos PX Class & 1 No. 0.2s Class) | NOS | 18 | 382298.97 | 34406.9073 | 34406.9073 | 451112.7846 | 8120030.1228 | SS-21 |  |  | 8120030.1228 | 0
8 | 245 KV, 3CORE, SINGLE PHASE VOLTAGE TRANSFORMER | NOS | 12 | 134349.71 | 12091.4739 | 12091.4739 | 158532.6578 | 1902391.8936 | SS-34 |  |  | 1902391.8936 | 0
9 | 245 KV, 2000A, 50KA, ISOLATORS WITH POST INSULATORS AS PER TS | [10 empty] | 0 | 0
9.1 | SINGLE ISOLATOR WITH OUT EARTH SWITCH | SET | 7 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 4928578.1216 | SS-05 |  |  | 4928578.1216 | 0
9.2 | TANDEM ISOLATOR WITH OUT EARTH SWITCH | SET | 10 | 596680.16 | 53701.2144 | 53701.2144 | 704082.5888 | 7040825.888 | SS-05 |  |  | 7040825.888 | 0
9.3 | SINGLE ISOLATOR WITH SINGLE EARTH SWITCH | SET | 6 | 775865.96 | 69827.9364 | 69827.9364 | 915521.8328 | 5493130.9968 | SS-06 |  |  | 5493130.9968 | 0
10 | 245KV, 3150A, 50KA, SF6 CIRCUIT BREAKER WITH SUPPORT STRUCTURE AND AS PER TS | SET | 6 | 1365681.73 | 122911.3557 | 122911.3557 | 1611504.4414 | 9669026.6484 | SS-2 |  |  | 9669026.6484 | 0
11 | 216KV Surge Arrester as per TS for 220KV System | NOS | 12 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 1012284.948 | SS-30 |  |  | 1012284.948 | 0
12 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 100 | 22505 | 2025.45 | 2025.45 | 26555.9 | 2655590 | Badakushasthali 5 |  |  | 2655590 | 0
13 | 132KV Circuit Breaker Single Pole for NGR with supporting structures | NOS | 2 | 190630.1333 | 17156.712 | 17156.712 | 224943.5573 | 449887.1147 | CD SS 3/3 |  |  | 449887.1147 | 0
14 | 145 KV CT (800-400-200/1-1-1) for NGR | NOS | 2 | 232701.42 | 20943.1278 | 20943.1278 | 274587.6756 | 549175.3512 | SS 24 |  |  | 549175.3512 | 0
15 | 120KV Surge Arrester as per TS for 132KV System | NOS | 2 | 29179.14 | 2626.1226 | 2626.1226 | 34431.3852 | 68862.7704 | CD SS 31 |  |  | 68862.7704 | 0
15A | 30KV Surge Arrester as per TS for 33KV System | NOS | 6 | 9416.38 | 847.47 | 847.47 | 11111.32 | 66667.92 | CD SS 32 |  |  | 66667.9704 | 0.0504
16 | 72.5 KV, 50-25 A / 1-1 A, 31.5KA for 1 sec, Single Phase Current Transformer as per technical specification | Nos. | 6 | 299439.85 | 26949.59 | 26949.59 | 353339.03 | 2120034.18 | Ramakrushnapur |  |  | 2120034.138 | -0.042
17 | 72.5kV, 400-200-100 A / 1-1-1-1 A, 31.5KA for 1 sec, Single Phase Current Transformer as per technical specification | Nos. | 6 | 68710.88 | 6183.98 | 6183.98 | 81078.84 | 486473.04 | Ramakrushnapur |  |  | 486473.0304 | -0.0096
17.1 | 72.5kV, 1250A, 31.5KA Single Isolator with Earth Switch. | Set | 2 | 301784.03 | 27160.56 | 27160.56 | 356105.15 | 712210.3 | Ramakrushnapur |  |  | 712210.3108 | 0.0108
17.2 | 72.5 KV, 33KV/√3/110V/√3, 2 CORE(3P,0.2), SINGLE PHASE IVT | Nos. | 6 | 132333.22 | 11909.99 | 11909.99 | 156153.2 | 936919.2 | Ramakrushnapur |  |  | 936919.1976 | -0.0024
17.3 | 72.5 KV, 1250A, 31.5kA for 3 sec, SF6 Circuit Breaker with supporting GI Structure as per technical specification | Set | 2 | 732150.14 | 65893.51 | 65893.51 | 863937.16 | 1727874.32 | Ramakrushnapur |  |  | 1727874.3304 | 0.0104
18 | 33KV BPI may be used | Nos. | 6 | 4187.84 | 376.91 | 376.91 | 4941.66 | 29649.96 | Amendment of Ersama |  |  | 29649.9072 | -0.0528
19 | Conductor Insulation: For use in insulation of ICT Tertiary - Station Transformer (2 SET) bare overhead Conductor. The insulating sleeve and insulation tape shall be Flame, Arc, UV & Ozone Resistant. Shall be rated for 33kV Class insulation. Shall be for outdoor use and shall be made of Silicone/EPR/Polyolefin compound. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | market rate | check if its needed |  | 118000 | 0
20 | BUS BAR & CIRCUIT MATERIALS | [10 empty] | 0 | 0
20.1 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT: 1. 400KV Bus-A & B and Equipment to Equipment connections are 120mm IPS Aluminium Pipe Bus and shall be for 6 nos of diameters (All "I" type). 2. Cross Bus shall be with Twin ACSR Moose for ICTs and Quad ACSR Moose for Lines and accordingly for the Cross bus to equipment. 3. Cross bus shall be strung for the spare diameters with Quad ACSR moose 3. 220KV Main Bus-I & II, Transfer Bus shall be with twin ACSR Moose (conductor spacing-300mm). 4. 220KV Equipment to Equipments connections shall be 114.2mm IPS Aluminium Tube/ACSR Moose (Twin/single) as per approved drawing. 5. 33/0.4KV Station transformer connections and equipment to equipment connection and ICT Tertiary shall be with ACSR Panther conductor. 6. The hardware fittings shall be of 160KN & 120KN for both 400KV & 220KV system. The UTS of the twin hardware fittings shall be 2x160KN or 2x120KN respectively. 10. The harware fittings shall be single anchored and without turn buckle. 11. This also includes any other hardware fittings and clamps required to complete the work. 12. The qty of hardware fittings, clamps & connectors, Conductor, IPS Aluminium tube and Insulators shall be as per the approved erection key diagram. | [10 empty] | 0 | 0
20.1.1 | All suspension & tension hardware fittings for 400KV system (Double tension for Twin Moose, Double Tension for Quad moose, Double Suspension for Quad/Twin moose) | LOT | 1 | 2500000 | 225000 | 225000 | 2950000 | 2950000 | Badakushasthali SS 12.1 |  |  | 2950000 | 0
20.1.2 | All suspension & tension hardware fittings for 220KV system for Twin ACSR Moose, Single ACSR Moose | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | Badakushasthali SS 12.2 |  |  | 2360000 | 0
20.1.3 | Clamps & Connectors, Spacers etc for Quad/Twin ACSR Moose, IPS Aluminium Tube for 400KV system | LOT | 1 | 2500000 | 225000 | 225000 | 2950000 | 2950000 | LS |  |  | 2950000 | 0
20.1.4 | Clamps & Connectors, Spacers etc for Twin ACSR Moose, Single ACSR Moose,IPS Aluminium Tube for 220KV system | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | LS |  |  | 2360000 | 0
20.1.5 | All Clamps, Connectors, Spacers etc required for 145 KV system | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | LS |  |  | 2360000 | 0
20.1.6 | All hardware fittings, Clamps, Connectors, Spacers etc required for 66/33KV system | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | market rate |  |  | 590000 | 0
21 | INSULATORS FOR SUBSTATION | [10 empty] | 0 | 0
21.1 | 160 kN Long Rod Insulator (Porcelain type Long rod) for 400 KV | SET | 300 | 12556.3258 | 1130.0693 | 1130.0693 | 14816.4645 | 4444939.3414 | BADAKUSHASTHALI 22 ( SANCTION ESTIMATE ON DATED 07.02.2025) |  |  | 4444939.3414 | 0
21.2 | 160 kN Long Rod Insulator (Porcelain type Long rod) for 220 KV | SET | 250 | 5058.42 | 455.2578 | 455.2578 | 5968.9356 | 1492233.9 |  |  |  | 1492233.9 | 0
21.3 | 120 kN Long Rod Insulator (Porcelain type Long rod) for 400 KV | SET | 120 | 10672.8769 | 960.5589 | 960.5589 | 12593.9948 | 1511279.3761 |  |  |  | 1511279.3761 | 0
21.4 | 120 kN Long Rod Insulator (Porcelain type Long rod) for 220 KV | SET | 100 | 5058.42 | 455.2578 | 455.2578 | 5968.9356 | 596893.56 |  |  |  | 596893.56 | 0
22 | ACSR MOOSE CONDUCTOR | KM | 15 | 446927.69 | 40223.4921 | 40223.4921 | 527374.6742 | 7910620.113 | TL-19 |  |  | 7910620.113 | 0
23 | ACSR Panther Conductor | MTR | 200 | 192.28 | 17.3052 | 17.3052 | 226.8904 | 45378.08 | TL-17 |  |  | 45378.08 | 0
24 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. | Mtr | 2500 | 3815.49 | 343.39 | 343.39 | 4502.27 | 11255675 | BADAKUSHASTHALI 25 ( SANCTION ESTIMATE ON DATED 07.02.2025) |  |  | 11255695.5 | 20.5
25 | IPS 4" ALUMINIUM TUBES(OD:114.2 mm & 8.51mm Thickness)( Required for Equipment to equipment connection in 220 KV side only) including welding sleeves,corona bell etc. | Mtr | 1200 | 3052.392 | 274.72 | 274.72 | 3601.832 | 4322198.4 | BADAKUSHASTHALI 26 ( SANCTION ESTIMATE ON DATED 07.02.2025) |  |  | 4322187.072 | -11.328
26 | SUBSTATION EARTHING SYSTEMS | [10 empty] | 0 | 0
26.1 | EARTHING CONDUCTOR FOR BURRIAL :(40MM MS ROD) for laying as main eartth mat (spacing maximum 5m both way) | MT | 275 | 70000 | 6300 | 6300 | 82600 | 22715000 | Badakushasthali SS 13.1 |  |  | 22715000 | 0
26.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MT | 70 | 70000 | 6300 | 6300 | 82600 | 5782000 | Badakushasthali SS 13.2 |  |  | 5782000 | 0
26.3 | EARTHING CONDUCTOR: 50X6 mm GI Flat for fencing,cable tray and auxiliary Boards earthing. | MT | 40 | 70000 | 6300 | 6300 | 82600 | 3304000 | Badakushasthali SS 13.3 |  |  | 3304000 | 0
26.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty Gl PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 600 | 2251.91 | 202.6719 | 202.6719 | 2657.2538 | 1594352.28 | Badakushasthali SS 13.4 |  |  | 1594352.28 | 0
26.5 | Cleats of size 100 mm height, 10 mm thickness, and 75 mm width on both sides for welding of 40mm GI rods at intersection. | LOT | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | market rate |  |  | 590000 | 0
26.6 | 100 Sq mm copper braid for gate earthing. | LOT | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | market rate |  |  | 59000 | 0
26.7 | Design and Supply of Direct Stroke Lightening Protection System: (As per TS, approved drawings and directions of Engineer-in-Charge.) using IEC 62305 / Razevig method / National Building Code. The scope includes design and supply of all materials (excluding switchyard columns and lighting cum lightning mast) for DSLP of entire switchyard area under present scope, all buildings, ICT and reactors. Includes all materials such as Shield wires, Horizontal Conductor & Down conductor, Droppers, Earth electrodes, Test link, Cleats, lugs, Air termination rods/ Lightning spike, PG Clamp, D Shackle. etc. and all other accessories (except specified above at 27.1-27.6) to complete the system in full shape. Earthing of the DSLP system is included in the scope. NOTE: Switchyard columns and lighting cum lightning mast specified under different line item. All other items and accessories required except columns and LCLM are included the scope of supply. | LOT | 1 | 1500000 | 135000 | 135000 | 1770000 | 1770000 | Market rate |  |  | 1770000 | 0
27 | Supply of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network to each treated earth pit as per approved drawing. | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | LS | 50000 |  | 236000 | 0
28 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained. | [10 empty] | 0 | 0
28.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 6000 | 781.2 | 70.31 | 70.31 | 921.82 | 5530920 | Autonagar Sl no- 14.1 |  |  | 5530896 | -24
28.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 2500 | 624.75 | 56.23 | 56.23 | 737.21 | 1843025 | Autonagar Sl no- 14.2 |  |  | 1843012.5 | -12.5
28.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 2000 | 469.35 | 42.24 | 42.24 | 553.83 | 1107660 | Autonagar Sl no- 14.3 |  |  | 1107666 | 6
29 | Support G.I. angle 50x50x6 mm for cable tray | MT | 20 | 93451 | 8410.59 | 8410.59 | 110272.18 | 2205443.6 | CD TL 4 |  |  | 2205443.6 | 0
30 | SWITCH YARD STRUCTURES(including Foundation Bolts and Nuts) GALVANISED (LATTICE) FOR ALL 400 KV, 220 KV & 33KV. The 400KV Columns & Beams shall be designed for Quad ACSR Moose and the 220KV Columns and beams shall be designed for Twin ACSR moose, for WZ-V. The soft copy (AutoCAD, pdf, excel etc.) shall be submitted for the GA, BOM and Shop drawings. | [10 empty] | 0 | 0
30.1 | 400 KV Columns & beams as per approved Layout (6 nos of Diameters of I type) | Lot | 1 | [8 empty] | 0 | 0
30.2 | 220 KV Column & beams as per approved Layout | Lot | 1 | [8 empty] | 0 | 0
30.5 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 600 | 82451 | 7420.59 | 7420.59 | 97292.18 | 58375308 | As per OPTCL RC no. 767 dtd. 24.06.2025 |  |  | 58375308 | 0
30.5 | Total weight of different size of GI Nuts and bolts for structures. | MT | 60 | 102000 | 9180 | 9180 | 120360 | 7221600 | As per OPTCL RC no. 767 dtd. 24.06.2025 |  |  | 7221600 | 0
31 | SUPPORT STRUCTURES (Including foundation Bolts and Nuts) GALVANISED (PIPE TYPE) FOR ALL 400 KV, 220 kV & 33KV EQUIPMENT INCLUDING NCTs. The Pipe type structures shall be designed for WZ-V. The soft copy (pdf, excel etc.) shall be submitted for the GA, BOM and Shop drawings. | [10 empty] | 0 | 0
31.1 | 400 KV Equipment structures as per approved Layout | Lot | 1 | [8 empty] | 0 | 0
31.2 | 220 KV Equipment structures as per approved Layout | Lot | 1 | [8 empty] | 0 | 0
31.3 | 132KV equipment structures as per approved layout | Lot | 1 | [8 empty] | 0 | 0
31.4 | 33Kv equipment structures as per approved layout | Lot | 1 | [8 empty] | 0 | 0
31.5 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 130 | 82451 | 7420.59 | 7420.59 | 97292.18 | 12647983.4 | As per OPTCL RC no. 767 dtd. 24.06.2025 | 180 | neulapoi | 12647983.4 | 0
31.6 | Total weight of different size of GI Nuts and bolts for structures. | MT | 35 | 102000 | 9180 | 9180 | 120360 | 4212600 | As per OPTCL RC no. 767 dtd. 24.06.2025 | 90 |  | 4212600 | 0
32 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES | [10 empty] | 0 | 0
32.1 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.) | [10 empty] | 0 | 0
32.1.1 | XLPE 1C X 630 mm2 | MTRS | 3000 | 831.4 | 74.83 | 74.83 | 981.06 | 2943180 | Ramakrushnapur |  |  | 2943156 | -24
32.1.2 | XLPE 3.5 CX185 mm2 | MTRS | 1000 | 488.67 | 43.98 | 43.98 | 576.63 | 576630 | CD SS 132 |  |  | 576630.6 | 0.6
32.1.3 | XLPE 3.5 CX120 mm2 | MTRS | 1500 | 459.11 | 41.32 | 41.32 | 541.75 | 812625 | CD SS 131 |  |  | 812624.7 | -0.3
32.1.4 | PVC 3.5 CX70 mm2 | MTRS | 1500 | 265.69 | 23.91 | 23.91 | 313.51 | 470265 | CD SS 129 |  |  | 470271.3 | 6.3
32.1.5 | PVC 3.5 CX35 mm2 | MTRS | 1500 | 147.5 | 13.28 | 13.28 | 174.06 | 261090 | CD SS 127 |  |  | 261075 | -15
32.1.6 | PVC 4 CX 16 mm2 | MTRS | 3000 | 115.78 | 10.42 | 10.42 | 136.62 | 409860 | CD SS 125 |  |  | 409861.2 | 1.2
32.1.7 | PVC 4 CX 6 mm2 | MTRS | 1000 | 114.31 | 10.29 | 10.29 | 134.89 | 134890 | BADAKUSTHASTHALI 16.1.7 |  |  | 134885.8 | -4.2
32.1.8 | PVC 2CX 6 mm2 | MTRS | 1000 | 114.31 | 10.29 | 10.29 | 134.89 | 134890 | BADAKUSTHASTHALI 16.1.8 |  |  | 134885.8 | -4.2
32.2 | CONTROL CABLES,1.1 KV, PVC ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule) | [10 empty] | 0 | 0
32.2.1 | 4 CX 2.5 mm2 | MTRS | 12000 | 123.67 | 11.13 | 11.13 | 145.93 | 1751160 | CD SS 109 |  |  | 1751167.2 | 7.2
32.2.2 | 5 CX 2.5 mm2 | MTRS | 13000 | 184.82 | 16.63 | 16.63 | 218.08 | 2835040 | BADAKUSTHASTHALI 16.2.2 |  |  | 2835138.8 | 98.8
32.2.3 | 7CX 2.5 mm2 | MTRS | 4000 | 187.2 | 16.85 | 16.85 | 220.9 | 883600 | CD SS 110 |  |  | 883584 | -16
32.2.4 | 10 CX 2.5 mm2 | MTRS | 6500 | 254.41 | 22.9 | 22.9 | 300.21 | 1951365 | CD SS 111 |  |  | 1951324.7 | -40.3
32.2.5 | 12 CX 2.5 mm2 | MTRS | 6000 | 289.73 | 26.08 | 26.08 | 341.89 | 2051340 | BADAKUSTHASTHALI 16.2.5 |  |  | 2051288.4 | -51.6
32.2.6 | 16 CX 2.5 mm2 | MTRS | 5000 | 387.03 | 34.83 | 34.83 | 456.69 | 2283450 | CD SS 112 |  |  | 2283477 | 27
32.2.7 | 19 CX 2.5 mm2 | MTRS | 8000 | 448.83 | 40.39 | 40.39 | 529.61 | 4236880 | CD SS 113 |  |  | 4236955.2 | 75.2
32.2.8 | 27 CX 2.5 mm2 | Mtrs | 3000 | 741.1 | 66.7 | 66.7 | 874.5 | 2623500 | market rate |  |  | 2623494 | -6
32.2.9 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTRS | 500 | 635 | 57.15 | 57.15 | 749.3 | 374650 | BADAKUSTHASTHALI 16.2.8 |  |  | 374650 | 0
33 | Supply of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI | [10 empty] | 0 | 0
33.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 | 296 | 26.64 | 26.64 | 349.28 | 523920 | BADAKUSHASTHALI 17.1 |  |  | 523920 | 0
33.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 750 | 59.322 | 5.339 | 5.339 | 70 | 52500 | BADAKUSHASTHALI 17.2 |  |  | 52500 | 0
34 | SUPPLY OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY | [10 empty] | 0 | 0
34.1 | STATION TRANSFORMER 33KV/433V,1000 KVA (AS PER SPECIFICATION and with 66KV bushings of HV side) | NOS | 2 | 1937500 | 174375 | 174375 | 2286250 | 4572500 | SS-67 |  |  | 4572500 | 0
34.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators of 66KV rating, channels complete in all respect (each set comprises three single HG fuse) | SETS | 2 | 9569 | 861.21 | 861.21 | 11291.42 | 22582.84 | LS |  |  | 22582.84 | 0
35 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) | [10 empty] | 0 | 0
35.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained).The qty of lighting fixtures shall bs as per the Lighting calculation. | Nos | 250 | 12000 | 1080 | 1080 | 14160 | 3540000 | BADAKUSHASTHALI 19.1 |  |  | 3540000 | 0
35.2 | STREET LIGHTING: HDG Octagonal street lighting poles 7 m height (Crompton/Bajaj/Skipper/Transrail Make) with arm bracket for holding light, foundation nuts & bolts and LED light fittings etc. The pole shall be manufactured in a single section with weight of galvanization 610 g/sqm or thickness of galvanization 86 micron. The pole shall be meant for installation in Wind Zone V. Poles should be suitable for installation on a RCC concrete foundation with 4nos x 20 mm dia foundation bolts with 225 mm PCD . (Poles shall have variable PCD (200-250 mm dia) type base plate with diagonal slotted holes ) It includes supply of LED lighting fixtures with lamps of 100 Watts of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro), with switch gear, GI Conduit etc. & as per technical specification. The pole shall have separate or inbuilt GI junction box with suitable cover with (water/dust) ingress protection for housing electrical accessories. The JB shall have provision of fuses/MCB, buses, TBs as required for cable in and out. N.B.: Actual quantity shall be as per site condition and as per approval of the competent authority considering the Lux standard. | Nos | 100 | 30000 | 2700 | 2700 | 35400 | 3540000 | BADAKUSHASTHALI 19.2 |  |  | 3540000 | 0
36 | Design and Supply of Air Conditioning System: (As per TS, approved drawings and directions of Engineer-in-Charge.) | [10 empty] | 0 | 0
| Supply of 2 Ton Split type Air Conditioners [both indoor and outdoor units] (Inverter, five star latest model - LG/Hitachi /Carrier/Mitsubishi Heavy Industries/Daikin/Voltas/O' General Make) with copper condensor having remote control. Scope includes all other additional accessories such as Automatic Voltage Stabilizers, copper piping, copper cable, insulation over copper pipe, PVC corrrugated drain pipes, steel brackets for holding outdoor units, first filling of refrigerant and all other accessories necessary for completion of the AC system. | [10 empty] | 0 | 0
| Air conditioning system shall be designed to maintain the inside Dry Bulb Temperature below 24 °C. Bidder shall submit necessary design calculations for OPTCL's approval. The qty of ACs shall be as per the approved design. Compressor of AC shall have minimum 5 years Warranty from the date of commissioning. Following item description also includes AC Control Panel(s) made of 2mm CR sheet, having suitable outgoing (one outgoing for one AC & with overload control gear) & wiring materials with 16 amp industrial socket & plug for each unit of AC etc (As per specification) for the following buildings. Number of such panels shall be as per reqirement and approved drawings. | [10 empty] | 0 | 0
| Additional requirement for GIS hall relay panel room, VRLA Battery room, CRB - Panel/HMI room, CRB - LT AC/DC room, Switchyard Kisok etc (as applicable): At least 50% spare/Stand by Air-Conditioning capacity shall be provided. Supply of Logic controller for Auto Switch ON & OFF of AC units as follows: • Standby units shall come in to operation automatically when the running main unit fails • Main and standby units shall be changed over periodically • Following alarms shall be provided: a. Compressor On/OFF condition of each unit b. Compressor failure of each unit c. Power OFF to AC unit d. High temperature in room | [10 empty] | 0 | 0
| Temperature transducer shall be provided to monitor the temperature. The Temperature transducer shall have the following specification: (Sensor : Air temperature sensor (indoor use), Output : 4 to 20mA, Temperature range : -5°C to 60°C, Resolution : 0.1°C, Accuracy : 0.5°C or better.) | [10 empty] | 0 | 0
36.1 | Control Room Building - Control/SAS Room, LT AC/DC Room, Communication room, office rooms, conference room, library, rest room & VRLA battery room. | Nos | 28 | 65000 | 5850 | 5850 | 76700 | 2147600 | BADAKUSHASTHALI 20.0 |  |  | 2147600 | 0
36.2 | AC for Switchyard Kiosk (3 nos per Kiosk) as per T.S. (The ACs shall run in tandem i.e 1 of the ACs at a time for 4 hours each.)[ 02nos Bay Kiosk for 400Kv side & 02nos Bay Kiosk for 220Kv side] | Nos | 12 | 65001 | 5850.09 | 5850.09 | 76701.18 | 920414.16 | BADAKUSHASTHALI 20.0 |  |  | 920414.16 | 0
36.3 | Air conditioning System for Transit House-Guest rooms & Dining hall | Nos | 8 | 65000 | 5850 | 5850 | 76700 | 613600 | BADAKUSHASTHALI 20.0 |  |  | 613600 | 0
37 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTEDFIRE EXTINGUSHERS SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC | [10 empty] | 0 | 0
37.1 | FOAM TYPE-9 LTRS | NOS | 20 | 6430 | 578.7 | 578.7 | 7587.4 | 151748 | BADAKUSHASTHALI 21.1 |  |  | 151748 | 0
37.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 4 | 49733 | 4475.97 | 4475.97 | 58684.94 | 234739.76 | BADAKUSHASTHALI 21.2 |  |  | 234739.76 | 0
37.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 10020 | 901.8 | 901.8 | 11823.6 | 70941.6 | BADAKUSHASTHALI 21.3 |  |  | 70941.6 | 0
37.4 | CO2 - 4.5 KGS | NOS | 15 | 21390 | 1925.1 | 1925.1 | 25240.2 | 378603 | BADAKUSHASTHALI 21.4 |  |  | 378603 | 0
37.5 | CO2 - 9 KGS | NOS | 10 | 31620 | 2845.8 | 2845.8 | 37311.6 | 373116 | BADAKUSHASTHALI 21.5 |  |  | 373116 | 0
37.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 37241 | 3351.69 | 3351.69 | 43944.38 | 175777.52 | BADAKUSHASTHALI 21.6 |  |  | 175777.52 | 0
37.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & CANOPY (3 mm thick) | SET | 6 | 5415 | 487.35 | 487.35 | 6389.7 | 38338.2 | BADAKUSHASTHALI 21.7 |  |  | 38338.2 | 0
37.8 | 9 litre water type | Nos. | 6 | 14810.12 | 1332.91 | 1332.91 | 17475.94 | 104855.64 | market rate |  |  | 104855.6496 | 0.0096
37.9 | 4.5 kg DCP type | Nos. | 6 | 5021.38 | 451.92 | 451.92 | 5925.22 | 35551.32 |  |  |  | 35551.3704 | 0.0504
37.1 | 50 Litres Mechanical Foam type | Nos. | 2 | 40135.15 | 3612.16 | 3612.16 | 47359.47 | 94718.94 |  |  |  | 94718.954 | 0.014
38 | SUBSTATION AUTOMATION SYSTEM FOR 400/220KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 400, 220 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type. | [10 empty] | 0 | 0
38.1 | SUBSTATION AUTOMATION SYSTEM (IEC 61850) Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification) system (for All 400, 220 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 | 11380285.09 | 1024225.66 | 1024225.66 | 13428736.41 | 13428736.41 | Badakushasthali SS 38.1+38.2+38.3 |  |  | 13428736.4062 | -0.0038
| RCC Communication Panel; comprising of: 1. Substation Ethernet Switches (Layer-3 type)- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Doublle jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | [10 empty] | 0 | 0
| Operator Workstations -2 nos | [10 empty] | 0 | 0
| Engineering workstation -1 no | [10 empty] | 0 | 0
| Workstation for RAS (Remote Access System) -1 no | [10 empty] | 0 | 0
| Black & whiter Laser jet Printer-1no | [10 empty] | 0 | 0
| Inverters - 3 KVA (Main & Stand by)- 2 nos | [10 empty] | 0 | 0
| Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. | [10 empty] | 0 | 0
| GPS System with IRIG-B/SNTP/PTP with VDU (Clock)-1 no | [10 empty] | 0 | 0
39 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification. | [10 empty] | 0 | 0
39.1 | 400KV feeder Protection Panel: MAIN-I , MAIN-II Distance protection relays of different make, separate Backup Protection, Bay control unit (BCU), 2nos of DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Nos | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | SS-34 |  |  | 6833575.0304 | 0
39.2 | 400KV Transformer Protection Panel: Differential Protection Main- I & II of different make , Separate REF relay, separate Backup Protection (considering HV, IV & LV side for 500 MVA 400/220/33 KV ICT), Bay control units (BCU), 2nos of DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 3576298.55 | 321866.8695 | 321866.8695 | 4220032.289 | 8440064.578 | SS-35 |  |  | 8440064.578 | 0
39.3 | 400KV Tie Bay protection Panel: with Bay control unit (BCU), separate backup protection, 2nos of DCCO & other protection & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 4 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 13667150.0608 | SS-34 |  |  | 13667150.0608 | 0
39.4 | 400KV BUS-BAR Protection System (Distributed architecture with Main-I & Main-II): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 3809977.15 | 342897.9435 | 342897.9435 | 4495773.037 | 4495773.037 | SS-37 |  |  | 4495773.037 | 0
39.5 | 400 KV Bus Reactor Panel: With Numerical Backup-Impedance, Differential, Separate REF, separate Back-up protection, Bay Control Unit (BCU), 2nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | SS-34 |  |  | 6833575.0304 | 0
39.6 | 400 KV Line Reactor Panel: with Numerical Backup-Impedance, Differential, separate REF, separate Back-up protection, Bay Control Unit (BCU), 2 nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 |  |  |  | 6833575.0304 | 0
40 | 220 KV SIDE PROTECTION & OTHER PANELS | [10 empty] | 0 | 0
40.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, separate Backup Protection relays, Bay control unit (BCU), 2nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 2 | 2895582.64 | 260602.4376 | 260602.4376 | 3416787.5152 | 6833575.0304 | SS-37 |  |  | 6833575.0304 | 0
40.2 | 220KV Bus Coupler Protection Panel: BCU, separate Backup Protection Relays and other aux relays, 2nos DCCOs and including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 1438647.3742 | SS-39 |  |  | 1438647.3742 | 0
40.3 | 220KV Transfer Bus Coupler Protection Panel: BCU, separate Backup Protection Relays and other aux relays, 2 nos DCCOs and including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 1438647.3742 | SS-39 |  |  | 1438647.3742 | 0
40.4 | 220KV BUS-BAR Protection Sysstem (Distributed architecture): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 3809977.15 | 342897.9435 | 342897.9435 | 4495773.037 | 4495773.037 | SS-40 |  |  | 4495773.037 | 0
40.5 | 220KV, 500MVA ICT Protection Panel: This includes all Relays (separate backup protection relay, LBB protection etc.) and Bay Control Units (BCU), complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 2 | 1219192.69 | 109727.3421 | 109727.3421 | 1438647.3742 | 2877294.7484 | SS-39 |  |  | 2877294.7484 | 0
41 | 33 KV SIDE PROTECTION PANELS: Single Panel Twin Bay type ( 2 Bays in One Panel) with IEC:61850-ED2 PRP on FO | [10 empty] | 0 | 0
41.1 | 33KV PROTECTION PANEL (WIth BCU, Separate backup protection relay & with other auxiliary relays, 2 DCCOs for DC as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) for protection of Station transformers. Note: 02 No.s of feeder bays to be considered in one Panel. | SET | 1 | 1015993.9067 | 91439.45 | 91439.45 | 1198872.8067 | 1198872.81 | BADAKUSHASTHALI 25.1 |  |  | 1198872.8099 | -0.00013333
42 | AC & DC SYSTEM | [10 empty] | 0 | 0
42.1 | AC SYSTEM | [10 empty] | 0 | 0
42.1.1 | MAIN AC DB (Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type ACB with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection). The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 1093219 | 98389.71 | 98389.71 | 1289998.42 | 1289998.42 | BADAKUSHASTHALI 26.1.1 |  |  | 1289998.42 | 0
42.1.2 | ACDB (Indoor Type) WITH BUS 1, BUS 2, BUS 3, Bus Coupler 1 & Bus Coupler 2: HAVING 400A Motorized MCCB for automatic operation in Incomers and Bus couplers with electrical interlock system. With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected with two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 771193 | 69407.37 | 69407.37 | 910007.74 | 910007.74 | BADAKUSHASTHALI 26.1.2 |  |  | 910007.74 | 0
42.1.3 | Main Lighting Distribution Board (having 250A MCCB as Incomer) as per TS (witc DB-1,DB-2 & B/C) with mechanicla Interlock through castle lock. | SET | 1 | 191442.23 | 17229.8 | 17229.8 | 225901.83 | 225901.83 | BADAKUSHASTHALI 26.1.3 |  |  | 225901.8314 | 0.0014
42.1.4 | Indoor Lighting Distribution Board as per TS. (WITH DB-1,DB-2 & B/C) | SET | 1 | 24249.35 | 2182.44 | 2182.44 | 28614.23 | 28614.23 | BADAKUSHASTHALI 26.1.4 |  |  | 28614.233 | 0.003
42.1.5 | Emergency Lighting Distribution Board as per specification. | SET | 1 | 329232.75 | 29630.95 | 29630.95 | 388494.65 | 388494.65 | BADAKUSHASTHALI 26.1.5 |  |  | 388494.645 | -0.005
42.1.6 | Indoor Receptacle Board as per Specification | SET | 2 | 209112.75 | 18820.15 | 18820.15 | 246753.05 | 493506.1 | BADAKUSHASTHALI 26.1.6 |  |  | 493506.09 | -0.01
42.1.7 | Outdoor Kiosk For Station Transformer: as per TS with 3 NOS. OF Cut-Outs (1000 Amps) at the Incoming side, 1No. of 3 phase SFU (800 Amps) at the Outgoing and suitable Busbar arrangement for termination of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 73216.5 | 6589.49 | 6589.49 | 86395.48 | 172790.96 | BADAKUSHASTHALI 26.1.7 |  |  | 172790.94 | -0.02
42.1.8 | Outdoor Kiosk for Switchyard Lights: as per TS having timer control for switching the lights ON & OFF. | SET | 16 | 56742.7875 | 5106.85 | 5106.85 | 66956.4875 | 1071303.8 | BADAKUSHASTHALI 26.1.8 |  |  | 1071303.828 | 0.028
42.1.9 | Ootdoor Kiosk for Colony/Transit House Supply: as per TS | SET | 1 | 56742.7875 | 5106.85 | 5106.85 | 66956.4875 | 66956.49 | BADAKUSHASTHALI 26.1.9 |  |  | 66956.4892 | -0.00075
42.1.10 | Outdoor Kiosk for Street Lights: as per TS having timer control for switching the lights ON & OFF. | NOS | 4 | 56742.7875 | 5106.85 | 5106.85 | 66956.4875 | 267825.95 | BADAKUSHASTHALI 26.1.10 |  |  | 267825.957 | 0.007
42.1.11 | Outdoor Receptacle Board: (Transformer filtration purpose): as per TS | NOS | 2 | 56742.7875 | 5106.85 | 5106.85 | 66956.4875 | 133912.98 | BADAKUSHASTHALI 26.1.11 |  |  | 133912.9785 | -0.0015
42.1.12 | Outdoor Receptacle Board: (Welding & other uses) : as per TS | NOS | 7 | 56742.7875 | 5106.85 | 5106.85 | 66956.4875 | 468695.41 | BADAKUSHASTHALI 26.1.12 |  |  | 468695.4248 | 0.01475
42.1.13 | Bay Marshalling Kiosk (Outdoor type): as per TS and approved layout (400Kv, 220Kv & 33KV). | Nos | 17 | 21058.65 | 1895.28 | 1895.28 | 24849.21 | 422436.57 | BADAKUSHASTHALI 26.1.13 |  |  | 422436.519 | -0.051
42.1.14 | CT Out Door Console Boxes: As per TS & approved layout (Outdoor type) (400Kv, 220Kv & 33KV). | Nos | 22 | 45108.48 | 4059.76 | 4059.76 | 53228 | 1171016 | BADAKUSHASTHALI 26.1.14 |  |  | 1171016.1408 | 0.1408
42.1.15 | IVT/PT Outdoor Console Boxes: as per TS & approved layout (400Kv, 220Kv & 33KV). | Nos | 8 | 45108.48 | 4059.76 | 4059.76 | 53228 | 425824 | BADAKUSHASTHALI 26.1.14 |  |  | 425824.0512 | 0.0512
42.1.16 | ACDB for Yard Kiosk | Nos | 4 | 45108.48 | 4059.7632 | 4059.7632 | 53228.0064 | 212912.0256 | BADAKUSHASTHALI 26.1.14 |  |  | 212912.0256 | 0
43 | DC SYSTEM (suitable for SAS operation) | [10 empty] | 0 | 0
43.1 | 220 V MAIN DCDB in Control Room Building (HAVING DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE protection (with BUS-1, BUS-2 & B/C). Consider separate source(DC1 & DC 2) to each DCDB of Bay Kiosks, local supply of CRB such as emergency lighting, SAS system etc. & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered ( with 20% spare). Incoming and outgoing ratings of MCBs shall be decided as per panel load during detail engineering. The construction shall be as per the TS. | Nos | 1 | 375905 | 33831.45 | 33831.45 | 443567.9 | 443567.9 | BADAKUSHASTHALI 27.1 |  |  | 443567.9 | 0
43.2 | 220 V DC Emergency Distribution Board: as per TS | Set | 1 | 371115.33 | 33400.3797 | 33400.3797 | 437916.0894 | 437916.0894 | BADAKUSHASTHALI 27.2 |  |  | 437916.0894 | 0
43.3 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output to be considered. | SET | 4 | 54087.06 | 4867.8354 | 4867.8354 | 63822.7308 | 255290.9232 |  |  |  | 255290.9232 | 0
44 | Stationary VRLA Battery, 350 Ah (C10 rate) for 220 V DC (Cells: 107 Nos + 3 Nos, 2V Nominal/Cell) as per TS and IS 15549 & IEC 60896-21/22. (The battery shall be capable of giving 1200 or more charge/discharge cycles at 80% DOD at an average temperature of 27º Celsius. The battery sets shall have a minimum expected life of 20 years at float operation.) Agency shall furnish battery sizing calculation, selection of number of cells, float and Boost voltages as per IEEE- 485. Duty cycle for sizing calculation shall be 3h for continious load, 1 hour for emergency load and 1 min for momentary load. | SET | 2 | 2043381.24 | 183904.31 | 183904.31 | 2411189.86 | 4822379.72 | BADAKUSHASTHALI 28 |  |  | 4822379.7264 | 0.0064
45 | FLOAT CUM BOOST Battery Charger for offered 350 Ah VRLA Type Battery: Float Charging: 2.13-2.27 V per cell, Boost Charging: 2.28-2.32 V per cell. (FC 35A/ BC 70A) Input from AC Source I & II without automatic selection. Filter circuit shall be provided to limit the ripple content (Peak to Peak) in the output voltage to 1%, irrespective of the DC load level. a. The battery charger shall support both automatic and manual control of output voltage and current, selectable via a mode selector switch. In automatic mode during float charging, the output voltage shall remain within ±1% of the set value under AC input voltage variation of ±10%, frequency variation of ±5%, combined variation of ±10%, and DC load variation from no load to full load. b. Battery chargers shall operate on constant voltage characteristics across the full load range (zero to full load) at float voltage, ensuring the battery remains fully charged without harmful overcharge. c. Load limiters with drooping characteristics shall be provided, which: * Gradually reduce output voltage when the DC load current exceeds the preset limit (in automatic voltage control mode). * Prevent damage or fuse failure during sustained overloads or short circuits in the DC system. * Ensure the charger does not trip under overload or external short circuit conditions. d. Uniform and stepless adjustment of output voltage shall be available in both manual and automatic modes, accessible from the charger’s front panel, covering the entire float voltage range. e. Stepless adjustment of load limiter setting shall also be provided, adjustable from 80% to 100% of the charger's rated output current during charging mode. f. It shall be possible to adjust the Boost charging current continuously over a range of 50 to 100% of the rated output current for Boost charging mode. g. While in Boost mode, the charger output voltage shall rise automatically as the battery charges. A potentiometer shall be provided on the front panel to set the upper voltage limit for Boost mode, adjustable anywhere within the specified output voltage range. [Charger shall be made from CRCA sheet steel-2mm thick, IP 42 rated, Painted: Phosphated-Primer-Painted 50um, ] The Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS. | SET | 2 | 400396.18 | 36035.66 | 36035.66 | 472467.5 | 944935 | BADAKUSHASTHALI 29 |  |  | 944934.9848 | -0.0152
46 | 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | NOS | 2 | 40000 | 3600 | 3600 | 47200 | 94400 | BADAKUSHASTHALI 30 |  |  | 94400 | 0
47 | Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | NOS | 2 | 21000 | 1890 | 1890 | 24780 | 49560 | BADAKUSHASTHALI 31 |  |  | 49560 | 0
48 | MAINTENANCE & TESTING EQUIPMENT | LOT | 1 | 15849817.39 | 1426483.5651 | 1426483.5651 | 18702784.5202 | 18702784.5202 | BADAKUSHASTHALI 33 |  |  | 18702784.5202 | 0
48.1 | 100KV Automatic Transformer Oil Breakdown Voltage test set (Megger- OTS 100AF / Baur- DTA 100C) | Nos | 1 | [8 empty] | 0 | 0
48.2 | 10KV Insulation Tester with 15m test leads (Megger- S1-1068 / Sonel-MIC 10K1) | Nos | 1 | [8 empty] | 0 | 0
48.3 | Digital Earth Tester (Facility for soil resistivity measurement and test leads suitable for connection to the test probe/spikes placed at 20m between each other ) (Megger-DET2/3 / Sonel MRU-120 / Fluke 1625) | Nos | 1 | [8 empty] | 0 | 0
48.4 | Digital Multimeter (Megger / Fluke) | Nos | 2 | [8 empty] | 0 | 0
48.5 | Digital Clamp meter (Megger/Fluke/Motwane) | Nos | 1 | [8 empty] | 0 | 0
48.6 | Leakage current clamp meter AC & DC both (30mA / 300mA / 30A / 300A) (Megger/Fluke/Kyoritsu) | Nos | 1 | [8 empty] | 0 | 0
48.7 | SF6 Gas Leakage Detector (Wika/DILO) | Nos | 1 | [8 empty] | 0 | 0
48.8 | Oil sampling Bottle- Stainless Steel, Capacity- 1 Ltr (Make- Tosin) | Nos | 6 | [8 empty] | 0 | 0
48.9 | Fibre Glass Discharge / Earth Rod: Grip up to 50mm, Min height-16ft, rubber grip, 35 sq.mm copper cable (1 set- 3 cables, 1 set of rod, carry bag) (Bemico) | Set | 6 | [8 empty] | 0 | 0
48.1 | Electrical Rubber Hand Gloves | Pairs | 4 | [8 empty] | 0 | 0
48.11 | Portable High Beam Light (with at least 2000mAh rechargeable battery, rated power-15W, Input-230V , 50Hz) (Phillips) | Nos | 2 | [8 empty] | 0 | 0
48.12 | Desktop Computer: (HP/Lenovo/Dell) | Set | 2 | [8 empty] | 0 | 0
| Processor-Intel Core i5 12th Gen or better | [10 empty] | 0 | 0
| RAM- 16GB DDR4 or More | [10 empty] | 0 | 0
| ROM- 512GB SSD | [10 empty] | 0 | 0
| Monitor- 21.5" FHD (1920 x 1080) or higher | [10 empty] | 0 | 0
| Graphics- Intel UHD | [10 empty] | 0 | 0
| OS- Genuine Windows 11 Pro | [10 empty] | 0 | 0
48.13 | Webcam- 720P Logitech | Nos | 2 | [8 empty] | 0 | 0
48.14 | Speaker- 2 nos Stereo type | Nos | 2 | [8 empty] | 0 | 0
48.15 | UPS 600VA (APC/V Guard) | Nos | 2 | [8 empty] | 0 | 0
48.16 | Laser Printer (A4 size), Black & White, Duplex printing (print, scan & copy) (HP/Canon/Epson) | Nos | 1 | [8 empty] | 0 | 0
49 | OTHER TOOLS AND PLANTS (T&P’S) REQUIREMENT: | Lot | 1 | 620000 | 55800 | 55800 | 731600 | 731600 | BADAKUSHASTHALI 34 |  |  | 731600 | 0
49.1 | D Spanner Set (6mm – 42mm) | Set | 1 | [8 empty] | 0 | 0
49.2 | Ring Spanner Set (6mm – 42mm) | Set | 2 | [8 empty] | 0 | 0
49.3 | Box spanner set | Set | 3 | [8 empty] | 0 | 0
49.4 | Pipe Wrench 24 " | Nos | 4 | [8 empty] | 0 | 0
49.5 | Pipe Wrench 18 " | Nos | 5 | [8 empty] | 0 | 0
49.6 | Adjustable spanner -12”(slide wrench) | Nos | 6 | [8 empty] | 0 | 0
49.7 | Adjustable spanner -18”(slide wrench) | Nos | 7 | [8 empty] | 0 | 0
49.8 | Insulated cutting plier (standard size) | Nos | 8 | [8 empty] | 0 | 0
49.9 | Nose Plier (standard size) | Nos | 9 | [8 empty] | 0 | 0
49.1 | Screw Driver set | [10 empty] | 0 | 0
49.11 | 12” Plain head | Nos | 2 | [8 empty] | 0 | 0
49.12 | 12” star head | Nos | 2 | [8 empty] | 0 | 0
49.13 | 8” Plain head | Nos | 2 | [8 empty] | 0 | 0
49.14 | 6” plain head | Nos | 2 | [8 empty] | 0 | 0
49.15 | 6” star head | Nos | 2 | [8 empty] | 0 | 0
49.16 | Set of screw driver cum line tester | Set | 1 | [8 empty] | 0 | 0
49.17 | Allen Key set | Set | 1 | [8 empty] | 0 | 0
49.18 | Files | [10 empty] | 0 | 0
49.19 | Flat File-12” | Nos | 1 | [8 empty] | 0 | 0
49.2 | Flat file-6” | Nos | 1 | [8 empty] | 0 | 0
49.21 | Round file- 12” | Nos | 1 | [8 empty] | 0 | 0
49.22 | Round file- 6” | Nos | 1 | [8 empty] | 0 | 0
49.23 | Hammer with Handle | [10 empty] | 0 | 0
49.24 | 1 lb | Nos | 2 | [8 empty] | 0 | 0
49.25 | 2 lb | Nos | 1 | [8 empty] | 0 | 0
49.26 | ½ lb | Nos | 2 | [8 empty] | 0 | 0
49.27 | Steel Tape (Any reputed make) | [10 empty] | 0 | 0
49.28 | 5Mtr | Nos | 1 | [8 empty] | 0 | 0
49.29 | 30Mtr | Nos | 1 | [8 empty] | 0 | 0
49.3 | Crow bar (Any reputed make) | [10 empty] | 0 | 0
49.31 | 5ft | Nos | 2 | [8 empty] | 0 | 0
49.32 | 3ft | Nos | 2 | [8 empty] | 0 | 0
49.33 | Oil Cane (Any reputed make) | Nos | 2 | [8 empty] | 0 | 0
49.34 | Hand Drill Machine (impact drill) with key (Make-Bosch/Black & Decker) | Nos | 1 | [8 empty] | 0 | 0
49.35 | Vacuum Cleaner (at least 15L) (Make-Eureka Forbes / Black & Decker / Phillips / Karcher) | Nos | 1 | [8 empty] | 0 | 0
49.36 | Stand Fan (450mm sweep,1400rpm, 240V AC) (Make-Crompton, Bajaj, Havells, Almonard, Usha) | Nos | 2 | [8 empty] | 0 | 0
49.37 | Self supproted cum extendable Ladder-25ft (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 | [8 empty] | 0 | 0
49.38 | Self supproted platform Ladder- 12feet (FRP) of Adequate Height to be used for Maintenance of Equipment Inside Switchyard. | Nos | 1 | [8 empty] | 0 | 0
49.39 | Adjustable Torque Wrench | Nos | 1 | [8 empty] | 0 | 0
49.4 | Self–Propelled Diesel Operated Articulated Boom Lift (to meet working height of 16m ±0.5m) with working platform, suitable for working in the switchyard, as per specifiction. | No | 1 | [8 empty] | 0 | 0
50 | 5 Ton Power winch (As per TS and Approved GTP) | SET | 2 | 100000 | 9000 | 9000 | 118000 | 236000 | Badakusasthali 35 & 36 |  |  | 236000 | 0
51 | Pedestal mounted wheel fitted derrick | SET | 4 | 15000 | 1350 | 1350 | 17700 | 70800 |  |  |  | 70800 | 0
52 | Supply of OFFICE FURNITURE (GODREJ MAKE) PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,SAS Room etc. | Lot | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000 | Badakusasthali 38 |  |  | 1180000 | 0
52.1 | For Control Room, conference room, office rooms, Library, testing room etc | [10 empty] | 0 | 0
52.2 | 5ftX3ft executive table with drawer on both sides | Nos | 4 | [8 empty] | 0 | 0
52.3 | 4.5ft X 2.5ft Table with one side drawer | Nos | 7 | [8 empty] | 0 | 0
52.4 | Computer table suitable keeping monitor, CPU, UPS and printer with two nos revolving arm chair suitable for computer use. | Set | 1 | [8 empty] | 0 | 0
52.5 | Executive revolving, adjustable (height) chairs with arm | Nos | 4 | [8 empty] | 0 | 0
52.6 | Cushion fixed “S” type steel chairs with arm | Nos | 16 | [8 empty] | 0 | 0
52.7 | 6ftX3ft conference table | Nos | 1 | [8 empty] | 0 | 0
52.8 | Cushion arm steel chairs for conference table purpose. | Nos | 6 | [8 empty] | 0 | 0
52.9 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 3 | [8 empty] | 0 | 0
52.1 | 6ft height steel almirah with glass doors for library purpose | Nos | 2 | [8 empty] | 0 | 0
52.11 | 6ft height (having minimum 6 lockers facility) steel cupboard with locking arrangement. | Nos | 2 | [8 empty] | 0 | 0
52.12 | 4ft steel rack (minimum three selves) for keeping the files and other items. | Nos | 8 | [8 empty] | 0 | 0
52.13 | For Communication Room | [10 empty] | 0 | 0
52.14 | 5ftX3ft executive table with drawer both sides | Nos | 1 | [8 empty] | 0 | 0
52.15 | Executive revolving, adjustable (height) chairs with arm | Nos | 1 | [8 empty] | 0 | 0
52.16 | Cushion fixed “S” type steel chairs with arm | Nos | 2 | [8 empty] | 0 | 0
52.17 | 6ft height steel almirah (only with selves) for keeping records and other valuable items. | Nos | 1 | [8 empty] | 0 | 0
53 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos. | 60 | 2500 | 225 | 225 | 2950 | 177000 | BADAKUSHASTHALI 40 |  |  | 177000 | 0
54 | 250 KVA Outdoor type silent Diesel Generator with control panel having adequate mechanical & electrical protection as per IS/IEC/TS. Max voltage variation: ± 1%, Max freq variation ± 2%. Voltage adjustment range -90% to +110%, Max vibration level 250um, Emergency Shutdown feature. Start/Stop: DG sets shall auto-start and take full load within 30 seconds of power failure. Feature for start/stop manually from remote as well as local. Alternator: 415V AC, 3Ph,50Hz, Rated PF 0.8, Brushless/SelfExcited, Class H insulation, 1500 rpm, with 10% overload capacity for 1 hour every 12 hours of continuous operation as per IS15999/IEC 60034. Engine: Multi cyliner, V type or Inline type, 1500 rpm, 4 stroke, Turbo Charged, Water Cooled, Battery Operated - Auto Start, Electronic Governer, Condensate traps shall be given on exhaust pipe, Diesel driven, as per IS 10002/BS 5514/ISO 3046/ IS 13018. Battery: Lead Acid, 24V DC, 180 AH, 2 Sets Charger: Float cum Boost SMPS Based, Ripple 1% max Fuel Tank & Pump: Tank: 990 liter, 2mm MS Sheet with Oil resistant paint, with Level Indicator, Filling Inlet with removable screen, outlet, drain plug, an air vent, air-breather and necessary piping with erection of the same as per Indian Explosive Act of 1932. Pump: Electrically Driven, Adequate to fill the fuel tank in 30 minutes Accuostic Enclosure: Sheet thickness 2 mm min, Rockwool insulation (min 50 mm thick) with fire resistant thermosetting resin, Noise level as per CPCB norms with a max of 75 dBA at a distance of 1 m. Emission standards: as per Latest MOEF/ CPCB/ SPCB guidelines. AMF Panel: Auto/Manual operation, IP 52, Controller, Metering CT (CL1, 15VA), Protection CT (Vk 300V, RCT 0.25 ohm) ions, Indications [DG Mains ON, Charger ON, DG Breaker ON/OFF, LT Source 1 ON, LT Source 2 ON] Controller: Microprocessor based, IEC 61850 compliant [for monitoring, meaurement , protection and control] * Meaurement: V, I, f, PF, O/P kVA, O/P kW, Speed, Run time, Lube Oil Pr., Coolant temp. etc. * Protection/Shurdown Functions: Differential, Short circuit protection, Over speed, Over Load, UV/OV, Low Lube OIl pressure, High Coolant Temp., High Enclosure Temp., Alternator Fault * Warning: Protection trip, Fail to crank, High/Low battery voltage, DG fail to start, Low fuel in tank * Indication (LED): DG running, Local/Remote mode, Manual/Auto mode, Warning, Shutdown. This includes all instrument transformers, internal wiring, indications and control switchgear etc. required to complete the system. | Nos. | 1 | 1619543.0475 | 145758.8743 | 145758.8743 | 1911060.7961 | 1911060.7961 | BADAKUSHASTHALI 41 |  |  | 1911060.7961 | 0
55 | 400/220/33 KV, 500 MVA ICT with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser, NCT and spare & other accessories etc as per Technical spec. | [10 empty] | 0 | 0
55.1 | 400/220KV, 500 MVA ICT with accessories and spares etc as per Technical spec. | NOS | 2 | 335708758.36 | 30213788.2524 | 30213788.2524 | 396136334.8648 | 792272669.7296 | CD SS-57 |  |  | 792272669.7296 | 0
55.2 | NCT for the ICTs- 2 nos | NOS | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 |  |  |  | 1180000 | 0
55.3 | Type Test Charges on 400/220/33 KV, 500 MVA ICT (on one unit out of the lot) for the following as per Technical Spec.: - Temperature Rise Test - Measurement of Zero Sequence Impedance - Auxiliary Power Consumption - Vacuum Test - Pressure Test - IP 55 Test | Lot | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000 | Badakusasthali 42.2 |  |  | 1180000 | 0
55.4 | (i) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) - 2 nos. | Nos | 2 | 10035869.78 | 903228.2802 | 903228.2802 | 11842326.3404 | 23684652.6808 | Badakusasthali 42.3 |  |  | 23684652.6808 | 0
55.5 | (ii) Online insulating oil drying system(As per Technical Specification) (1 set for each of the ICT)- 2 nos | Nos | 2 | 3500000 | 315000 | 315000 | 4130000 | 8260000 |  |  |  | 8260000 | 0
55.6 | (iii) Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification)- 2 nos | Nos | 2 | 3000000 | 270000 | 270000 | 3540000 | 7080000 |  |  |  | 7080000 | 0
55.7 | (iv) Oil storage Tank (25kL) as per Technical Specification -2 nos | Nos | 2 | 1287663.27 | 115889.6943 | 115889.6943 | 1519442.6586 | 3038885.3172 |  |  |  | 3038885.3172 | 0
56 | 400 kV, 125 MVAr BUS Reactor with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spare & other accessories etc as per Technical spec. | [10 empty] | 0 | 0
56.1 | 400 kV, 125 MVAr BUS Reactor with accessories and spares etc as per Technical spec. | Nos | 2 | 148000000 | 13320000 | 13320000 | 174640000 | 349280000 | Badakusasthali 43.1 |  |  | 349280000 | 0
56.2 | Type Test Charges on 400 kV 125 MVAr BUS Reactor for the following as per Technical Spec.: - Temperature Rise Test - Top oil and hot spot temperature rise test - Winding temperature rise test - Measurement of Zero Sequence Reactance -IP-55 Test | Lot | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | Badakusasthali 43.2 |  |  | 1180000 | 0
56.3 | (i) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) . | Nos | 2 | 3559348.9 | 320341.401 | 320341.401 | 4200031.702 | 8400063.404 | Badakusasthali 43.3 |  |  | 8400063.404 | 0
56.4 | (ii) Online insulating oil drying system(As per Technical Specification) (1 set for each of the Bus reactor) | Nos | 2 | 1000000 | 90000 | 90000 | 1180000 | 2360000 | market rate |  |  | 2360000 | 0
56.5 | (iii) Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (1 set for each of the Bus reactor) | Nos | 2 | 1000000 | 90000 | 90000 | 1180000 | 2360000 | market rate |  |  | 2360000 | 0
57 | 80 MVAR, 400 KV Line Reactor with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spares etc. as per Technical spec including all materials. | [10 empty] | 0 | 0
57.1 | 80 MVAR, 400 KV Line Reactor with accessories and spares as per Technical Spec. | Nos. | 2 | 39434005.92 | 3549060.5328 | 3549060.5328 | 46532126.9856 | 93064253.9712 | CD SS 65 |  |  | 93064253.9712 | 0
57.2 | Type Test Charges for any one of the entire LOT of 80 MVAR, 400 KV Line Reactor for the following as per Technical Spec.: - Temperature Rise Test - Top oil and hot spot temperature rise test - Winding temperature rise test - Measurement of Zero Sequence Reactance -IP-55 Test | Lot | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | market rate |  |  | 1180000 | 0
57.3 | (i) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) . | Lot | 2 | 3559348.9 | 320341.401 | 320341.401 | 4200031.702 | 8400063.404 | market rate |  |  | 8400063.404 | 0
57.4 | (ii) Online insulating oil drying system(As per Technical Specification) (1 set for each of the Line reactor) | Lot | 2 | 1000000 | 90000 | 90000 | 1180000 | 2360000 | market rate |  |  | 2360000 | 0
57.5 | (iii) Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (1 set for each of the Line reactor) | Lot | 2 | 1000000 | 90000 | 90000 | 1180000 | 2360000 | market rate |  |  | 2360000 | 0
58 | NGR, 132KV for 80MVAr Line Reactor as per Technical spec including all materials & its accessories. | Nos | 2 | 3470793.74 | 312371.4366 | 312371.4366 | 4095536.6132 | 8191073.2264 | CD SS 64 |  |  | 8191073.2264 | 0
59 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | [10 empty] | 0 | 0
59.1 | 48 fibre optic approach cable including HDPE pipes | KM | 2 | 127089.72 | 11438.07 | 11438.07 | 149965.86 | 299931.72 | BADAKUSHASTHALI 47.1 |  |  | 299931.7392 | 0.0192
59.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at Other end 400KV and 220 kV S/s | SET | 14 | 313986.07 | 28258.75 | 28258.75 | 370503.57 | 5187049.98 | BADAKUSHASTHALI 47.2 |  |  | 5187049.8764 | -0.1036
59.3 | 48V , 500Ah, maintenance free VRLA battery set | NO | 2 | 205516.42 | 18496.48 | 18496.48 | 242509.38 | 485018.76 | BADAKUSHASTHALI 47.3 |  |  | 485018.7512 | -0.0088
59.4 | SMPS based battery charger of 125A suitable for 48V, 500Ah VRLA battery | NO | 2 | 127187.61 | 11446.88 | 11446.88 | 150081.37 | 300162.74 | BADAKUSHASTHALI 47.4 |  |  | 300162.7596 | 0.0196
59.5 | 48 V DC board (having 100A DC MCCB as incomer, E/F (earth leakage), under & over voltage as per specification (DC DB-1,DC DB-2 & B/C). | SET | 1 | 11988 | 1078.92 | 1078.92 | 14145.84 | 14145.84 | BADAKUSHASTHALI 47.5 |  |  | 14145.84 | 0
59.6 | Optical Line Terminal Equipent(OLTE), STM16 type (5 MSP) SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module support upto 150kms ( 02 Nos.) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 637295.01 | 57356.55 | 57356.55 | 752008.11 | 752008.11 | BADAKUSHASTHALI 47.6 |  |  | 752008.1118 | 0.0018
59.7 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 53708.34 | 4833.75 | 4833.75 | 63375.84 | 126751.68 | BADAKUSHASTHALI 47.7 |  |  | 126751.6824 | 0.0024
59.8 | Voice gateway 2x(FXS) | Nos | 1 | 53000 | 4770 | 4770 | 62540 | 62540 | Autonagar Sl no- 20.4 |  |  | 62540 | 0
60 | Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Supply, Installation, Commissioning, Testing for IP Based CCTV Surveillance System (Server Based approach), DVR with 4TB Hard Disk, Day/Night Cameras, PC Monitor (Full HD - 32 inch) including all materials for areas inside & outside Control room building, Entire Switchyard areas covering boundaries, entry/exit points of substation & Other areas etc., suitable for 360 deg movement with all necessary hardware fittings for monitoring and surveillance of the entire substation. The CCTV system shall be able to be integrated with the SAS system. No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations. Tentative Requirement: 1. Fixed type bullet cameras for monitoring of Security shed cum Main gate complex, Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House, Main Entrance door of store shed, Open stockyard, Main entrance gate of switchyard and all gates of switchyard etc. 2. Dome/Bullet cameras for indoor areas - 3. PTZ cameras (as per requirement ): Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 | 1000000 | 90000 | 90000 | 1180000 | 1180000 | LS |  |  | 1180000 | 0
| Design and Supply for IP Based VMS (Server Based with VMS software), which shall include ONVIF Compliant Colour Cameras with Night Vision(Bullet/Done/PTZ), PTZ Controller, Server (Rack mounted/Tower type) Based NVR with VMS Software,VMS Client PC, NAS Storage, Mounting arrangement for cameras, cables (Armoured/Un armoured FO/Ethernet/AC/DC/HDMI etc.), HDPE Pipes, Ethernet Switches, UPS, Battery, LIU,POE Injectors, Media Converters, Surge Protection Device (SPD), Ethernet Surge Protectors (ESP), Outdoor/Indoor Junction Boxes/Panels, Main display unit (32 inch Full HD), Keyboard, Mouse, Routers, Networking Rack etc. including any other hardware or software to complete the system as per TS. | [10 empty] | 0 | 0
| An additional display unit (32 inch Full HD) shall also be provided in the security shed for monitoring purpose as per TS. | [10 empty] | 0 | 0
| Any other materials (Hardware & Software) required at the substation for connection of VMS system with remote control center of OPTCL including configuration of the same are also included in the scope of supply. (Configuration at Remote Control Center not the scope of the Contractor.) | [10 empty] | 0 | 0
| Network Topology: Ring | [10 empty] | 0 | 0
| No. of such cameras (different type viz. PTZ, bullet or dome) are to be calculated as per standard practice & its installations at the strategic locations so as to avoid blind spots. | [10 empty] | 0 | 0
| The following areas are to be covered without any blind spots: | [10 empty] | 0 | 0
| 1. Entry and exits of Store and Equipment storage Platforms/Open stockyard - Bullet cameras | [10 empty] | 0 | 0
| 2. All entry and exits of Control room building - Bullet cameras | [10 empty] | 0 | 0
| 3. All gates of substation and switchyard - Bullet cameras | [10 empty] | 0 | 0
| 4. Control Room Building (Inside Areas) - Panel Room, HMI Room, Communication Room, LT(AC/DC) Panel Room, Battery Room. - Bullet/Dome cameras | [10 empty] | 0 | 0
| 5. Switchyard Kiosk (Inside Areas) - GI Switchgear Hall, Panel Room - Bullet/Dome cameras | [10 empty] | 0 | 0
| 6. Entry and Exit of Security Shed cum main gate complex - Bullet cameras | [10 empty] | 0 | 0
| 7. Entry and Exit of FFPH - Bullet cameras | [10 empty] | 0 | 0
| 8. Switchyard areas (All voltage levels) - PTZ Cameras | [10 empty] | 0 | 0
| 9. Transformers and Reactors under present scope- Bullet/PTZ cameras | [10 empty] | 0 | 0
| 10. Substation boundary wall | [10 empty] | 0 | 0
| Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | [10 empty] | 0 | 0
61 | Binoculars Nikon Monarch M7 8X42/Moarch M7 10X42 | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | market rate |  |  | 59000 | 0
62 | Design and Supply of FIRE FIGHTING EQIPMENT: As per TS - (This includes Electric motor driven Main Pump, Jockey Pump-Main and Standby, Diesel engine driven standby Pump, various control & annunciation Panels, Different sizes of MS pipe (to be painted for rust proofing), reducers, different type of valves, pressure gauges, pressure switches, level gauges, level switches, alarms, different type of strainers, Water motor Gong, air vessels, vents, hydrant posts, hydrant valves, hose pipes, QB detectors, HVW spray nozzles, Deluge Valves, Hume pipes, cables and all other equipment/accessories etc. required to complete the Hydrant and HVWS Fire Fighting System.) Hydrant and Mulsifyre system to take care of 2 nos 400/220 KV 500 MVA three phase ICT, 2 Nos 125 MVAR 400 KV three phase Bus Reactor, switchyard equipment, 400KV GIS Hall, 200KV GIS Hall, control room building, LT transformer area, FFPH and Stores. | [10 empty] | 0 | 0
62.1 | HVW spray system, Hydrant system system and complete U/G & O/G piping and accessories etc. outside the pump house for 500 MVA, 400/220/33 kV, 3-phase ICT | Set | 2 | 1540321.39 | 138628.93 | 138628.93 | 1817579.25 | 3635158.5 | BADAKUSHASTHALI 55 |  |  | 3635158.4804 | -0.0196
62.2 | HVW spray system, Hydrant system and complete U/G & O/G piping and accessories etc. outside the pump house for 125MVAR, 400 kV 3- phase Bus Reactor | Set | 2 | 1540321.39 | 138628.93 | 138628.93 | 1817579.25 | 3635158.5 |  |  |  | 3635158.4804 | -0.0196
62.3 | HVW spray system, Hydrant system and complete U/G & O/G piping and accessories etc. outside the pump house for 80MVAR, 400 kV 3- phase LINE Reactor | Set | 2 | 1540321.39 | 138628.93 | 138628.93 | 1817579.25 | 3635158.5 |  |  |  | 3635158.4804 | -0.0196
62.4 | Pumping arrangement for HVW system & hydrant system, complete withall piping, valves, fittings,etc. inside pump house for Fire Protection System of 400/220kV Substation | Set | 1 | 2209267.97 | 198834.12 | 198834.12 | 2606936.21 | 2606936.21 | BADAKUSHASTHALI 53 |  |  | 2606936.2046 | -0.0054
62.5 | Hydrant system, complete piping andaccessories etc, outside the Pump House for Fire Protection of 400/220KV Substation | Set | 1 | 2129694.97 | 191672.55 | 191672.55 | 2513040.07 | 2513040.07 | BADAKUSHASTHALI 54 |  |  | 2513040.0646 | -0.0054
A | TOTAL COST OF SUPPLY FOR SUBSTATION-2A | [6 empty] | 1855915589.8044 |  |  |  | 1855915622.996 | 33.1916
[12 empty] | 0 | 0
B | MADATORY SPARES | [10 empty] | 0 | 0
1 | 420KV, 3000-2000-1000/1A, 63kA, 5 core Single Phase Current Transformer as per TS | NOS | 3 | 564583.56 | 50812.5204 | 50812.5204 | 666208.6008 | 1998625.8024 |  |  |  | 1998625.8024 | 0
2 | 420 KV, 63 kA, 3 Core Single Phase CVT | NOS | 3 | 231050.72 | 20794.5648 | 20794.5648 | 272639.8496 | 817919.5488 |  |  |  | 817919.5488 | 0
3 | 420KV, 3150A, 63KA,SF6 CIRCUIT BREAKER |  |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0
3.1 | SPRING CHARGING MOTOR | NOS | 1 | 12185.3766 | 1096.6839 | 1096.6839 | 14378.7444 | 14378.7444 |  |  |  | 14378.7444 | 0
3.2 | BREKER AUXILIARY CONTACTS | SET | 1 | 4513.5081 | 406.2157 | 406.2157 | 5325.9396 | 5325.9396 |  |  |  | 5325.9396 | 0
3.3 | DENSITY MONITORING SYSTEM | SET | 1 | 16698.8847 | 1502.8996 | 1502.8996 | 19704.6839 | 19704.6839 |  |  |  | 19704.6839 | 0
3.4 | CLOSING COIL | NOS | 4 | 1354.152 | 121.8737 | 121.8737 | 1597.8994 | 6391.5974 |  |  |  | 6391.5974 | 0
3.5 | TRIPPING COIL | NOS | 4 | 1354.152 | 121.8737 | 121.8737 | 1597.8994 | 6391.5974 |  |  |  | 6391.5974 | 0
3.6 | SF6 GAS FILLING DEVICE | NOS | 1 | 22565.5491 | 2030.8994 | 2030.8994 | 26627.3479 | 26627.3479 |  |  |  | 26627.3479 | 0
4 | 336KV Surge Arrester as per TS for 400KV System | NOS | 2 | 150724.122 | 13565.171 | 13565.171 | 177854.464 | 355708.9279 |  |  |  | 355708.9279 | 0
5 | 420 KV, 3000A, 63 KA, HORIZONTAL DOUBLE END BREAK ISOLATORS WITH POST INSULATORS as per TS | [10 empty] | 0 | 0
5.1 | MALE & FEMALE CONTACTS | SET | 4 | 86720.6625 | 7804.8596 | 7804.8596 | 102330.3818 | 409321.527 |  |  |  | 409321.527 | 0
5.2 | LIMIT SWITCH | SET | 2 | 3468.8265 | 312.1944 | 312.1944 | 4093.2153 | 8186.4305 |  |  |  | 8186.4305 | 0
5.3 | ISOLATOR OPERATING MECHANISM BOX | SET | 1 | 15610.165 | 1404.9149 | 1404.9149 | 18419.9947 | 18419.9947 |  |  |  | 18419.9947 | 0
5.4 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1 | 4336.256 | 390.263 | 390.263 | 5116.7821 | 5116.7821 |  |  |  | 5116.7821 | 0
5.5 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1 | 34688.265 | 3121.9438 | 3121.9438 | 40932.1527 | 40932.1527 |  |  |  | 40932.1527 | 0
6 | 420KV 1 phase Solid core bus post insulator (8 kN) (AIS) as per technical specification. | NOS | 6 | 57778.115 | 5200.0303 | 5200.0303 | 68178.1757 | 409069.0542 |  |  |  | 409069.0542 | 0
7 | 245 KV, 1200-600-300 A, 50 KA, 5 core Single Phase Current Transformer (4 Nos PX Class & 1 No. 0.2s Class) | NOS | 3 | 382298.97 | 34406.9073 | 34406.9073 | 451112.7846 | 1353338.3538 |  |  |  | 1353338.3538 | 0
8 | 245 KV, 3CORE, SINGLE PHASE VOLTAGE TRANSFORMER | NOS | 2 | 134349.71 | 12091.4739 | 12091.4739 | 158532.6578 | 317065.3156 |  |  |  | 317065.3156 | 0
9 | 216KV Surge Arrester as per TS for 220KV System | NOS | 3 | 71489.05 | 6434.0145 | 6434.0145 | 84357.079 | 253071.237 |  |  |  | 253071.237 | 0
10 | 245KV, 3150A, 50KA, SF6 CIRCUIT BREAKER WITH SUPPORT STRUCTURE AND AS PER TS | [10 empty] | 0 | 0
10.1 | SPRING CHARGING MOTOR | NOS | 1 | 12185.3766 | 1096.6839 | 1096.6839 | 14378.7444 | 14378.7444 |  |  |  | 14378.7444 | 0
10.2 | BREKER AUXILIARY CONTACTS | SET | 1 | 4513.5081 | 406.2157 | 406.2157 | 5325.9396 | 5325.9396 |  |  |  | 5325.9396 | 0
10.3 | DENSITY MONITORING SYSTEM | SET | 1 | 16698.8847 | 1502.8996 | 1502.8996 | 19704.6839 | 19704.6839 |  |  |  | 19704.6839 | 0
10.4 | CLOSING COIL | NOS | 4 | 1354.152 | 121.8737 | 121.8737 | 1597.8994 | 6391.5974 |  |  |  | 6391.5974 | 0
10.5 | TRIPPING COIL | NOS | 4 | 1354.152 | 121.8737 | 121.8737 | 1597.8994 | 6391.5974 |  |  |  | 6391.5974 | 0
10.6 | SF6 GAS FILLING DEVICE | NOS | 1 | 22565.5491 | 2030.8994 | 2030.8994 | 26627.3479 | 26627.3479 |  |  |  | 26627.3479 | 0
11 | 245 KV, 2000A, 50KA, ISOLATORS WITH POST INSULATORS AS PER TS | [10 empty] | 0 | 0
11.1 | MALE & FEMALE CONTACTS | SET | 4 | 86720.6625 | 7804.8596 | 7804.8596 | 102330.3818 | 409321.527 |  |  |  | 409321.527 | 0
11.2 | LIMIT SWITCH | SET | 2 | 3468.8265 | 312.1944 | 312.1944 | 4093.2153 | 8186.4305 |  |  |  | 8186.4305 | 0
11.3 | ISOLATOR OPERATING MECHANISM BOX | SET | 1 | 15610.165 | 1404.9149 | 1404.9149 | 18419.9947 | 18419.9947 |  |  |  | 18419.9947 | 0
11.4 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1 | 4336.256 | 390.263 | 390.263 | 5116.7821 | 5116.7821 |  |  |  | 5116.7821 | 0
11.5 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1 | 34688.265 | 3121.9438 | 3121.9438 | 40932.1527 | 40932.1527 |  |  |  | 40932.1527 | 0
12 | 245KV, 1 phase solid core Bus Post Insulator (8 kN) (AIS) as per Technical Specification. | NOS | 2 | 30409.9565 | 2736.8961 | 2736.8961 | 35883.7487 | 71767.4973 |  |  |  | 71767.4973 | 0
13 | INSULATORS FOR SUBSTATION | [10 empty] | 0 | 0
13.1 | 160 kN Long Rod Insulator (Porcelain type) for 400 KV | SET | 6 | 12556.3258 | 1130.0693 | 1130.0693 | 14816.4645 | 88898.7868 |  |  |  | 88898.7868 | 0
13.2 | 160 kN Long Rod Insulator (Porcelain type) for 220 KV | SET | 6 | 5058.42 | 455.2578 | 455.2578 | 5968.9356 | 35813.6136 |  |  |  | 35813.6136 | 0
13.3 | 120 kN Long Rod Insulator (Porcelain type) for 400 KV | SET | 6 | 10672.8769 | 960.5589 | 960.5589 | 12593.9948 | 75563.9688 |  |  |  | 75563.9688 | 0
13.4 | 120 kN Long Rod Insulator (Porcelain type) for 220 KV | SET | 6 | 5058.42 | 455.2578 | 455.2578 | 5968.9356 | 35813.6136 |  |  |  | 35813.6136 | 0
14 | ACSR MOOSE CONDUCTOR | MTRS | 1000 | 446.9277 | 40.2235 | 40.2235 | 527.3747 | 527374.6742 |  |  |  | 527374.6742 | 0
15 | Spares for Control & Relay Panels | [10 empty] | 0 | 0
15.1 | 400 KV SIDE | [10 empty] | 0 | 0
15.1.1 | BCU | NOS | 1 | 260639.43 | 23457.5487 | 23457.5487 | 307554.5274 | 307554.5274 |  |  |  | 307554.5274 | 0
15.1.2 | DISTANCE PROTECTION RELAY (MAIN I= 1 No. & MAIN-II = 1 No.) | NOS | 2 | 213250.44 | 19192.5396 | 19192.5396 | 251635.5192 | 503271.0384 |  |  |  | 503271.0384 | 0
15.1.3 | OVER CURRENT & EARTH FAULT RELAY | NOS | 2 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 251635.5192 |  |  |  | 251635.5192 | 0
15.1.4 | MASTER TRIP RELAY | NOS | 2 | 10070.16 | 906.3144 | 906.3144 | 11882.7888 | 23765.5776 |  |  |  | 23765.5776 | 0
15.1.5 | DIFFERENTIAL PROTECTION RELAY (MAIN I= 1 No. & MAIN-II = 1 No.) | NOS | 2 | 236944.94 | 21325.0446 | 21325.0446 | 279595.0292 | 559190.0584 |  |  |  | 559190.0584 | 0
15.1.6 | TRIP CIRCUIT SUPERVISION RELAY | NOS | 4 | 7996.89 | 719.7201 | 719.7201 | 9436.3302 | 37745.3208 |  |  |  | 37745.3208 | 0
15.1.7 | DCCO | SET | 4 | 12125.6346 | 1091.3071 | 1091.3071 | 14308.2488 | 57232.9953 |  |  |  | 57232.9953 | 0
15.1.8 | LBB TRIP RELAY | SET | 2 | 10070.16 | 906.3144 | 906.3144 | 11882.7888 | 23765.5776 |  |  |  | 23765.5776 | 0
15.2 | 220 KV SIDE | [10 empty] | 0 | 0
15.2.1 | BCU | NOS | 1 | 260639.43 | 23457.5487 | 23457.5487 | 307554.5274 | 307554.5274 |  |  |  | 307554.5274 | 0
15.2.2 | DISTANCE PROTECTION RELAY (MAIN I= 1 No. & MAIN-II = 1 No.) | NOS | 2 | 213250.44 | 19192.5396 | 19192.5396 | 251635.5192 | 503271.0384 |  |  |  | 503271.0384 | 0
15.2.3 | OVER CURRENT & EARTH FAULT RELAY | NOS | 1 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 125817.7596 |  |  |  | 125817.7596 | 0
15.2.4 | MASTER TRIP RELAY | NOS | 1 | 10070.16 | 906.3144 | 906.3144 | 11882.7888 | 11882.7888 |  |  |  | 11882.7888 | 0
15.2.5 | TRIP SUPERVISION RELAY | NOS | 2 | 7996.89 | 719.7201 | 719.7201 | 9436.3302 | 18872.6604 |  |  |  | 18872.6604 | 0
15.2.6 | DCCO | SET | 4 | 12125.6346 | 1091.3071 | 1091.3071 | 14308.2488 | 57232.9953 |  |  |  | 57232.9953 | 0
15.2.7 | LBB TRIP RELAY | SET | 2 | 10070.16 | 906.3144 | 906.3144 | 11882.7888 | 23765.5776 |  |  |  | 23765.5776 | 0
15.3 | 33KV SYSTEM | [10 empty] | 0 | 0
15.3.1 | BCU | NOS | 1 | 201403.2 | 18126.288 | 18126.288 | 237655.776 | 237655.776 |  |  |  | 237655.776 | 0
15.3.2 | Backup Relay | NOS | 1 | 106625.22 | 9596.2698 | 9596.2698 | 125817.7596 | 125817.7596 |  |  |  | 125817.7596 | 0
| Total Mandatory Spares | [6 empty] | 10637655.4874 |  |  |  | 10637655.4874 | 0
| Total Supply and Mandatory Spares | [6 empty] | 1866553245.2918 |  |  |  | 1866553278.4834 | 33.1916

## SS ERECTION
ODISHA POWER TRANSMISSION CORPORATION LIMITED
#REF!
(ERECTION SUB-STATION) |  | 400/220kV Substation at Balasore 400 KV Bays-[10 Nos Bays (2 Fdr+ 2 ICT+ 4 Tie+2 Bus Reactor+2 Line Reactor+ 02 unequipped Spare for line FDR)] In 1 & 1/2 CB System, 220KV Bay-[11 Nos. bays (FDR-6,ICT-2, B/C-1, TB/C-1) & 02nos unequipped Spare Bays] In 02 Main Bus & 01 Transfer Bus System
Sl. No. | ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION | UNIT | Quantity | RUPEES IN INR
| DESCRIPTION OF ITEMS(SCHEDULE-2C) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) |  |  | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | AMOUNT | Remarks
[5 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=8x4 | 10
A | ELECTRICAL WORKS
1 | 420KV, 3000-2000-1000/1A, 63kA, 5 core Single Phase Current Transformer as per TS | NOS | 42 | 18885.01 | 1699.6509 | 1699.6509 | 22284.3118 | 935941.0956 | RC SS 10.3 d | 935941.0956 | 0 | 42 |  | 0
2 | 420 KV, 3000A, 63 KA, HORIZONTAL DOUBLE END BREAK ISOLATORS WITH POST INSULATORS as per TS | [8 empty] | 0 | 0
2.1 | WITH ONE EARTH SWITCH | SET | 30 | 36930.68 | 3323.7612 | 3323.7612 | 43578.2024 | 1307346.072 | RC SS 10.3 c | 1307346.072 | 0 | 30 |  | 0
2.2 | WITH TWO EARTH SWITCH | SET | 2 | 36930.68 | 3323.7612 | 3323.7612 | 43578.2024 | 87156.4048 | RC SS 10.3 c | 87156.4048 | 0 | 2 |  | 0
3 | 420 KV, 63 kA, 3 Core Single Phase CVT | NOS | 12 | 18885.01 | 1699.6509 | 1699.6509 | 22284.3118 | 267411.7416 | RC SS 10.3 d | 267411.7416 | 0 | 12 |  | 0
4 | 420KV, 3150A, 63KA,SF6 CIRCUIT BREAKER WITH SUPPORT STRUCTURE AND AS PER TS | [8 empty] | 0 | 0 |  |  | 0
4.1 | CIRCUIT BREAKER WITHOUT CSD | SET | 2 | 131775.37 | 11859.7833 | 11859.7833 | 155494.9366 | 310989.8732 | RC SS 10.3 a | 310989.8732 | 0 | 2 |  | 0
4.2 | CIRCUIT BREAKER WITH CSD | SET | 10 | 131775.37 | 11859.7833 | 11859.7833 | 155494.9366 | 1554949.366 | RC SS 10.3 a | 1554949.366 | 0 | 10 |  | 0
5 | 336KV Surge Arrester as per TS for 400KV System | NOS | 24 | 9232.67 | 830.9403 | 830.9403 | 10894.5506 | 261469.2144 | RC SS 10.3 e | 261469.2144 | 0 | 24 |  | 0
6 | 420KV 1 phase Solid core bus post insulator (8 kN) (AIS) as per technical specification. | NOS | 212 | 5036 | 453.24 | 453.24 | 5942.48 | 1259805.76 | RC SS 10.3 f | 1259805.76 | 0 | 212 |  | 0
7 | 245 KV,(1200-600-300/1-1-1-1-1-1A),50KA,5 CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 18 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 333373.482 | RC SS 10.10 h | 333373.482 | 0 | 30 |  | 12
8 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) | NOS | 12 | 15695.55 | 1412.5995 | 1412.5995 | 18520.749 | 222248.988 | RC SS 10.10 h | 222248.988 | 0 | 24 |  | 12
9 | 245 KV, 2000A, 50KA, ISOLATORS WITH POST INSULATORS AS PER TS | [8 empty] | 0 | 0
9.1 | SINGLE ISOLATOR WITH OUT EARTH SWITCH | SET | 7 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 246811.1128 | RC SS 10.10 b | 246811.1128 | 0 | 11 |  | 4
9.2 | TANDEM ISOLATOR WITH OUT EARTH SWITCH | SET | 10 | 29880.28 | 2689.2252 | 2689.2252 | 35258.7304 | 352587.304 | RC SS 10.10 b | 352587.304 | 0 | 18 |  | 8
9.3 | SINGLE ISOLATOR WITH SINGLE EARTH SWITCH | SET | 6 | 33153.68 | 2983.8312 | 2983.8312 | 39121.3424 | 234728.0544 | RC SS 10.10 d | 234728.0544 | 0 | 10 |  | 4
10 | 245KV, 3150A, 50KA, SF6 CIRCUIT BREAKER WITH SUPPORT STRUCTURE AND AS PER TS | SET | 6 | 97698.43 | 8792.8587 | 8792.8587 | 115284.1474 | 691704.8844 | RC SS 10.10 a | 691704.8844 | 0 | 10 |  | 4
11 | 216KV Surge Arrester as per TS for 220KV System | NOS | 12 | 5203.87 | 468.3483 | 468.3483 | 6140.5666 | 73686.7992 | RC SS 10.10 i | 73686.7992 | 0 | 24 |  | 12
12 | 220 KV Bus Post Insulators | NOS | 100 | 2853.73 | 256.8357 | 256.8357 | 3367.4014 | 336740.14 | RC SS 10.10 j | 336740.14 | 0 | 150 |  | 50
13 | 132KV Circuit Breaker Single Pole for NGR with supporting structures | NOS | 2 | 16786.67 | 1510.8003 | 1510.8003 | 19808.2706 | 39616.5412 | RC SS 10.2 a/3 | 39616.5412 | 0 | 2 |  | 0
14 | 145 KV CT (800-400-200/1-1-1) for NGR | NOS | 2 | 8057.6 | 725.184 | 725.184 | 9507.968 | 19015.936 | RC SS 10.2 f | 19015.936 | 0 | 2 |  | 0
15 | 120KV Surge Arrester as per TS for 132KV System | NOS | 2 | 4532.4 | 407.916 | 407.916 | 5348.232 | 10696.464 | RC SS 10.2 g | 10696.464 | 0 | 2 |  | 0
15B | 30KV Surge Arrester as per TS for 33KV System | NOS | 6 | 1300.96 | 117.0864 | 117.0864 | 1535.1328 | 9210.7968 | RC SS 10.4 i | 9210.7968 | 0 | 6 |  | 0
16 | 72.5 KV, 50-25 A / 1-1 A, 31.5KA for 1 sec, Single Phase Current Transformer as per technical specification | Nos. | 6 | 8057.6 | 725.184 | 725.184 | 9507.968 | 57047.808 | RC SS 10.2 f | 57047.808 | 0 | 6 |  | 0
17 | 72.5kV, 400-200-100 A / 1-1-1-1 A, 31.5KA for 1 sec, Single Phase Current Transformer as per technical specification | Nos. | 6 | 8057.6 | 725.184 | 725.184 | 9507.968 | 57047.808 | RC SS 10.2 f | 57047.808 | 0 | 6 |  | 0
17.1 | 72.5kV, 1250A, 31.5KA Single Isolator with Earth Switch. | Set | 2 | 14058.83 | 1265.2947 | 1265.2947 | 16589.4194 | 33178.8388 | RC SS 10.2 b | 33178.8388 | 0 | 2 |  | 0
17.2 | 72.5 KV, 33KV/√3/110V/√3, 2 CORE(3P,0.2), SINGLE PHASE IVT | Nos. | 6 | 8057.6 | 725.184 | 725.184 | 9507.968 | 57047.808 | RC SS 10.2 f | 57047.808 | 0 | 6 |  | 0
17.3 | 72.5 KV, 1250A, 31.5kA for 3 sec, SF6 Circuit Breaker with supporting GI Structure as per technical specification | Set | 2 | 50360.01 | 4532.4009 | 4532.4009 | 59424.8118 | 118849.6236 | RC SS 10.2 a | 118849.6236 | 0 | 2 |  | 0
18 | 33KV BPI may be used | Nos. | 6 | 1846.53 | 166.1877 | 166.1877 | 2178.9054 | 13073.4324 | RC SS 10.2 h | 13073.4324 | 0 | 6 |  | 0
19 | Conductor Insulation: For use in insulation of ICT Tertiary - Station Transformer (2 SET) bare overhead Conductor. The insulating sleeve and insulation tape shall be Flame, Arc, UV & Ozone Resistant. Shall be rated for 33kV Class insulation. Shall be for outdoor use and shall be made of Silicone/EPR/Polyolefin compound. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | MARKET RATE | 118000 | 0 | 1 |  | 0
20 | BUS BAR STRINGING: Supply of labour, T&P and other necessary arrangements for stringing of bus bar conductors, hoisting of single or double insulator strings, Single or Double Hard-wares Fittings, Clamp & connectors as per requirements, Jumpers, connections to Equipments (except IPS Tube), drops, testing, commissioning etc. as per the instruction of Engineer-in charge. | MTRS | 15000 | 252.05 | 22.6845 | 22.6845 | 297.419 | 4461285 | RC SS 14.00 f | 4461285 | 0
| HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS FOR FOLLOWING ARRANGEMENT: 1. 400KV Bus-A & B and Equipment to Equipment connections are 120mm IPS Aluminium Pipe Bus and shall be for 6 nos of diameters (All "I" type). 2. Cross Bus shall be with Twin ACSR Moose for ICTs and Quad ACSR Moose for Lines and accordingly for the Cross bus to equipment. 3. Cross bus shall be strung for the spare diameters with Quad ACSR moose 3. 220KV Main Bus-I & II, Transfer Bus shall be with twin ACSR Moose (conductor spacing-300mm). 4. 220KV Equipment to Equipments connections shall be 114.2mm IPS Aluminium Tube/ACSR Moose (Twin/single) as per approved drawing. 5. 33/0.4KV Station transformer connections and equipment to equipment connection and ICT Tertiary shall be with ACSR Panther conductor. 6. The hardware fittings shall be of 160KN & 120KN for both 400KV & 220KV system. The UTS of the twin hardware fittings shall be 2x160KN or 2x120KN respectively. 10. The harware fittings shall be single anchored and without turn buckle. 11. This also includes any other hardware fittings and clamps required to complete the work. 12. The qty of hardware fittings, clamps & connectors, Conductor, IPS Aluminium tube and Insulators shall be as per the approved erection key diagram. | [8 empty] | 0 | 0
21 | ACSR Panther Conductor | MTRS | 200 | 184.65 | 16.6185 | 16.6185 | 217.887 | 43577.4 | RC SS 14.00 b | 43577.4 | 0
22 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. including all harrdware fittings | MTRS | 2500 | 451.647 | 40.6482 | 40.6482 | 532.9435 | 1332358.65 | Badakushasthali 23 ( SANCTION ESTIMATE ON DATED 07.02.2025) | 1332358.65 | 0
23 | IPS 4" ALUMINIUM TUBES(OD:114.2 mm & 8.51mm Thickness)( Required for Equipment to equipment connection in 220KV side only) including all hardware fittings | MTRS | 1200 | 451.647 | 40.6482 | 40.6482 | 532.9435 | 639532.152 | Badakushasthali 24 ( SANCTION ESTIMATE ON DATED 07.02.2025) | 639532.152 | 0
24 | Supply of labour,T&P and other necessary arrangements for DESIGN OF SUBSTATION EARTHING SYSTEMS and DSLP, testing,commissioning for the following as per the instruction of Engineer-in charge:- [The Soil resistivity for the substation area is to be measured and approved by OPTCL & The Earth Mat design and layout is to prepared based on the soil resistivity and approved by OPTCL.] (a) Laying of earth-mat conductors of of size 40mm dia Rod, excavation of earth for laying of earth flat as per approved drawing, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors & etc with back filling and good compaction.The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. (b) 40 mm MS solid rod: Provision of grounding driven 40 mm MS Solid rod, (c) 50 mm,3 mtr long Heavy duty perforated GI pipes: for treated earth pits (with details of treatment as per IS). (d) Provision of water taps inside the switch yard areas and peripheral for treated earth pit for watering the treated earth pits. Note: The no. of treated pits are to be done as per the practice and as indicated in the drawing for different equipment. (e) The erection of risers of size 50X6 mm /75X10 mm GI flats including welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc as per requirement. This is as per approved drawing and specification. (f) This includes earthing provision for switchyard buildings. (g) DSLP of Switchyard and its buildings as described below. NOTE: Earthing design and philosophy shall be as per IEEE 80, 81, IS 3043, CBIP Manual on Earthing of AC Power Systems and OPTCL TS. Detail earthing design shall be submitted by the agency considering soil restivity survey. | [8 empty] | 0 | 0
24.1 | EARTHING CONDUCTOR FOR BURRIAL :(40MM MS ROD) for laying as main eartth mat (spacing maximum 5m both way) | Per Mtr | 27890.4665 | 154.35 | 13.8915 | 13.8915 | 182.133 | 5079774.3408 | Badakushasthali 16.1 | 5079774.3408 | 0
24.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | Per Mtr | 11864.4068 | 86.64 | 7.7976 | 7.7976 | 102.2352 | 1212960 | RC SS 21.20 | 1212960 | 0
24.3 | EARTHING CONDUCTOR: 50X6mm GI (HDG) Flat for Raiser for console box,LT panels,DC panels,Marshalling boxes etc) | Per Mtr | 16666.6667 | 86.64 | 7.7976 | 7.7976 | 102.2352 | 1703920 | RC SS 21.20 | 1703920 | 0
24.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) [MORRUM & LATERITE LAYER] | NOS | 600 | 3780.63 | 340.2567 | 340.2567 | 4461.1434 | 2676686.04 | RC SS 21.40 | 2676686.04 | 0
24.5 | Cleats of size 100 mm height, 10 mm thickness, and 75 mm width on both sides for welding of 40mm GI rods at intersection. | LOT | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | MARKET RATE | 236000 | 0
24.6 | 100 Sq mm copper braid for gate earthing. | LOT | 1 | 5000 | 450 | 450 | 5900 | 5900 | MARKET RATE | 5900 | 0
24.7 | Direct Stroke Lightening Protection System as described in supply section. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | MARKET RATE | 118000 | 0
25 | Laying of UPVC Pipes (2", 1.5", 1" & 1/2" etc), Joints, bends, Valves and all accessories for spreading the water network to each treated earth pit as per approved drawing. | LOT | 1 | 100001 | 9000.09 | 9000.09 | 118001.18 | 118001.18 | MARKET RATE | 118001.18 | 0
26 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained. | [8 empty] | 0 | 0
26.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 6000 | 100 | 9 | 9 | 118 | 708000 | Badkushasthali | 708000 | 0
26.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 2500 | 100 | 9 | 9 | 118 | 295000 | Badkushasthali | 295000 | 0
26.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 2000 | 100 | 9 | 9 | 118 | 236000 | Badkushasthali | 236000 | 0
26.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 20 | 10000 | 900 | 900 | 11800 | 236000 | Badkushasthali | 236000 | 0
27 | SWITCH YARD STRUCTURES(including Foundation Bolts and Nuts) GALVANISED (LATTICE) FOR ALL 400 KV, 220 KV & 33KV. The 400KV Columns & Beams shall be designed for Quad ACSR Moose and the 220KV Columns and beams shall be designed for Twin ACSR moose, for WZ-V. The soft copy (AutoCAD, pdf, excel etc.) shall be submitted for the GA, BOM and Shop drawings. | [8 empty] | 0 | 0
27.1 | 400 KV Columns & beams as per approved Layout (6 nos of Diameters of I type) | [8 empty] | 0 | 0
27.2 | 220 KV Column & beams as per approved Layout | Lot | 1 | [6 empty] | 0 | 0
27.5 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 600 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 4126556.76 | RC SS 16.00 | 4126556.76 | 0
28 | Total weight of different size of GI Nuts and bolts for structures. | MT | 60 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 412655.676 | RC SS 16.00 | 412655.676 | 0
29 | SUPPORT STRUCTURES (Including foundation Bolts and Nuts) GALVANISED (PIPE TYPE) FOR ALL 400 KV, 220 kV & 33KV EQUIPMENT INCLUDING NCTs. The Pipe type structures shall be designed for WZ-V. The soft copy (pdf, excel etc.) shall be submitted for the GA, BOM and Shop drawings. | [8 empty] | 0 | 0
29.1 | 400 KV Equipment structures as per approved Layout | Lot | 1 | [6 empty] | 0 | 0
29.2 | 220 KV Equipment structures as per approved Layout | Lot | 1 | [6 empty] | 0 | 0
29.3 | 132KV equipment structures as per approved layout | Lot | 1 | [6 empty] | 0 | 0
| 33Kv equipment structures as per approved layout | Lot | 1 | [6 empty] | 0 | 0
29.4 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 130 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 894087.298 | RC SS 16.00 | 894087.298 | 0
29.5 | Total weight of different size of GI Nuts and bolts for structures. | MT | 35 | 5828.47 | 524.5623 | 524.5623 | 6877.5946 | 240715.811 | RC SS 16.00 | 240715.811 | 0
30 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES | [8 empty] | 0 | 0
30.1 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.) | [8 empty] | 0 | 0
30.1.1 | XLPE 1C X 630 mm2 | MTRS | 3000 | 2284.14 | 205.5726 | 205.5726 | 2695.2852 | 8085855.6 | RC SS 17.20 | 8085855.6 | 0
30.1.2 | XLPE 3.5 CX185 mm2 | MTRS | 1000 | 1732.79 | 155.9511 | 155.9511 | 2044.6922 | 2044692.2 | RC SS 17.20 | 2044692.2 | 0
30.1.3 | XLPE 3.5 CX120 mm2 | MTRS | 1500 | 1023.93 | 92.1537 | 92.1537 | 1208.2374 | 1812356.1 | RC SS 17.20 | 1812356.1 | 0
30.1.4 | PVC 3.5 CX70 mm2 | MTRS | 1500 | 685.24 | 61.6716 | 61.6716 | 808.5832 | 1212874.8 | RC SS 17.20 | 1212874.8 | 0
30.1.5 | PVC 3.5 CX35 mm2 | MTRS | 1500 | 519.83 | 46.7847 | 46.7847 | 613.3994 | 920099.1 | RC SS 17.20 | 920099.1 | 0
30.1.6 | PVC 4 CX 16 mm2 | MTRS | 3000 | 275.67 | 24.8103 | 24.8103 | 325.2906 | 975871.8 | RC SS 17.20 | 975871.8 | 0
30.1.7 | PVC 4 CX 6 mm2 | MTRS | 1000 | 157.53 | 14.1777 | 14.1777 | 185.8854 | 185885.4 | RC SS 17.20 | 185885.4 | 0
30.1.8 | PVC 2CX 6 mm2 | MTRS | 1000 | 126.02 | 11.3418 | 11.3418 | 148.7036 | 148703.6 | RC SS 17.20 | 148703.6 | 0
30.2 | CONTROL CABLES,1.1 KV, PVC ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule) | [8 empty] | 0 | 0
30.2.1 | 4 CX 2.5 mm2 | MTRS | 12000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 780782.4 | RC SS 17.10 | 780782.4 | 0
30.2.2 | 5 CX 2.5 mm2 | MTRS | 13000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 845847.6 | RC SS 17.10 | 845847.6 | 0
30.2.3 | 7CX 2.5 mm2 | MTRS | 4000 | 55.14 | 4.9626 | 4.9626 | 65.0652 | 260260.8 | RC SS 17.10 | 260260.8 | 0
30.2.4 | 10 CX 2.5 mm2 | MTRS | 6500 | 63 | 5.67 | 5.67 | 74.34 | 483210 | RC SS 17.10 | 483210 | 0
30.2.5 | 12 CX 2.5 mm2 | MTRS | 6000 | 63 | 5.67 | 5.67 | 74.34 | 446040 | RC SS 17.10 | 446040 | 0
30.2.6 | 16 CX 2.5 mm2 | MTRS | 5000 | 63 | 5.67 | 5.67 | 74.34 | 371700 | RC SS 17.10 | 371700 | 0
30.2.7 | 19 CX 2.5 mm2 | MTRS | 8000 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 743588.8 | RC SS 17.10 | 743588.8 | 0
30.2.8 | 27 CX 2.5 mm2 | Mtrs | 3000 | 78.77 | 7.09 | 7.09 | 92.95 | 278850 | market rate |  |  |  | 278845.8 | -4.2
30.2.9 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTRS | 500 | 78.77 | 7.0893 | 7.0893 | 92.9486 | 46474.3 | RC SS 17.10 | 46474.3 | 0
31 | Laying of screened / Shielded Twisted pair copper cable for Analog Communication for showing winding temp, Oil temp,lighting, fire fighting, DG etc, LT current & LT voltage signals of sub-station auxiliary system in HMI | [8 empty] | 0 | 0
31.1 | 8PX1.5 mm2 screened copper cable | Mtrs | 1500 | 78.77 | 7.09 | 7.09 | 92.95 | 139425 | RC SS 17.10 | 139422.9 | -2.1
31.2 | 2PX1.5 mm2 screened copper cable | Mtrs | 750 | 78.77 | 7.09 | 7.09 | 92.95 | 69712.5 | RC SS 17.10 | 69711.45 | -1.05
32 | Installation, Testing & Commissioning of OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY | [8 empty] | 0 | 0
32.1 | STATION TRANSFORMER 33KV/433V,1000 KVA (AS PER SPECIFICATION and with 66KV bushings of HV side) | NOS | 2 | 61609.06 | 5544.8154 | 5544.8154 | 72698.6908 | 145397.3816 | RC SS 22.2.6 | 145397.3816 | 0
32.2 | HG Fuse set- for 33kV side of the station transformer including the mounting insulators of 66KV rating, channels complete in all respect (each set comprises three single HG fuse) | SETS | 2 | 75000 | 6750 | 6750 | 88500 | 177000 | LS | 177000 | 0
33 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) | [8 empty] | 0 | 0
33.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | Nos | 250 | 2651.53 | 238.6377 | 238.6377 | 3128.8054 | 782201.35 | RC SS 32.10 | 782201.35 | 0
33.2 | STREET LIGHTING, IT INCLUDES SUPPLY OF GI TUBULAR POLE, WITH LED LIGHTING FIXTURES WITH LAMPS of reputed make (Philips/CGL/Bajaj)(TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos | 100 | 2651.53 | 238.6377 | 238.6377 | 3128.8054 | 312880.54 | RC SS 32.10 | 312880.54 | 0
34 | Air Conditioning System: (As per TS, approved drawings and directions of Engineer-in-Charge.):- 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR CONTROL ROOM, CARRIER ROOM & CONFERENCE ROOM.,OFFICE ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. | [8 empty] | 0 | 0
34.1 | Control Room Building - Control/SAS Room, LT AC/DC Room, Communication room, office rooms, conference room, library, transit/rest room & VRLA battery room | NOS | 28 | 5000 | 450 | 450 | 5900 | 165200 | LS | 165200 | 0
34.2 | AC for Switchyard Kiosk (3 nos per Kiosk) as per T.S (Outdoor type): | NOS | 12 | 5000 | 450 | 450 | 5900 | 70800 | LS | 70800 | 0
34.3 | Air conditioning System for Transit House-Guest rooms & Dining hall | NOS | 8 | 5000 | 450 | 450 | 5900 | 47200 | LS | 47200 | 0
35 | SUBSTATION AUTOMATION SYSTEM FOR 400/220 KV SUBSTATION ON PRP MODE AND INTEGRATION WITH REMOTE CONTROL STATION & SLDC: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS and Integration with Remote Control Station & SLDC as per technical specification. NOTE: All protective relays & BCU shall be numerical type. | [8 empty] | 0 | 0
35.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification) system (for All 220 & 33 KV side bays) and with other accessories, comprising: 1. Gateway (Non-Windows or Linus or Firmware based)- 2 nos with 8 ethernet ports each 2. BCU for Substation Auxilliary System 3. Ethernet Switches (with 20% spares Port) for bay & station level 4. LIU 5. Multimode glass fibre Doublle jacket armoured optical cables 6. Red boxes etc. including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 | 222463.1 | 20021.68 | 20021.68 | 262506.46 | 262506.46 | Badakushasthali 24.1 +24.2+24.3 | 262506.458 | -0.002
| RCC Communication Panel; comprising of: 1. Substation Ethernet Switches (Layer-3 type)- 2 nos 2. Firewall cum Router-2 set 3. Station Data Concentrator (SDC)- 2 nos 5. LIU 6. Multimode glass fibre Doublle jacket armoured optical cables 7. Red boxes etc. 8. Provision for mounting the VMS switch etc including all type of devices & accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system for completeness in all respect for remote communication & as per technical specification. | [8 empty] | 0 | 0
| Operator Workstations -2 nos | [8 empty] | 0 | 0
| Engineering workstation -1 no | [8 empty] | 0 | 0
| Workstation for RAS (Remote Access System) -1 no | [8 empty] | 0 | 0
| Black & whiter Laser jet Printer-1no | [8 empty] | 0 | 0
| Inverters - 3 KVA (Main & Stand by)- 2 nos | [8 empty] | 0 | 0
| Furniture (Operator desk 3 Nos (for SAS, RAS, VMS) & Chair-6Nos) etc. | [8 empty] | 0 | 0
| GPS System with IRIG-B/SNTP/PTP with VDU (Clock)-1 no | [8 empty] | 0 | 0
36 | Erection, Testing and commissioning of 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification. | [8 empty] | 0 | 0
36.1 | 400KV feeder Protection Panel: MAIN-I , MAIN-II Distance protection relays of different make, separate Backup Protection, Bay control unit (BCU), 2nos of DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Nos | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.1224 | RC SS-H- 18.10- (i) | 67348.1224 | 0
36.2 | 400KV Transformer Protection Panel: Differential Protection Main- I & II of different make , Separate REF relay, separate Backup Protection (considering HV, IV & LV side for 500 MVA 400/220/33 KV ICT), Bay control units (BCU), 2nos of DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.1224 | RC SS-H- 18.10- (i) | 67348.1224 | 0
36.3 | 400KV Tie Bay protection Panel: with Bay control unit (BCU), separate backup protection, 2nos of DCCO & other protection & aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 4 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 134696.2448 | RC SS-H- 18.10- (i) | 134696.2448 | 0
36.4 | 400KV BUS-BAR Protection System (Distributed architecture with Main-I & Main-II): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 33674.0612 | RC SS-H- 18.10- (i) | 33674.0612 | 0
36.5 | 400 KV Bus Reactor Panel: With Numerical Backup-Impedance, Differential, Separate REF, separate Back-up protection, Bay Control Unit (BCU), 2nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.1224 | RC SS-H- 18.10- (i) | 67348.1224 | 0
36.6 | 400 KV Line Reactor Panel: with Numerical Backup-Impedance, Differential, separate REF, separate Back-up protection, Bay Control Unit (BCU), 2 nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. Breaker with CSD scheme shall be considered. | NOS | 2 | 28537.34 | 2568.3606 | 2568.3606 | 33674.0612 | 67348.1224 | RC SS-H- 18.10- (i) | 67348.1224 | 0
37 | Erection, Testing and commissioning of 220 KV SIDE PROTECTION & OTHER PANELS | [8 empty] | 0 | 0
37.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, separate Backup Protection relays, Bay control unit (BCU), 2nos DCCO & other protection and aux relays including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 2 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 59424.8236 | RC SS-H- 18.10- (iii) | 59424.8236 | 0
37.2 | 220KV Bus Coupler Protection Panel: BCU, separate Backup Protection Relays and other aux relays, 2nos DCCOs and including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 29712.4118 | RC SS-H- 18.10- (iii) | 29712.4118 | 0
37.3 | 220KV Transfer Bus Coupler Protection Panel: BCU, separate Backup Protection Relays and other aux relays, 2 nos DCCOs and including LBB trip relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 29712.4118 | RC SS-H- 18.10- (iii) | 29712.4118 | 0
37.4 | 220KV BUS-BAR Protection Sysstem (Distributed architecture): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 29712.4118 | RC SS-H- 18.10- (iii) | 29712.4118 | 0
37.5 | 220KV, 500MVA ICT Protection Panel: This includes all Relays (separate backup protection relay, LBB protection etc.) and Bay Control Units (BCU), complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 2 | 25180.01 | 2266.2009 | 2266.2009 | 29712.4118 | 59424.8236 | RC SS-H- 18.10- (iii) | 59424.8236 | 0
38 | Erection, Testing and commissioning of 33 KV SIDE PROTECTION PANELS: Single Panel Twin Bay type ( 2 Bays in One Panel) with IEC:61850-ED2 PRP on FO | [8 empty] | 0 | 0
38.1 | 33KV PROTECTION PANEL (WIth BCU, Separate backup protection relay & with other auxiliary relays, 2 DCCOs for DC as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) for protection of Station transformers. Note: 02 No.s of feeder bays to be considered in one Panel. | Nos | 1 | 19052.88 | 1714.7592 | 1714.7592 | 22482.3984 | 22482.3984 | RC-SS-H-18.10 (vii) | 22482.3984 | 0
39 | AC & DC SYSTEM | [8 empty] | 0 | 0
39.1 | Erection, Testing and commissioning of AC SYSTEM : Indoor Type with 2 mm CRCA sheet and 3 mm CRCA gland plate & as per TS including supply of labour,T&P and other necessary arrangements etc for completion and testing & commissioning of work (as described in supply section) as per the instruction of Engineer-in charge: | [8 empty] | 0 | 0
39.1.1 | MAIN AC DB (Indoor Type): MAIN DB-1, MAIN DB-2 with B/C. The incomer & Bus coupler shall have 800 A, 50KA, drawout type ACB with Numerical SAS compliant Relay (O/C, E/F, U/V, O/V protection). The ACDB shall be suitable for automatic switching OFF & ON during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 10474.88 | 942.7392 | 942.7392 | 12360.3584 | 12360.3584 | RC-SS-H-18.30 | 12360.3584 | 0
39.1.2 | ACDB (Indoor Type) WITH BUS 1, BUS 2, BUS 3, Bus Coupler 1 & Bus Coupler 2: HAVING 400A Motorized MCCB for automatic operation in Incomers and Bus couplers with electrical interlock system. With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected with two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. The ACDB shall be suitable for automatic switching OFF & ON , auto start of DG set etc during power failure. Facilities for integration with SAS as per the site requirement. | SET | 1 | 10474.88 | 942.7392 | 942.7392 | 12360.3584 | 12360.3584 | RC-SS-H-18.30 | 12360.3584 | 0
39.1.3 | Main Lighting Distribution Board (having 250A MCCB as Incomer) as per TS (witc DB-1,DB-2 & B/C) with mechanicla Interlock through castle lock. | SET | 1 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 11686.8852 | RC-SS-H-18.40 | 11686.8852 | 0
39.1.4 | Indoor Lighting Distribution Board as per TS. (WITH DB-1,DB-2 & B/C) | SET | 1 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 11686.8852 | RC-SS-H-18.40 | 11686.8852 | 0
39.1.5 | Emergency Lighting Distribution Board as per specification. | SET | 1 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 11686.8852 | RC-SS-H-18.40 | 11686.8852 | 0
39.1.6 | Indoor Receptacle Board as per Specification | SET | 2 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 23373.7704 | RC-SS-H-18.40 | 23373.7704 | 0
39.1.7 | Outdoor Kiosk For Station Transformer: as per TS with 3 NOS. OF Cut-Outs (1000 Amps) at the Incoming side, 1No. of 3 phase SFU (800 Amps) at the Outgoing and suitable Busbar arrangement for termination of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 9904.14 | 891.3726 | 891.3726 | 11686.8852 | 23373.7704 | RC-SS-H-18.40 | 23373.7704 | 0
39.1.8 | Outdoor Kiosk for Switchyard Lights: as per TS having timer control for switching the lights ON & OFF. | SET | 16 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 57681.6096 | RC-SS-H-18.60 | 57681.6096 | 0
39.1.9 | Ootdoor Kiosk for Colony/Transit House Supply: as per TS | SET | 1 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 3605.1006 | RC-SS-H-18.60 | 3605.1006 | 0
39.1.10 | Outdoor Kiosk for Street Lights: as per TS having timer control for switching the lights ON & OFF. | NOS | 4 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 14420.4024 | RC-SS-H-18.60 | 14420.4024 | 0
39.1.11 | Outdoor Receptacle Board: (Transformer filtration purpose): as per TS | NOS | 2 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 7210.2012 | RC-SS-H-18.60 | 7210.2012 | 0
39.1.12 | Outdoor Receptacle Board: (Welding & other uses) : as per TS | NOS | 7 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 25235.7042 | RC-SS-H-18.60 | 25235.7042 | 0
39.1.13 | Bay Marshalling Kiosk (Outdoor type): as per TS and approved layout (400Kv, 220Kv & 33KV). | Nos | 17 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 61286.7102 | RC-SS-H-18.60 | 61286.7102 | 0
39.1.14 | CT Out Door Console Boxes: As per TS & approved layout (Outdoor type) (400Kv, 220Kv & 33KV). | Nos | 22 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 79312.2132 | RC-SS-H-18.60 | 79312.2132 | 0
39.1.15 | IVT/PT Outdoor Console Boxes: as per TS & approved layout (400Kv, 220Kv & 33KV). | Nos | 8 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 28840.8048 | RC-SS-H-18.60 | 28840.8048 | 0
39.1.16 | ACDB for Yard Kiosk | Nos | 4 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 14420.4024 | RC-SS-H-18.60 | 14420.4024 | 0
40 | Erection, Testing and commissioning of DC SYSTEM including supply of labour,T&P and other necessary arrangements etc for completion and testing & commissioning of work (as described in supply section) as per the instruction of Engineer-in charge: | [8 empty] | 0 | 0
40.1 | 220 V MAIN DCDB in Control Room Building (HAVING DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE protection (with BUS-1, BUS-2 & B/C). Consider separate source(DC1 & DC 2) to each DCDB of Bay Kiosks, local supply of CRB such as emergency lighting, SAS system etc. & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered ( with 20% spare). Incoming and outgoing ratings of MCBs shall be decided as per panel load during detail engineering. The construction shall be as per the TS. | Nos | 1 | 10474.88 | 942.7392 | 942.7392 | 12360.3584 | 12360.3584 | RC-SS-H-18.30 | 12360.3584 | 0
40.2 | 220 V DC Emergency Distribution Board: as per TS | Set | 1 | 10474.88 | 942.7392 | 942.7392 | 12360.3584 | 12360.3584 | RC-SS-H-18.30 | 12360.3584 | 0
40.3 | DCDB for Yard Kiosk (Indoor Type): DC supply to Protection panels having source-1 & 2 with auto changeover facility. Consider separate source (DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output to be considered. | SET | 4 | 3055.17 | 274.9653 | 274.9653 | 3605.1006 | 14420.4024 | RC-SS-H-18.60 | 14420.4024 | 0
41 | Stationary VRLA Battery, 350 Ah (C10 rate) for 220 V DC (Cells: 107 Nos + 3 Nos, 2V Nominal/Cell) as per TS and IS 15549 & IEC 60896-21/22. (The battery shall be capable of giving 1200 or more charge/discharge cycles at 80% DOD at an average temperature of 27º Celsius. The battery sets shall have a minimum expected life of 20 years at float operation.) Agency shall furnish battery sizing calculation, selection of number of cells, float and Boost voltages as per IEEE- 485. Duty cycle for sizing calculation shall be 3h for continious load, 1 hour for emergency load and 1 min for momentary load. | SET | 2 | 19640.41 | 1767.64 | 1767.64 | 23175.69 | 46351.38 | RC-SS-H-20.00 i | 46351.3676 | -0.0124
42 | FLOAT CUM BOOST Battery Charger for offered 350 Ah VRLA Type Battery: Float Charging: 2.13-2.27 V per cell, Boost Charging: 2.28-2.32 V per cell. (FC 35A/ BC 70A) Input from AC Source I & II without automatic selection. Filter circuit shall be provided to limit the ripple content (Peak to Peak) in the output voltage to 1%, irrespective of the DC load level. a. The battery charger shall support both automatic and manual control of output voltage and current, selectable via a mode selector switch. In automatic mode during float charging, the output voltage shall remain within ±1% of the set value under AC input voltage variation of ±10%, frequency variation of ±5%, combined variation of ±10%, and DC load variation from no load to full load. b. Battery chargers shall operate on constant voltage characteristics across the full load range (zero to full load) at float voltage, ensuring the battery remains fully charged without harmful overcharge. c. Load limiters with drooping characteristics shall be provided, which: * Gradually reduce output voltage when the DC load current exceeds the preset limit (in automatic voltage control mode). * Prevent damage or fuse failure during sustained overloads or short circuits in the DC system. * Ensure the charger does not trip under overload or external short circuit conditions. d. Uniform and stepless adjustment of output voltage shall be available in both manual and automatic modes, accessible from the charger’s front panel, covering the entire float voltage range. e. Stepless adjustment of load limiter setting shall also be provided, adjustable from 80% to 100% of the charger's rated output current during charging mode. f. It shall be possible to adjust the Boost charging current continuously over a range of 50 to 100% of the rated output current for Boost charging mode. g. While in Boost mode, the charger output voltage shall rise automatically as the battery charges. A potentiometer shall be provided on the front panel to set the upper voltage limit for Boost mode, adjustable anywhere within the specified output voltage range. [Charger shall be made from CRCA sheet steel-2mm thick, IP 42 rated, Painted: Phosphated-Primer-Painted 50um, ] The Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS. | SET | 2 | 5455.68 | 491.01 | 491.01 | 6437.7 | 12875.4 | RC-SS-H-18.50 | 12875.4048 | 0.0048
43 | Installation and commissioining of 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | Nos | 2 | 2500 | 225 | 225 | 2950 | 5900 | LS | 5900 | 0
44 | Installation and commissioining of Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | Nos | 2 | 3500 | 315 | 315 | 4130 | 8260 | LS | 8260 | 0
46 | Lifting, installation, testing, commissioning of the 250KVA Diesel generator and other accessories required for complete installation in compliance with the Standard applicable, specifications and the manufacturer’s instructions, with all statuatory approvals for 250 KVA outdoor type silent Generator with control panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature, and with Stator CT for differential protection as per Technical spec. Metering CT for DG to be provided with installation of meter as per statutory requirement. Indoor AMF panel with switchgears also included. | Nos. | 1 | 25000 | 2250 | 2250 | 29500 | 29500 | Badakushasthali 33 | 29500 | 0
48 | Installation, Testing and Commissioning of Transformers/Reactors: Receiving, Dragging and installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & Ps. | [8 empty] | 0 | 0
48.1 | 400/220KV,500 MVA ICT & accessories (including the Digital RTCC panels, NIFPES, Online insulating drying out system, Online Dissolve gas analyser, oil storage tank etc) in complete shape as per Technical spec | Nos | 2 | 806346.36 | 72571.17 | 72571.17 | 951488.7 | 1902977.4 | Badakushasthali 34.1 | 1902977.4096 | 0.0096
48.2 | 400 KV, 125 MVAR BUS REACTOR & accessories (including the NIFPES, Online insulating drying out system, Online Dissolve gas analyser etc) in complete shape as per Technical spec: | Nos | 2 | 318865.155 | 28697.86 | 28697.86 | 376260.875 | 752521.75 | Badakushasthali 34.2 | 752521.7658 | 0.0158
48.3 | 400 KV, 80 MVAR LINE REACTOR (Including NGR) & accessories (including the NIFPES, Online insulating drying out system, Online Dissolve gas analyser, oil storage tank etc) in complete shape as per Technical spec: | Nos | 2 | 318866.155 | 28697.95 | 28697.95 | 376262.055 | 752524.11 | Badakushasthali 34.2 | 752524.1258 | 0.0158
49 | FIRE FIGHTING EQIPMENT: As per TS - (This includes Electric motor driven Main Pump, Jockey Pump-Main and Standby, Diesel engine driven standby Pump, various control & annunciation Panels, Different sizes of MS pipe (to be painted for rust proofing), reducers, different type of valves, pressure gauges, pressure switches, level gauges, level switches, alarms, different type of strainers, Water motor Gong, air vessels, vents, hydrant posts, hydrant valves, hose pipes, QB detectors, HVW spray nozzles, Deluge Valves, Hume pipes, cables and all other equipment/accessories etc. required to complete the Hydrant and HVWS Fire Fighting System.) Hydrant and Mulsifyre system to take care of 2 nos 400/220 KV 500 MVA three phase ICT, 2 Nos 125 MVAR 400 KV three phase Bus Reactor,02nos 80MVAR Line Reactors, switchyard equipment, control room building, LT transformer area, FFPH and Stores. | [8 empty] | 0 | 0
49.1 | HVW spray system, Hydrant system system and complete U/G & O/G piping and accessories etc. outside the pump house for 500 MVA, 400/220/33 kV, 3-phase ICT | Set | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | LS | 1180000 | 0
49.2 | HVW spray system, Hydrant system and complete U/G & O/G piping and accessories etc. outside the pump house for 125MVAR, 400 kV 3- phase Bus Reactor | Set | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | LS | 1180000 | 0
49.3 | HVW spray system, Hydrant system and complete U/G & O/G piping and accessories etc. outside the pump house for 80MVAR, 400 kV 3- phase Line Reactor | Set | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | LS | 1180000 | 0
49.4 | Pumping arrangement for HVW system & hydrant system, complete withall piping, valves, fittings,etc. inside pump house for Fire Protection System of 400/220kV Substation | Set | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS | 590000 | 0
49.5 | Hydrant system, complete piping andaccessories etc, outside the Pump House for Fire Protection of 400/220KV Substation | Set | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS | 590000 | 0
50 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 60 | 100 | 9 | 9 | 118 | 7080 | LS | 7080 | 0
51 | INSTALLATION & COMMISSIONING OF ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | [8 empty] | 0 | 0
51.1 | 48 fibre optic approach cable including HDPE pipes | KM | 2 | 74340 | 6690.6 | 6690.6 | 87721.2 | 175442.4 | Badakushasthali 34 | 175442.4 | 0
51.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at Other end 400KV and 220 kV S/s | SET | 14 | 33000 | 2970 | 2970 | 38940 | 545160 | Badakushasthali 34 | 545160 | 0
51.3 | 48V , 500Ah, maintenance free VRLA battery set | NO | 2 | 5795.88 | 521.6292 | 521.6292 | 6839.1384 | 13678.2768 | Badakushasthali 34 | 13678.2768 | 0
51.4 | SMPS based battery charger of 125A suitable for 48V, 500Ah VRLA battery | NO | 2 | 15750 | 1417.5 | 1417.5 | 18585 | 37170 | Badakushasthali 34 | 37170 | 0
51.5 | 48 V DC board (having 100A DC MCCB as incomer, E/F (earth leakage), under & over voltage as per specification (DC DB-1,DC DB-2 & B/C). | SET | 1 | 8190 | 737.1 | 737.1 | 9664.2 | 9664.2 | Badakushasthali 34 | 9664.2 | 0
51.6 | Optical Line Terminal Equipent(OLTE), STM16 type (5 MSP) SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module support upto 150kms ( 02 Nos.) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 150000 | 13500 | 13500 | 177000 | 177000 | Badakushasthali 34 | 177000 | 0
51.7 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 7434 | 669.06 | 669.06 | 8772.12 | 17544.24 | Badakushasthali 34 | 17544.24 | 0
51.8 | Voice gateway 2x(FXS) | Nos | 1 | 15000 | 1350 | 1350 | 17700 | 17700 | LS | 17700 | 0
52 | INSTALLATION & COMMISSIONING OF Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. Description of system as below: | LOT | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | LS | 236000 | 0
54 | INSTALLATION OF OFFICE FURNITURE (GODREJ MAKE) PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,SAS Room etc. | SET | 1 | 10000 | 900 | 900 | 11800 | 11800 | LS | 11800 | 0
55 | INSTALLATION AND PLACEMENT OF FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTEDFIRE EXTINGUSHERS SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC | [8 empty] | 0 | 0
55.1 | FOAM TYPE-9 LTRS | NOS | 20 | 200 | 18 | 18 | 236 | 4720 | LS | 4720 | 0
55.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 4 | 200 | 18 | 18 | 236 | 944 | LS | 944 | 0
55.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 200 | 18 | 18 | 236 | 1416 | LS | 1416 | 0
55.4 | CO2 - 4.5 KGS | NOS | 15 | 200 | 18 | 18 | 236 | 3540 | LS | 3540 | 0
55.5 | CO2 - 9 KGS | NOS | 10 | 200 | 18 | 18 | 236 | 2360 | LS | 2360 | 0
55.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 200 | 18 | 18 | 236 | 944 | LS | 944 | 0
55.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND & CANOPY (3 mm thick) | SET | 6 | 200 | 18 | 18 | 236 | 1416 | LS | 1416 | 0
55.8 | 9 litre water type | Nos. | 6 | 200 | 18 | 18 | 236 | 1416 | LS | 1416 | 0
55.9 | 4.5 kg DCP type | Nos. | 6 | 200 | 18 | 18 | 236 | 1416 | LS | 1416 | 0
56 | 50 Litres Mechanical Foam type | Nos. | 2 | 200 | 18 | 18 | 236 | 472 | LS | 472 | 0
B | TOTAL PRICE FOR THE ERECTION COMPONENT OF THE ELECTRICAL WORKS | [6 empty] | 66205869.803 |  | 65927016.6846 | -278853.1184

## SS ERECTION (hidden)
ODISHA POWER TRANSMISSION CORPORATION LIMITED
(ERECTION SUB-STATION) |  |  | #REF!
400/220/33 kV Substation at Badakushasthali (Gopalpur) 400 KV Bays-[11 Nos (4 Fdr+2 ICT+ 4Tie+1 Reactor)] In 1 & 1/2 CB System, 220KV Bay-10 Nos.(FDR-4,ICT-2+ PTR -2, B/C-1,, TB/C-1) 33KV Bay-8 Nos.(FDR-5,TFR-2, B/C -1]
Sl. No. | ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS(SCHEDULE-2C) ERECTION,TESTING & COMMISSIONING OF FOLLOWING EQUIPMENTS ALONG WITH CIVIL WORKS (As per Technical Specification) | UNIT | Quantity | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | AMOUNT | Remarks
[5 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=8x4 | 10
A | ELECTRICAL WORKS
1 | 420 KV,2000-1000-500A,63 KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 42 | 18576.56 | 1671.8904 | 1671.8904 | 21920.3408 | 920654.3136 | RC SS 1.3 | 920654.3136
2 | 420 KV,4000A,63 KA,ISOLATORS (8 kN) with Post Insulators | [8 empty] | 0
2.1 | WITH ONE EARTH SWITCH | SET | 30 | 36327.47 | 3269.4723 | 3269.4723 | 42866.4146 | 1285992.438 | RC SS 1.3 | 1285992.438
2.2 | WITH TWO EARTH SWITCH | SET | 2 | 36327.47 | 3269.4723 | 3269.4723 | 42866.4146 | 85732.8292 | RC SS 1.3 | 85732.8292
3 | 420 KV, 63 kA, 3 Core Single Phase Line Capacitor Voltage Transformer | NOS | 12 | 18576.56 | 1671.8904 | 1671.8904 | 21920.3408 | 263044.0896 | RC SS 1.3 | 263044.0896
4 | 420KV,4000A,63KA,SF6,CIRCUIT BREAKER WITH SUPPORT STRUCTURE | [8 empty] | 0
4.1 | CIRCUIT BREAKER WITHOUT CSD | SET | 2 | 129623.01 | 11666.0709 | 11666.0709 | 152955.1518 | 305910.3036 | RC SS 1.3 | 305910.3036
4.2 | CIRCUIT BREAKER WITH CSD | SET | 10 | 129623.01 | 11666.0709 | 11666.0709 | 152955.1518 | 1529551.518 | RC SS 1.3 | 1529551.518
5 | Metal oxide polymer housed surge arrrestor for 400 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 24 | 9081.86 | 817.3674 | 817.3674 | 10716.5948 | 257198.2752 | RC SS 1.3 | 257198.2752
6 | 420KV 1 phase Solid core bus post insulator (8 kN) (AIS) as per technical specification. | NOS | 212 | 4953.74 | 445.8366 | 445.8366 | 5845.4132 | 1239227.5984 | RC SS 1.3 | 1239227.5984
7 | 245 KV,(1200-600-300/1-1-1-1-1-1A),40KA,5 CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 18 | 15439.18 | 1389.5262 | 1389.5262 | 18218.2324 | 327928.1832 |  | 327928.1832
8 | 245KV, 3 Core, Single Phase Inductive Volatage Transformer (2 core 3P class & 1 core 0.2 class) (AIS) | NOS | 12 | 15439.18 | 1389.5262 | 1389.5262 | 18218.2324 | 218618.7888 |  | 218618.7888
9 | 245KV, 2000A, 50KA, Isolator (AIS) including post insulators (8 KN) as per TS suitable for SCADA operation | [8 empty] | 0
9.1 | SINGLE ISOLATOR WITH OUT EARTH SWITCH | SET | 7 | 29392.22 | 2645.2998 | 2645.2998 | 34682.8196 | 242779.7372 |  | 242779.7372
9.2 | TANDEM ISOLATOR WITH OUT EARTH SWITCH | SET | 10 | 29392.22 | 2645.2998 | 2645.2998 | 34682.8196 | 346828.196 |  | 346828.196
9.3 | SINGLE ISOLATOR WITH SINGLE EARTH SWITCH | SET | 6 | 32612.16 | 2935.0944 | 2935.0944 | 38482.3488 | 230894.0928 |  | 230894.0928
10 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORT STRUCTURE | SET | 6 | 96102.67 | 8649.2403 | 8649.2403 | 113401.1506 | 680406.9036 |  | 680406.9036
11 | Metal oxide polymer housed surge arrrestor for 220 kV system. Station Class Medium Duty (SM) type In, Ur, Uc, Wth & Qrs as per technical specification/Latest IEC complete with insulating base and Surge monitor (AIS). - As per TS | NOS | 12 | 5118.87 | 460.6983 | 460.6983 | 6040.2666 | 72483.1992 |  | 72483.1992
12 | 220 KV Bus Post Insulators | NOS | 100 | 2807.13 | 252.6417 | 252.6417 | 3312.4134 | 331241.34 |  | 331241.34
13 | 132KV Circuit Breaker Single Pole for NGR with supporting structures | NOS | 2 | 16512.4867 | 1486.1238 | 1486.1238 | 19484.7343 | 38969.4685 |  | 38969.4685
14 | 145 KV CT (800-400-200/1-1-1) for NGR | NOS | 2 | 7925.99 | 713.3391 | 713.3391 | 9352.6682 | 18705.3364 |  | 18705.3364
15 | 36 KV CLASS NCT FOR TRANSFORMER PROTECTION (2000-1000-500/1-1, ) , HAVING TWO CORE OF PS CLASS (IN EACH ICT 2 No. NCT, IN EACH PTR 2 No. OF NCT ) | NOS | 9 | 2559.44 | 230.3496 | 230.3496 | 3020.1392 | 27181.2528 |  | 27181.2528
16 | 36 KV,800-400-200,25KA,3CORE/4 CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 24 | 2559.44 | 230.3496 | 230.3496 | 3020.1392 | 72483.3408 |  | 72483.3408
17 | 36 KV,800A,25KA,ISOLATORS | [8 empty] | 0
17.1 | S/I WITH OUT EARTH SWITCH | SET | 2 | 6605 | 594.45 | 594.45 | 7793.9 | 15587.8 |  | 15587.8
17.2 | S/I WITH SINGLE EARTH SWITCH | SET | 6 | 6605 | 594.45 | 594.45 | 7793.9 | 46763.4 |  | 46763.4
17.3 | S/I WITH BEAM MOUNTED | SET | 2 | 5449.12 | 490.4208 | 490.4208 | 6429.9616 | 12859.9232 |  | 12859.9232
18 | 30 KV, METAL OXIDE SURGE ARRESTOR, 10KA, class II | NOS | 6 | 1155.87 | 104.0283 | 104.0283 | 1363.9266 | 8183.5596 |  | 8183.5596
19 | 36 KV ,2 CORE,SINGLE PHASE,IVT | NOS | #REF! | 2311.75 | 208.0575 | 208.0575 | 2727.865 | #REF! |  | #REF!
20 | 36KV,1250A,25KA,VACUUM CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | SET | #REF! | 23777.98 | 2140.0182 | 2140.0182 | 28058.0164 | #REF! |  | #REF!
21 | 33 KV Bus Post Insulators | NOS | #REF! | 643.99 | 57.9591 | 57.9591 | 759.9082 | #REF! |  | #REF!
22 | BUS BAR & CIRCUIT MATERIALS | [8 empty] | 0
22.1 | 160 kN Long Rod Insulator (Polymer type) for twin Moose cond (Double TENSION)-400 KV | SET | 300 | [6 empty] | 0
22.2 | 160 kN Long Rod Insulator (Polymer type) for twin Moose cond (Double TENSION)-220 KV | SET | 250 | [6 empty] | 0
22.3 | 120 kN Long Rod Insulator (Polymer type) for Twin Moose cond (SUSPENSION)-400 KV | SET | 120 | [6 empty] | 0
22.4 | 120 kN Long Rod Insulator (Polymer type) for Twin Moose cond ( SUSPENSION)-220 KV | SET | 100 | [6 empty] | 0
22.5 | 120 KNLong Rod Porcelain INSULATOR(33KV Side) | SET | #REF! | [6 empty] | #REF!
22.6 | 90 KNLong Rod Porcelain INSULATOR(33KV Side) | SET | #REF! | [6 empty] | #REF!
23 | BUS BAR (INCLUDING CROSS BUS, DROPS etc. ) stringing withh fixing of insulator string (ACSR TWIN MOOSE CONDUCTOR WITH THE ABOVE ACCESSORIES IN COMPETE ) including all hardware fittings | MTRS | 15000 | 247.93 | 22.3137 | 22.3137 | 292.5574 | 4388361 |  | 4388361
24 | ACSR Panther Conductor | MTRS | 200 | 181.64 | 16.3476 | 16.3476 | 214.3352 | 42867.04 |  | 42867.04
25 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. including all harrdware fittings | MTRS | 2500 | 451.647 | 40.6482 | 40.6482 | 532.9435 | 1332358.65 | Badakushasthali 23 ( SANCTION ESTIMATE ON DATED 07.02.2025) | 1332358.65
26 | IPS 4" ALUMINIUM TUBES(OD:114.2 mm & 8.51mm Thickness)( Required for Equipment to equipment connection in 220 KV side only) including all hardware fittings | MTRS | 1200 | 451.647 | 40.6482 | 40.6482 | 532.9435 | 639532.152 | Badakushasthali 24 ( SANCTION ESTIMATE ON DATED 07.02.2025) | 639532.152
27 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT | 1 | 336495 | 30284.55 | 30284.55 | 397064.1 | 397064.1 |  | 397064.1
28 | SUBSTATION EARTHING SYSTEMS | [8 empty] | 0
28.1 | EARTHING CONDUCTOR FOR BURRIAL :(40MM MS ROD) for laying as main eartth mat (spacing maximum 5m both way) | Per Mtr | 27890.4665 | 154.35 | 13.8915 | 13.8915 | 182.133 | 5079774.3408 | Badakushasthali 16.1 | 5079774.3408
28.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | Per Mtr | 11864.4068 | 85.22 | 7.6698 | 7.6698 | 100.5596 | 1193080 | RC Page 18 (1.2 v b) | 1193080
28.3 | EARTHING CONDUCTOR: 50X6mm GI (HDG) Flat for Raiser for console box,LT panels,DC panels,Marshalling boxes etc) | Per Mtr | 16666.6667 | 85.22 | 7.6698 | 7.6698 | 100.5596 | 1675993.3333 | RC Page 18 (1.2 v b) | 1675993.3333
28.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 600 | 2944.11 | 264.9699 | 264.9699 | 3474.0498 | 2084429.88 | RC Page 18 (1.3 ii) | 2084429.88
28.5 | Cleats of size 100 mm height, 10 mm thickness, and 75 mm width on both sides for welding of 40mm GI rods at intersection. | LOT | 1 | 200000 | 18000 | 18000 | 236000 | 236000
28.6 | 100 Sq mm copper braid for gate earthing. | LOT | 1 | 5000 | 450 | 450 | 5900 | 5900
28.7 | Direct Stroke Lightening Protection System: (As per TS, approved drawings and directions of Engineer-in-Charge.) using IEC 62305 / Razevig method / National Building Code. The scope includes design and supply of all materials (excluding switchyard columns and lighting cum lightning mast) for DSLP of entire switchyard area under present scope, all buildings, ICT and reactors. Includes all materials such as Shield wires, Horizontal Conductor, Down conductor, Droppers, Earth electrodes, Test link, Cleats, lugs, Air termination rods/ Lightning spike, PG Clamp, D Shackle. etc. and all other accessories to complete the system in full shape. Earthing of the DSLP system is included in the scope. | LOT | 1 | 100000 | 9000 | 9000 | 118000 | 118000
28.8 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained.
28.8.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 500 | 80 | 7.2 | 7.2 | 94.4 | 47200
28.1.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 1750 | 80 | 7.2 | 7.2 | 94.4 | 165200
28.8.2 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 1250 | 80 | 7.2 | 7.2 | 94.4 | 118000
28.1.3 | Support G. I angle 50x50x6 mm for cable tray | MT | 13 | 10000 | 900 | 900 | 11800 | 153400
29 | SWITCH YARD STRUCTURES (including Foundation Bolts and Nuts) GALVANISED (LATTICE) FOR ALL 400 KV, 220 KV & 33KV The 400KV & 220KV Column & Beams shall be designed for Quad ACSR Moose & Wind Zone-VI. The 33KV Column & beams shall be the existing design OPTCL design. | [8 empty] | 0
29.1 | 400 KV Columns & beams as per approved Layout | [8 empty] | 0
29.2 | 220 KV Column & beams as per approved Layout | Lot | 1 | [6 empty] | 0
29.3 | 33 KV Column & beams as per approved Layout | Lot | 1 | [6 empty] | 0
29.4 | Structures for NCTs for ICTs, Power TFRs, 132KV CT for NGR) | Lot | 1 | [6 empty] | 0
29.5 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 600 | [6 empty] | 0
29.6 | Total weight of different size of GI Nuts and bolts for structures. | MT | 60 | [6 empty] | 0
30 | SUPPORT STRUCTURES (Including foundation Bolts and Nuts) GALVANISED (PIPE TYPE) FOR ALL 400 KV, 220 kV & 33KV EQUIPMENT INCLUDING NCTs. The Pipe type structures shall be designed for Wind Zone- VI. | [8 empty] | 0
30.1 | 400 KV Equipment as per approved Layout | Lot | 1 | [6 empty] | 0
30.2 | 220 KV Equipment as per approved Layout | Lot | 1 | [6 empty] | 0
30.3 | 33 KV Equipment as per approved Layout | Lot | 1 | [6 empty] | 0
30.4 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 130 | 5733.2673 | 515.9941 | 515.9941 | 6765.2554 | 879483.2054 | RC Page 14 (3.10) | 879483.2054
30.5 | Total weight of different size of GI Nuts and bolts for structures. | MT | 35 | 5733.2673 | 515.9941 | 515.9941 | 6765.2554 | 236783.9399 | RC Page 14 (3.10) | 236783.9399
30.6 | Total weight of different size of GI Nuts and bolts for structures. | MT | 85 | 5733.2673 | 515.9941 | 515.9941 | 6765.2554 | 575046.7112 | RC Page 14 (3.10) | 575046.7112
31 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES | [8 empty] | 0
31.1 | POWER CABLES, 1.1KV, XLPE & PVC, ARMOURED, FRLSH, ALUMINIUM CONDUCTOR (As per Specification) including Power cable termination, all accessories & other materials - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule, based on which material shall be supplied and measurement will be done.) | [8 empty] | 0
31.1.1 | XLPE 3.5 CX630 mm2 | MTRS | 3000 | 2246.83 | 202.2147 | 202.2147 | 2651.2594 | 7953778.2 | RC Page 15 (1.2 xiv) | 7953778.2
31.1.2 | XLPE 3.5 CX185 mm2 | MTRS | 1000 | 1704.4849 | 153.4036 | 153.4036 | 2011.2922 | 2011292.1536 | RC Page 15 (1.2 xii) | 2011292.1536
31.1.3 | XLPE 3.5 CX120 mm2 | MTRS | 1500 | 1007.2025 | 90.6482 | 90.6482 | 1188.4989 | 1782748.3725 | RC Page 15 (1.2 x) | 1782748.3725
31.1.4 | PVC 3.5 CX70 mm2 | MTRS | 1500 | 674.0484 | 60.6644 | 60.6644 | 795.3771 | 1193065.5802 | RC Page 15 (1.2 viii) | 1193065.5802
31.1.5 | PVC 3.5 CX35 mm2 | MTRS | 1500 | 511.3413 | 46.0207 | 46.0207 | 603.3828 | 905074.1819 | RC Page 15 (1.2 vi) | 905074.1819
31.1.6 | PVC 4 CX 16 mm2 | MTRS | 3000 | 271.1646 | 24.4048 | 24.4048 | 319.9742 | 959922.7461 | RC Page 15 (1.2 iv) | 959922.7461
31.1.7 | PVC 4 CX 6 mm2 | MTRS | 1000 | 154.9532 | 13.9458 | 13.9458 | 182.8447 | 182844.7412 | RC Page 15 (1.2 ii) | 182844.7412
31.1.8 | PVC 2CX 6 mm2 | MTRS | 1000 | 123.97 | 11.1573 | 11.1573 | 146.2846 | 146284.6 | RC | 146284.6
31.2 | CONTROL CABLES,1.1 KV, PVC ARMOURED, FRLSH, Stranded Copper (As per specification) including control cable termination & other materials. - (Below quanity is only indicative, actual quantity shall be as per approved cable schedule) | [8 empty] | 0
31.2.1 | 4 CX 2.5 mm2 | MTRS | 12000 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 767977.0621 | RC Page 15 (1.1 iii) | 767977.0621
31.2.2 | 5 CX 2.5 mm2 | MTRS | 13000 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 831975.1506 | RC Page 15 (1.1 iii) | 831975.1506
31.2.3 | 7CX 2.5 mm2 | MTRS | 4000 | 54.2357 | 4.8812 | 4.8812 | 63.9981 | 255992.354 | RC Page 15 (1.1 iii) | 255992.354
31.2.4 | 10 CX 2.5 mm2 | MTRS | 6500 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 475354.2232 | RC Page 15 (1.1 vi) | 475354.2232
31.2.5 | 12 CX 2.5 mm2 | MTRS | 6000 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 438788.5137 | RC Page 15 (1.1 vi) | 438788.5137
31.2.6 | 16 CX 2.5 mm2 | MTRS | 5000 | 61.9758 | 5.5778 | 5.5778 | 73.1314 | 365657.0948 | RC Page 15 (1.1 vi) | 365657.0948
31.2.7 | 19 CX 2.5 mm2 | MTRS | 8000 | 77.4834 | 6.9735 | 6.9735 | 91.4305 | 731443.7404 | RC Page 15 (1.1 ix) | 731443.7404
31.2.8 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | MTRS | 500 | 66 | 5.94 | 5.94 | 77.88 | 38940 | Badakushasthali 19.2.8 | 38940
32 | Installation, Testing & Commissioning of 220/33 KV, 20 MVA Power & all accessories | [8 empty] | 0
32.1 | STATION TRANSFORMER 33KV/433V,1000 KVA (AS PER SPECIFICATION) | NOS | 2 | 60242.3727 | 5421.8135 | 5421.8135 | 71085.9998 | 142171.9996 | RC Page 21 (1.2.6 iv) | 142171.9996
32.2 | 33 KV AB SWITCH IN 33 KV SIDE(400AMP),HG FUSE, DP STRUCTURE(preferably by using 200X100 mm RS Joist),ANGLE FOR BRACING OF DP STRUCTURE,POWER CABLES, CHANEL, FOR ERECTION OF TRANSFORMER INCLUDING INSULATORS, CONDUCTOR, CLAMPS & CONNECTOR, JUMPERING AND OTHER ACCESSORIES FOR COMMISSIONING OF THE STN TRANSFORMER.IT INCLUDES LT OUT DOOR KIOSK MADE OUT OF 14 SWG GI MARSH-ALLING BOX OR BETTER , HAVING CABLE TERMINATING FACILITY FOR INCOMING & OUT GOING TO THE BOX. THE RATING OF THE BUS BAR, TERMINAL BOX & STUDS TO BE USED SHALL HAVE CONTINEOUS RATING OF 2000 AMP. MARSHALLING BOXES ARE TO BE INSTALLED NEAR TO THE AUXILIARY STATION TRANSFORMERS. | SETS | 2 | 75000 | 6750 | 6750 | 88500 | 177000 | LS | 177000
33 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) | [8 empty] | 0
33.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | Nos | 450 | 2592.71 | 233.3439 | 233.3439 | 3059.3978 | 1376729.01 | RC Page 23 (10.1) | 1376729.01
33.2 | STREET LIGHTING, IT INCLUDES SUPPLY OF GI TUBULAR POLE, WITH LED LIGHTING FIXTURES WITH LAMPS of reputed make (Philips/CGL/Bajaj)(TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos | 50 | 2219.6 | 199.764 | 199.764 | 2619.128 | 130956.4 | Badakushasthali 21.2 | 130956.4
34 | Air Conditioning System: (As per TS, approved drawings and directions of Engineer-in-Charge.):- 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR CONTROL ROOM, CARRIER ROOM & CONFERENCE ROOM.,OFFICE ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. | [8 empty] | 0
34.1 | Control Room Building - Control/SAS Room, LT AC/DC Room, Communication room, office rooms, conference room, library, transit/rest room & VRLA battery room | NOS | 20 | 5000 | 450 | 450 | 5900 | 118000 | LS
34.2 | Bay Marshalling Kiosk (Outdoor type): as per TS | NOS | 20 | 5000 | 450 | 450 | 5900 | 118000 | LS
34.3 | Air conditioning System for Transit House-Guest rooms & Dining hall | NOS | 8 | 5000 | 450 | 450 | 5900 | 47200 | LS
35 | SUBSTATION AUTOMATION SYSTEM FOR 400/220/33 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 400, 220 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type. | [8 empty] | 0
35.1 | Gateway Panel: for Sub-Station Automation (in PRP on FO as per the specification & indicative drawing) system (for All 400KV, 220KV & 33 KV side bays) and with other accessories, comprising: 1. HMI servers (Main & Stand By) for Local and only Main for Remote (3 sets) 2. DR PC for Local & Remote- 2 sets 3. Gateway- 2 nos (both in hot mode) 4. Color Laser jet Printer-1Nos 5. Dot Matrix Printer-1Nos 6. Ethernet Fiber Switches (with 20% spares Port) 7. LIU 8. Multimode glass fibre Doublle jacket armoured optical cables 9. Red boxes 10. Inverters(Input shall be both A.C & D.C and output shall be A.C) - 3 KVA (Main & Stand by) for local & remote- 3 nos 11. Furniture (Operator desk 1 Nos & Chair-6Nos) for local, (Operator desk & 2 chairs) for Remote 12.Full HD LED TV (Sony, LG, Samsung) for display etc as per TS, including all type of accessories & special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system complete in all respect as per latest IEC 61850- ED-2 standard & as per technical specification. | SET | 1 | 181463.1 | 16331.679 | 16331.679 | 214126.458 | 214126.458 | Badakushasthali 24.1 | 214126.458
35.2 | BCU for Substation Auxilliary System (Station AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) | LOT | 1 | 21000 | 1890 | 1890 | 24780 | 24780 | Badakushasthali 24.2 | 24780
35.3 | GPS System with IRIG-B/SNTP/PTP with VDU (Clock) | Nos. | 1 | 20000 | 1800 | 1800 | 23600 | 23600 | Badakushasthali 24.3 | 23600
36 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification. | [8 empty] | 0
36.1 | 400KV feeder Protection Panel: MAIN-I , MAIN-II Distance protection relays of different make & Backup Protection with Bay control unit (BCU) & other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | Nos | 2 | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | 66248.0947 | RC-H- 1.10- (i) | 66248.0947
36.2 | 400KV Transformer Protection Panel: Differential Protection Main- I & II of different make , Separate REF- Main- I & II (different make) & BACK-UP PROTECTION for HV & IV side (considering HV, IV & LV side for 500 MVA 400/220/33 KV ICT) with Bay control units (BCU) & other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 2 | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | 66248.0947 | RC-H- 1.10- (i) | 66248.0947
36.3 | 400KV Tie Bay protection Panel: with Bay control unit (BCU), other protection & aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 4 | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | 132496.1893 | RC-H- 1.10- (i) | 132496.1893
36.4 | 400KV BUS-BAR Protection System (Distributed architecture with Main-I & Main-II): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | 33124.0473 | RC-H- 1.10- (i) | 33124.0473
36.5 | 400 KV Bus Reactor Panel: With Numerical Backup-Impedance, Differential, Separate REF & Back-up protection & Bay Control Unit (BCU) & aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 2 | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | 66248.0947 | RC-H- 1.10- (i) | 66248.0947
36.6 | 400 KV Line Reactor Panel: with Numerical Backup-Impedance, Differential, REF & Back-up protection & Bay Control Unit (BCU) & aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | #REF! | 28071.2265 | 2526.4104 | 2526.4104 | 33124.0473 | #REF! | RC-H- 1.10- (i) | #REF!
37 | 220 KV SIDE PROTECTION & OTHER PANELS | [8 empty] | 0
37.1 | 220KV Feeder Protection Panel: MAIN-I , MAIN-II of different make, Backup Protection relays, Bay control unit (BCU) & other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC, for substation automation system. | NOS | 2 | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | 58454.2012 | RC-H- 1.10- (iii) | 58454.2012
37.2 | 220KV Bus Coupler Protection Panel: Backup Protection Relays and other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | 29227.1006 | RC-H- 1.10- (iii) | 29227.1006
37.3 | 220KV Transfer Bus Coupler Protection Panel: Backup Protection Relays and other aux relays as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | 1 | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | 29227.1006 | RC-H- 1.10- (iii) | 29227.1006
37.4 | 220KV BUS-BAR Protection Sysstem (Distributed architecture): This includes all peripheral units, Relays, Panels & other accessories complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. Provision of bus bar modules for at least Four future bays shall be made. The bus bar protection system shall be integrated with the Automation system. | LOT | 1 | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | 29227.1006 | RC-H- 1.10- (iii) | 29227.1006
37.5 | 220KV, 500MVA ICT Protection Panel: This includes all Relays and Bay Control Units (BCU), complete in all respect compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC. | NOS | 2 | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | 58454.2012 | RC-H- 1.10- (iii) | 58454.2012
37.6 | 220KV, 20MVA Power Transformer Protection Panel: Differential, saparate numerical REF, Backup Protection and other aux relays with Bay control units (BCU) as per requirement compliant to IEC 61850-ED-2 protocol with PRP on FO. Power Supply 220V DC for substation automation system. | NOS | #REF! | 24768.7293 | 2229.1856 | 2229.1856 | 29227.1006 | #REF! | RC-H- 1.10- (iii) | #REF!
38 | 33 KV SIDE PROTECTION PANELS: Single Panel Twin Bay type ( 2 Bays in One Panel) with IEC:61850-ED2 PRP on FO | [8 empty] | 0
38.1 | FEEDER PROTECTION PANEL (WIth BCPU & with other auxiliary relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) POWER TRANSFORMER PROTECTION PANEL (WIth BCPU & separate numerical REF and other auxiliary relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) BUS COUPLER PROTECTION RELAY PANEL WIth BCPU & with other auxiliary relays as required as per the scheme complaint to IEC 61850-ED-2 rpotocol with PRP on FO, Power supply: 220V DC.) Note: 05 No.s of Line feeder bays, 2 transformer bays & one Bus Coupler bay panel to be considered in 04 panels. | Nos | 4 | 18741.68 | 1686.7512 | 1686.7512 | 22115.1824 | 88460.7296 | RC-H- 1.10- (vii) | 88460.7296
39 | AC & DC SYSTEM | [8 empty] | 0
39.1 | AC SYSTEM | [8 empty] | 0
39.1.1 | MAIN AC DB,(HAVING A 1600 A,50KA,DRAWOUT TYPE ACB WITH Numerical protective relay for O/C , E/F, UV, OV etc FACILITY and MECH & ELECT INTERLOCK FACILITY.(MAIN DB-1,MAIN DB-2 WITH B/C). The outgoing of the station Transformers shall be the two incomers for the Mian ACDB. The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% / at least 1 no. (whichever is higher) spares of each rating feeder. The cosntruction of the Main ACDB shall be as per the TS. | SET | 1 | 7307.17 | 657.6453 | 657.6453 | 8622.4606 | 8622.4606 | Badakushasthali 28.1.1 | 8622.4606
39.1.2 | ACDB (HAVING 800A MCCB in Incomer and Bus couplers with electrical interlock system) AS PER SPECIFICATION (With Three Bus sections and Two nos of Bus couplers. Two bus sections shall be connected from two bus sections of the Main ACDB and the 3rd bus section shall be connected to the DG having all emergency loads.). The outgoing feeders for the Main ACDB shall be appropriately designed to cater all loads having 20% spares of each rating feeder in each section. The cosntruction of the ACDB shall be as per the TS. | SET | 1 | 7307.1705 | 657.6453 | 657.6453 | 8622.4612 | 8622.4612 | Badakushasthali 28.1.2 | 8622.4612
39.1.3 | Main Lighting Distribution Board (having 250A MCCB as Incomer) as per TS (witc DB-1,DB-2 & B/C) | SET | 1 | 7307.1705 | 657.6453 | 657.6453 | 8622.4612 | 8622.4612 | Badakushasthali 28.1.3 | 8622.4612
39.1.4 | Indoor Lighting Distribution Board as per TS. (WITH DB-1,DB-2 & B/C) | SET | 1 | 7307.1705 | 657.6453 | 657.6453 | 8622.4612 | 8622.4612 | Badakushasthali 28.1.4 | 8622.4612
39.1.5 | Emergency Lighting Distribution Board as per specification. | SET | 1 | 7307.1705 | 657.6453 | 657.6453 | 8622.4612 | 8622.4612 | Badakushasthali 28.1.5 | 8622.4612
39.1.6 | Indoor Receptacle Board as per Specification | SET | 2 | 7307.1705 | 657.6453 | 657.6453 | 8622.4612 | 17244.9224 | Badakushasthali 28.1.6 | 17244.9224
39.1.7 | Outdoor Kiosk For Station Transformer: as per TS with 3 NOS. OF Cut-Outs (1000 Amps) at the Incoming side, 1No. of 3 phase SFU (1000 Amps) at the Outgoing and suitable Busbar arrangement for termination of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 8673 | 780.57 | 780.57 | 10234.14 | 20468.28 | Badakushasthali 28.1.7 | 20468.28
39.1.8 | Outdoor Kiosk for Switchyard Lights: as per TS having timer control for switching the lights ON & OFF. | SET | 16 | 5900 | 531 | 531 | 6962 | 111392 | Badakushasthali 28.1.8 | 111392
39.1.9 | Ootdoor Kiosk for Colony/Transit House Supply: as per TS | SET | 1 | 5900 | 531 | 531 | 6962 | 6962 | Badakushasthali 28.1.9 | 6962
39.1.10 | Outdoor Kiosk for Street Lights: as per TS having timer control for switching the lights ON & OFF. | NOS | 4 | 5900 | 531 | 531 | 6962 | 27848 | Badakushasthali 28.1.10 | 27848
39.1.11 | Outdoor Receptacle Board: (Transformer filtration purpose): as per TS | NOS | 3 | 2037 | 183.33 | 183.33 | 2403.66 | 7210.98 | Badakushasthali 28.1.11 | 7210.98
39.1.12 | Outdoor Receptacle Board: (Welding & other uses) : as per TS | NOS | 7 | 2037 | 183.33 | 183.33 | 2403.66 | 16825.62 | Badakushasthali 28.1.12 | 16825.62
39.1.13 | Bay Marshalling Kiosk (Outdoor type): as per TS, (10 nos on 220 kV bay, 10 Nos for 400 kv bays, 3 Nos for 33KV bays ) | Nos | 23 | 6601 | 594.09 | 594.09 | 7789.18 | 179151.14 | Badakushasthali 28.1.13 | 179151.14
39.1.14 | CT Out Door Console Boxes: As per TS, ( 400KV CT-20 Nos, 220KV CT: 10 Nos, 33 KV CT-9 Nos) (Outdoor type) | Nos | 39 | 2037 | 183.33 | 183.33 | 2403.66 | 93742.74 | Badakushasthali 28.1.14 | 93742.74
39.1.15 | PT Outdoor Console Boxes: as per TS, (400 KV : 4 Nos , 220KV: 6 Nos, 33KV PT-01 No) | Nos | 11 | 2037 | 183.33 | 183.33 | 2403.66 | 26440.26 | Badakushasthali 28.1.14 | 26440.26
39.1.16 | ACDB for Yard Kiosk | Nos | 7 | 2037 | 183.33 | 183.33 | 2403.66 | 16825.62 | Badakushasthali 28.1.14 | 16825.62
40 | DC SYSTEM (suitable for SAS operation) | [8 empty] | 0
40.1 | 220 V MAIN DCDB in Control Room Building (HAVING DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE protection (with BUS-1, BUS-2 & B/C). Consider separate source(DC1 & DC 2) to each DCDB of GIS buildings, DCDB of Bay Kiosks, local supply of CRB such as emergency lighting, SAS system etc. & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered ( with 20% spare). Incoming and outgoing ratings of MCBs shall be decided as per panel load during detail engineering. The construction shall be as per the TS. | Nos | 1 | 7724.85 | 695.2365 | 695.2365 | 9115.323 | 9115.323 | Badakushasthali 29.1 | 9115.323
40.2 | 220 V DC Emergency Distribution Board: as per TS | Set | 1 | 7703.3 | 693.297 | 693.297 | 9089.894 | 9089.894 | Badakushasthali 29.2 | 9089.894
40.3 | DCDB for Yard Kiosk | Nos | 7 | 2037 | 183.33 | 183.33 | 2403.66 | 16825.62 | Badakushasthali 28.1.14 | 16825.62
41 | Stationary VRLA Battery, 800 Ah (C10 rate) for 220 V DC (Cells: 107 Nos + 3 Nos, 2V Nominal/Cell) as per TS and IS 15549 & IEC 60896-21/22. (The battery shall be capable of giving 1200 or more charge/discharge cycles at 80% DOD at an average temperature of 27º Celsius. The battery sets shall have a minimum expected life of 20 years at float operation.) Agency shall furnish battery sizing calculation, selection of number of cells, float and Boost voltages as per IEEE- 485. Duty cycle for sizing calculation shall be 3h for continious load, 1 hour for emergency load and 1 min for momentary load. | SET | 2 | 19319.6089 | 1738.76 | 1738.76 | 22797.1289 | 45594.2577 | Badakushasthali 30 | 45594.2769
42 | FLOAT CUM BOOST Battery Charger for offered 800 Ah VRLA Type Battery: Float Charging: 2.13-2.27 V per cell, Boost Charging: 2.28-2.32 V per cell. Input from AC Source I & II without automatic selection. Filter circuit shall be provided to limit the ripple content (Peak to Peak) in the output voltage to 1%, irrespective of the DC load level. a. The battery charger shall support both automatic and manual control of output voltage and current, selectable via a mode selector switch. In automatic mode during float charging, the output voltage shall remain within ±1% of the set value under AC input voltage variation of ±10%, frequency variation of ±5%, combined variation of ±10%, and DC load variation from no load to full load. b. Battery chargers shall operate on constant voltage characteristics across the full load range (zero to full load) at float voltage, ensuring the battery remains fully charged without harmful overcharge. c. Load limiters with drooping characteristics shall be provided, which: * Gradually reduce output voltage when the DC load current exceeds the preset limit (in automatic voltage control mode). * Prevent damage or fuse failure during sustained overloads or short circuits in the DC system. * Ensure the charger does not trip under overload or external short circuit conditions. d. Uniform and stepless adjustment of output voltage shall be available in both manual and automatic modes, accessible from the charger’s front panel, covering the entire float voltage range. e. Stepless adjustment of load limiter setting shall also be provided, adjustable from 80% to 100% of the charger's rated output current during charging mode. f. It shall be possible to adjust the Boost charging current continuously over a range of 50 to 100% of the rated output current for Boost charging mode. g. While in Boost mode, the charger output voltage shall rise automatically as the battery charges. A potentiometer shall be provided on the front panel to set the upper voltage limit for Boost mode, adjustable anywhere within the specified output voltage range. [Charger shall be made from CRCA sheet steel-2mm thick, IP 42 rated, Painted: Phosphated-Primer-Painted 50um, ] The Charger ON/OFF status, input/output voltage, output current, associated charger protection signals shall be provided for integration with SAS. | SET | 2 | 5366.5653 | 482.99 | 482.99 | 6332.5453 | 12665.0907 | Badakushasthali 31 | 12665.0942
43 | Installation and commissioining of de-Mineralised Plant of 50 L/Hr for Making Distilled Water for Battery Banks. (Cation and anion resin bed type) | SET | 1 | 3000 | 270 | 270 | 3540 | 3540 |  | 3540
44 | Installation and commissioining of 20 Ltr Storage Water Cooler (Voltas/Bluestar only) | Nos | 1 | 2500 | 225 | 225 | 2950 | 2950 | LS | 2950
45 | Installation and commissioining of Water Purifier (RO+UV+UF type) suitable for connecting to the above water storage cooler (Kent/Aquaguard/Livpure/Pureit/Bluestar/LG)only | Nos | 1 | 3500 | 315 | 315 | 4130 | 4130 | LS | 4130
46 | INDOOR LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS ) ( Control room building, Open Store shed, store room, Security room cum Visitors room and other area) | Lot | 1 | 6956.21 | 626.0589 | 626.0589 | 8208.3278 | 8208.3278 |  | 8208.3278
47 | 250 KVA outdoor type silent Generator with control panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature as per Technical spec. | Nos. | 1 | 25000 | 2250 | 2250 | 29500 | 29500 | Badakushasthali 33 | 29500
48 | Installation, Testing and Commissioning of Transformers/Reactors: Receiving, Dragging and installing on the plinth and placing in position, Erection of accessories of the Transformers, erection of NCTs on the Transformers, Earthing as per Standard (Including Supply of Materials), Vacuum Treatment of the tank and winding, Oil Filtration (Including Supply of Vacuum cum Oil Filter Machine), Supply & Laying of all types of Control & Power Cables Pertaining to Transformers, Testing and Commissioning including all tests of the Oil as per stipulation in the Standard Approved Testing Laboratory and as per the instruction of the Engineer in Charge. This include all related works for Erection, Testing and Commissioning of the Power Transformers/Auto Transformers. (Contractor to arrange Power Supply for Filtration And Vacuum Treatment works). It also includes supply of all materials required for erection Including T & Ps. | [8 empty] | 0
48.1 | 400/220KV,500 MVA ICT & accessories (including the Digital RTCC panels, NIFPES, Online insulating drying out system, Online Dissolve gas analyser, oil storage tank etc) in complete shape as per Technical spec | Nos | 2 | 806346.36 | 72571.17 | 72571.17 | 951488.7 | 1096631.04 | Badakushasthali 34.1 | 1902977.4096
48.2 | 400 KV, 125 MVAR BUS REACTOR & accessories (including the NIFPES, Online insulating drying out system, Online Dissolve gas analyser etc) in complete shape as per Technical spec: | Nos | 1 | 318865.155 | 28697.86 | 28697.86 | 376260.875 | 376260.875 | Badakushasthali 34.2 | 376260.8829
48.3 | 400 KV, 80 MVAR LINE REACTOR (Including NGR) & accessories (including the NIFPES, Online insulating drying out system, Online Dissolve gas analyser, oil storage tank etc) in complete shape as per Technical spec: | Nos | 2 | 382638.186 | 34437.4367 | 34437.4367 | 451513.0595 | 903026.119 |  | 903026.119
48.4 | 20MVA 220/33KV Power Transformer & accessories in complete shape as per TS. | Nos | 2 | 173315.646 | 15598.4081 | 15598.4081 | 204512.4623 | 409024.9246 |  | 409024.9246
49 | FIRE FIGHTING EQIPMENT: As per TS - (This includes Electric motor driven Main Pump, Jockey Pump-Main and Standby, Diesel engine driven standby Pump, various control & annunciation Panels, Different sizes of MS pipe (to be painted for rust proofing), reducers, different type of valves, pressure gauges, pressure switches, level gauges, level switches, alarms, different type of strainers, Water motor Gong, air vessels, vents, hydrant posts, hydrant valves, hose pipes, QB detectors, HVW spray nozzles, Deluge Valves, Hume pipes, cables and all other equipment/accessories etc. required to complete the Hydrant and HVWS Fire Fighting System.) Hydrant and Mulsifyre system to take care of 2 nos 400/220 KV 500 MVA three phase ICT, 1 Nos 125 MVAR 400 KV three phase Bus Reactor, switchyard equipment, 400KV GIS Hall, 200KV GIS Hall, control room building, LT transformer area, FFPH and Stores. | [8 empty] | 0
49.1 | HVW spray system, Hydrant system system and complete U/G & O/G piping and accessories etc. outside the pump house for 500 MVA, 400/220/33 kV, 3-phase ICT | Set | 2 | 500000 | 45000 | 45000 | 590000 | 1180000 | LS | 1180000
49.2 | HVW spray system, Hydrant system and complete U/G & O/G piping and accessories etc. outside the pump house for 125MVAR, 400 kV 3- phase Bus Reactor | Set | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS | 590000
49.3 | Pumping arrangement for HVW system & hydrant system, complete withall piping, valves, fittings,etc. inside pump house for Fire Protection System of 400/220kV Substation | Set | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS | 590000
49.4 | Hydrant system, complete piping andaccessories etc, outside the Pump House for Fire Protection of 400/220KV Substation | Set | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | LS | 590000
50 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 60 | 20 | 1.8 | 1.8 | 23.6 | 1416 | LS | 1416
51 | INSTALLATION & COMMISSIONING OF ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | [8 empty] | 0
51.1 | 48 fibre optic approach cable including HDPE pipes | KM | 2 | 74340 | 6690.6 | 6690.6 | 87721.2 | 175442.4 | Badakushasthali 34 | 175442.4
51.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at Other end 400KV and 220 kV S/s | SET | 14 | 33000 | 2970 | 2970 | 38940 | 545160 | Badakushasthali 34 | 545160
51.3 | 48V , 500Ah, maintenance free VRLA battery set | NO | 2 | 5795.88 | 521.6292 | 521.6292 | 6839.1384 | 13678.2768 | Badakushasthali 34 | 13678.2768
51.4 | SMPS based battery charger of 125A suitable for 48V, 500Ah VRLA battery | NO | 2 | 15750 | 1417.5 | 1417.5 | 18585 | 37170 | Badakushasthali 34 | 37170
51.5 | 48 V DC board (having 100A DC MCCB as incomer, E/F (earth leakage), under & over voltage as per specification (DC DB-1,DC DB-2 & B/C). | SET | 1 | 8190 | 737.1 | 737.1 | 9664.2 | 9664.2 | Badakushasthali 34 | 9664.2
51.6 | Optical Line Terminal Equipent(OLTE), STM16 type (5 MSP) SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module support upto 150kms ( 02 Nos.) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 150000 | 13500 | 13500 | 177000 | 177000 | Badakushasthali 34 | #REF!
51.7 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 7434 | 669.06 | 669.06 | 8772.12 | 17544.24 | Badakushasthali 34
51.8 | Voice gateway 2x(FXS) | Nos | 1 | 15000 | 1350 | 1350 | 17700 | 17700 | LS
52 | INSTALLATION & COMMISSIONING OF Visual Monitering System (VMS) with Connection to OPTCL Remote Control Center: Note: Any other requirement besides above to be explored & can be finalised during detail Engg. Description of system as below: | LOT | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | LS
53 | CCTV Surveilance system with Latest Version PC Monitor, DBR with 1TB Hard Disk, (Night Hawk) cameras including all materials for areas in Control room building & Entire Switchyard areas,GIS Buildings, Other areas etc suitable for 180 & 360 deg movement with all necessary hardware fittings for monitoring with SCADA compatibility. No. of such cameras (different type) are to be calculated as per standard practice & its installations at the strategic locations. Additional Information: 1. Fixed type cameras for monitoring of main gate , Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House,Main Entrance door of GIS Hall, Main Entrance door of store shed and indoor areas. 2. The areas (Staretgic Location) to be monitored through CCTV system are : a) 220 and 400 kV GIS hall indoor area b) All the Transformer and Reactors under present scope c) Main Entrance door of Control Room Building, Fire-fighting Pump House, GIS Hall, store shed. d) Main entrance gate of switchyard and all gates of switchyard. e) 400 and 220 kV bays Line side equipment (Surge Arrester) of present scope Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 | 45000 | 4050 | 4050 | 53100 | 53100 | Badakushasthali 43
#REF!

## SS CIVIL
ODISHA POWER TRANSMISSION CORPORATION LIMITED
(CIVIL SUB-STATION)
|  |  | 400/220kV Substation at Balasore 400 KV Bays-[10 Nos Bays (2 Fdr+ 2 ICT+ 4 Tie+2 Bus Reactor+2 Line Reactor+ 02 unequipped Spare for line FDR)] In 1 & 1/2 CB System, 220KV Bay-[10 Nos. bays (FDR-6,ICT-2, B/C-1, TB/C-1) & 02nos unequipped Spare Bays] In 02 Main Bus & 01 Transfer Bus System | [9 empty] | OBSERVATIONS TO BE CONSIDERED FOR REVISION
Sl. No. | CIVIL_WORKS _SUBSTATION |  |  | RUPEES IN INR
| DESCRIPTION OF ITEMS (SCHEDULE-2C) SUBSTATION CIVIL WORKS (As per Technical Specification) | UNIT | Quantity | UNIT PRICE | GST PER UNIT |  | TOTAL PER UNIT PRICE | AMOUNT
[5 empty] | SGST@9%(INTRA STATE PER UNIT) | CGST@9%(INTER STATE PER UNIT)
1 | 2 | 3 | 4 | 5 | 6=5x9% | 7=5x9% | 8=5+6+7 | 9=4X8
B | CIVIL WORKS
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 150000 | 5.87 | 0.5283 | 0.5283 | 6.9266 | 1038990 | RC SS 1.10 |  | 1038990 | 0
2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. [15.00mtrs] | PER POINT | 15 | 38609.34 | 3474.8406 | 3474.8406 | 45559.0212 | 683385.318 | RC TL 1.5 B |  | 683385.318 | 0
3 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P | [9 empty] | 0 | 0
3.1 | LEVELLING OF S/S AREA:Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification. | [9 empty] | 0 | 0
3.1.1 | Cutting of earth from substation area, filling & compaction of the usable earth in the substation area and disposal of the unusable soil beyond the substation area including all T & P, labour, carriage etc complete in all respect as per the direction of Engineer in Charge. | Cum | 3000 | 187.16 | 16.8444 | 16.8444 | 220.8488 | 662546.4 | RC-SS-1.2 |  | 662546.4 | 0
3.1.2 | Filling with borrowed earth & compaction: beyond the substation area & up to 100mtrs lead as per the direction of Engineer in Charge. | Cum | 45000 | 658.65 | 59.2785 | 59.2785 | 777.207 | 34974315 | RC-SS-1.30 | Doubt ask why | 34974315 | 0
3.1.3 | Filling with borrowed earth beyond 100 mtrs lead as per the direction of Engineer in Charge. | Cum | 15000 | 1170.92 | 105.3828 | 105.3828 | 1381.6856 | 20725284 | RC-SS-1.30 |  | 20725284 | 0
4 | OPEN CAST & PILE FOUNDATIONS WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc: Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod(FE-500), coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation, concreting, shoring & shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal / column structures and equipment support & others as per the technical specification and approved drawings. (RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (a) For Switch yard gantry/portal structure foundations (b) For 400KV, 220 KV & 33 KV Equipment foundations. (c) For other equipment foundations such as LT distribution boards etc | [9 empty] | 0 | 0
4.1 | EXCAVATION FOR PREPARATION OF FOUNDATION WORK FOR THE SWITCHYARD COLUMN,EQUIPMENT etc.: Excavation for following type of soil and rocks (including shoring where required) and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), including supply of sand, all T&P, labour as required as per instruction of Engineer Incharge. | [9 empty] | 0 | 0
4.1.1 | Normal/Soft Soil | Cum | 6500 | 187.17 | 16.8453 | 16.8453 | 220.8606 | 1435593.9 | RC-SS-2.10 |  | 1435593.9 | 0
4.1.2 | Dense/Compact/Ps/FS/Muddy Soil | Cum | 15500 | 296.35 | 26.6715 | 26.6715 | 349.693 | 5420241.5 | RC-SS-2.10 |  | 5420241.5 | 0
4.1.3 | Soft rock Not required blasting | Cum | 1500 | 662.88 | 59.6592 | 59.6592 | 782.1984 | 1173297.6 | RC-SS-2.10 |  | 1173297.6 | 0
4.1.4 | Hard Rock required Blasting | Cum | 150 | 1091.81 | 98.2629 | 98.2629 | 1288.3358 | 193250.37 | RC-SS-2.10 |  | 193250.37 | 0
4.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in for the above column/equipment/marshalling box foundations for column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 700 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 5004370.56 | RC-SS-3.2- i |  | 5004370.56 | 0
4.3 | Open cast foundation for the above column/equipment/marshalling box foundations with RCC: 1:1.5:3 (Grade M-20) ,including supply of Labour all materials like cement, coarse and fine aggregates,shuttering,proper curing of the foundations/concrete and T&P in line with the Techinical Specification and as per direction of Engineer in Charge. ( without cost of steel) | Cum | 7000 | 8451.26 | 760.6134 | 760.6134 | 9972.4868 | 69807407.6 | RC-SS-3.4-i |  | 69807407.6 | 0
4.4 | Supply of steel different sizes(TATA/RINL/SAIL make only). No other make of steel shall be allowed. As per the design with cutting, bending, binding and placing in position of steel rods for foundation concreting including cost of binding wire. | MT | 225 | 63984.42 | 5758.5978 | 5758.5978 | 75501.6156 | 16987863.51 | RC-SS-3.50 |  | 16987863.51 | 0
5 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling and disposal of excess earth as per the direction of Engineer In charge. | [9 empty] | 0 | 0
| (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in cable trench as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | [9 empty] | 0 | 0
| (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | [9 empty] | 0 | 0
| (4) Fly ash Brickwork with fly ash Brick, plastering (1:6 Ratio) & curing, wherever required including the supply of labour, material, cement, etc. | [9 empty] | 0 | 0
| (5) For Cable trench sections 2-2, 3-3, 4-4, the outdoor cable trench wall top surface shall be "L" shaped and the cover slabs shall be placed with in the"L shaped" surface of both the walls. The top surface of the trench shall be smooth finished. For section 1-1, the slabs shall be placed over the walls of the cable trench. (6)Supply,fabrication & Fixing of GI Angle for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the GI insert plate fixed on the trench wall for better rigidity. The Insert plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. | [9 empty] | 0 | 0
| (7) Precast of RCC covers (1:1.5:3) with MS sheet(2mm) frame and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (8) All the RCC cover slabs shall have the lifting hooks. The slabs without the MS sheet frame and Lifting hooks shall not be accepted. | [9 empty] | 0 | 0
| (9) Cable Trenches Inside The Control Room Shall Be Covered With M.S Chequered Plate(Duly Painted As Per Instruction Of Engg In Charge) Including Standard Support Stand {Hd Galvanised (M.S Joist , Channel, Angle). Stoppers shall be fixed at the underneath so that the chequered shall not be falling into the cable trench in any case. | [9 empty] | 0 | 0
| Cable trench with covers | [9 empty] | 0 | 0
5.1 | Section 1-1 ( Inside clearance- Wall to wall-1400mm, Top to bottom-1275mm, Concrete thickness- Wall-100mm, Bed/floor-100mm), The design is similar to Section 2-2, but the cable trays are arranged on both side of the cable trench. | Mtrs | 800 | 17788.46 | 1600.9614 | 1600.9614 | 20990.3828 | 16792306.24 | Badakushasthali 4.1.1 |  | 16792306.24 | 0
5.2 | Section 2- 2 | Mtrs | 600 | 17788.46 | 1600.9614 | 1600.9614 | 20990.3828 | 12594229.68 | Badakushasthali 4.1.2 |  | 12594229.68 | 0
5.3 | Section 3-3 | Mtrs | 600 | 12019.23 | 1081.7307 | 1081.7307 | 14182.6914 | 8509614.84 | Badakushasthali 4.1.3 |  | 8509614.84 | 0
5.4 | Section 4-4 | Mtrs | 600 | 7211.54 | 649.0386 | 649.0386 | 8509.6172 | 5105770.32 | Badakushasthali 4.1.4 |  | 5105770.32 | 0
5.5 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | NOS | 3 | 450000 | 40500 | 40500 | 531000 | 1593000 | Badakushasthali 4.2 |  | 1593000 | 0
5.6 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing.(Road crossing ). | [9 empty] | 0 | 0
5.6.1 | Road crossing for | [9 empty] | 0 | 0
5.6.2 | Section 1-1 | Nos | 4 | 250000 | 22500 | 22500 | 295000 | 1180000 | Badakushasthali 4.3.1 |  | 1180000 | 0
5.6.3 | Section 2- 2 | Nos | 4 | 250000 | 22500 | 22500 | 295000 | 1180000 | Badakushasthali 4.3.2 |  | 1180000 | 0
5.6.4 | Section 3-3 | Nos | 2 | 250000 | 22500 | 22500 | 295000 | 590000 | Badakushasthali 4.3.3 |  | 590000 | 0
6 | CONTROL ROOM cum office BUILDING: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, brick wall, plastering,painting, Flooring etc.The cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. It shall be ensured that the various room sizes are sufficient to accomodate the offered equipment. Design shall be done considering C/R building to be done at 1.00 TO 1.50mtrs filling area. | [9 empty] | 0 | 0
6.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 472218.55 | 42499.6695 | 42499.6695 | 557217.889 | 557217.889 | Neulapoi 27.1 |  | 557217.889 | 0
6.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 399089.82 | 35918.0838 | 35918.0838 | 470925.9876 | 470925.9876 | Neulapoi 27.2 |  | 470925.9876 | 0
6.3 | Providing & laying Plain cement concrete (1:2:4) (in sunken slab areas)using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 33311.04 | 2997.9936 | 2997.9936 | 39307.0272 | 39307.0272 | Neulapoi 27.3 |  | 39307.0272 | 0
6.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 3166323.25 | 284969.0925 | 284969.0925 | 3736261.435 | 3736261.435 | Neulapoi 27.4 |  | 3736261.435 | 0
6.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 4139142.58 | 372522.8322 | 372522.8322 | 4884188.2444 | 4884188.2444 | Neulapoi 27.5 |  | 4884188.2444 | 0
6.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 952316.33 | 85708.4697 | 85708.4697 | 1123733.2694 | 1123733.2694 | Neulapoi 27.6 |  | 1123733.2694 | 0
6.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 307132.95 | 27641.9655 | 27641.9655 | 362416.881 | 362416.881 | Neulapoi 27.7 |  | 362416.881 | 0
6.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 161769.49 | 14559.2541 | 14559.2541 | 190887.9982 | 190887.9982 | Neulapoi 27.8 |  | 190887.9982 | 0
6.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 124675.99 | 11220.8391 | 11220.8391 | 147117.6682 | 147117.6682 | Neulapoi 27.9 |  | 147117.6682 | 0
6.1 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 551821.51 | 49663.9359 | 49663.9359 | 651149.3818 | 651149.3818 | Neulapoi 27.10 |  | 651149.3818 | 0
6.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 75635.64 | 6807.2076 | 6807.2076 | 89250.0552 | 89250.0552 | Neulapoi 27.11 |  | 89250.0552 | 0
6.12 | Supplying, fitting and Fixing Matt finish full body vitrified Acid proof tiles in floor and in dado upto lintel level of Battery room of 10MM thick, size 300mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 150000 | 13500 | 13500 | 177000 | 177000 | Neulapoi 27.12 |  | 177000 | 0
6.13 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 39320.66 | 3538.8594 | 3538.8594 | 46398.3788 | 46398.3788 | Neulapoi 27.13 |  | 46398.3788 | 0
6.14 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 149553.44 | 13459.8096 | 13459.8096 | 176473.0592 | 176473.0592 | Neulapoi 27.14 |  | 176473.0592 | 0
6.15 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 212776.97 | 19149.9273 | 19149.9273 | 251076.8246 | 251076.8246 | Neulapoi 27.15 |  | 251076.8246 | 0
6.16 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 32408.47 | 2916.7623 | 2916.7623 | 38241.9946 | 38241.9946 | Neulapoi 27.16 |  | 38241.9946 | 0
6.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 172573.2 | 15531.588 | 15531.588 | 203636.376 | 203636.376 | Neulapoi 27.17 |  | 203636.376 | 0
6.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (In toilets, rest rooms) | Lot | 1 | 94601.43 | 8514.1287 | 8514.1287 | 111629.6874 | 111629.6874 | Neulapoi 27.18 |  | 111629.6874 | 0
6.19 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board, Vision glass panel (1.5ft x 1ft) and paisting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. (All except in toilets & rest rooms) | Lot | 1 | 581918.03 | 52372.6227 | 52372.6227 | 686663.2754 | 686663.2754 | Neulapoi 27.19 |  | 686663.2754 | 0
6.2 | Supplying, fitting and fixing of M.S grills, Grill window (as per I.S. specification and as per approved drawings) in proper position in all floors as per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 118410.72 | 10656.9648 | 10656.9648 | 139724.6496 | 139724.6496 | Neulapoi 27.20 |  | 139724.6496 | 0
6.21 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [6 empty] | 0 |  |  | 0 | 0
6.21.1 | Inside walls and Ceiling: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 523170.83 | 47085.3747 | 47085.3747 | 617341.5794 | 617341.5794 | Neulapoi 27.21.1 |  | 617341.5794 | 0
6.21.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 101515.94 | 9136.4346 | 9136.4346 | 119788.8092 | 119788.8092 | Neulapoi 27.21.2 |  | 119788.8092 | 0
6.21.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 9298.75 | 836.8875 | 836.8875 | 10972.525 | 10972.525 | Neulapoi 27.21.3 |  | 10972.525 | 0
6.22 | Supplying, fitting and fixing of Stainless steel of 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with Balustrade of size 32mm x 32mm x 2mm @ 0.90mtr. C/C and stainless square pipe bracing of size 32mm x 32mm x 2mm in 3 rows in stair case as per approved design and specification, buffing, polishing etc with cost, conveyance, cost of all labour,labour cess, T&P etc. required for the work complete in all respect as per direction of the Engineer-in-charge. | Lot | 1 | 50521.27 | 4546.9143 | 4546.9143 | 59615.0986 | 59615.0986 | Neulapoi 27.22 |  | 59615.0986 | 0
6.23 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 100978.98 | 9088.1082 | 9088.1082 | 119155.1964 | 119155.1964 | Neulapoi 27.23 |  | 119155.1964 | 0
6.24 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 66936.46 | 6024.2814 | 6024.2814 | 78985.0228 | 78985.0228 | Neulapoi 27.24 |  | 78985.0228 | 0
6.25 | Providing and fixing of UPVC sliding windows in the Control room Building as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 574776 | 51729.84 | 51729.84 | 678235.68 | 678235.68 | Neulapoi 27.25 |  | 678235.68 | 0
6.26 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 173473.8 | 15612.642 | 15612.642 | 204699.084 | 204699.084 | Neulapoi 27.26 |  | 204699.084 | 0
6.27 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 12652.79 | 1138.7511 | 1138.7511 | 14930.2922 | 14930.2922 | Neulapoi 27.27 |  | 14930.2922 | 0
6.28 | Providing and fixing removable Raised/False Flooring System in the control room as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 364390 | 32795.1 | 32795.1 | 429980.2 | 429980.2 | Neulapoi 27.28 |  | 429980.2 | 0
6.29 | Plinth Potection for control room building as per the provided drawing and as per sepcification in TS. | Lot | 1 | 92194.88 | 8297.5392 | 8297.5392 | 108789.9584 | 108789.9584 | Neulapoi 27.29 |  | 108789.9584 | 0
6.3 | Construction of covered drain for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 330956.09 | 29786.0481 | 29786.0481 | 390528.1862 | 390528.1862 | Neulapoi 27.30 |  | 390528.1862 | 0
6.31 | Provision of PHD and other fittings of Jaguar make for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. Provision of rain water discharge pipes at different locations and two nos of over head water tank of 2000 ltrs capacity etc as per requirement and approved drawing. All bath room & toilet shall have water & termite proof doors and provision of sliding louvers with exhaust fan. | Lot | 1 | 776921.44 | 69922.9296 | 69922.9296 | 916767.2992 | 916767.2992 | Neulapoi 27.31 |  | 916767.2992 | 0
6.32 | Construction of septic tank and soak pit for control room building as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.106 | 23024.106 | 301871.612 | 301871.612 | Neulapoi 27.32 |  | 301871.612 | 0
6.33 | Provision for Electrical Work:Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 1108185.91 | 99736.7319 | 99736.7319 | 1307659.3738 | 1307659.3738 | Neulapoi 27.34 |  | 1307659.3738 | 0
6.34 | Provision of Fire alarm system:- Addressable type Smoke, Heat detector, Beam Detector, Reflector for Beam Detector for the following buildings including all accessories, the Addressable type Main control panel (Microprocessor based 10 loop fire alarm control panel) expandable upto 16 loops (minimum) fully networkable with each loop capable of taking 99 devices, alpha- numeric liquid crystal display. The panel shall be soft addressable type. The panel shall be able to give pin point location of all fire/fault conditions. Further, the panel must be able to automatically switch off respective control switches when ever any alarm is triggered. The panel shall have in built rectifier, Loop cards, provision for externel & internal printer, LCD unit to indicate Fire/Fault Signal with address and analog output, integral SMF lead acid batteries with sealed cells of 24 V capable of running for a minimum of 8 hours with integral battery charger complete as required and as per specification. The fire alarm panel shall be suitable for software integration with SAS system, wall mounting loop powered addressable type hooter with all accessories, addressable manual call box made of polycarbonate with plastic break glass front and complete with monitor module, MCB, addressable isolator module with required PVC box, fittings and fixtures, wiring with PVC FRLS wire to cover the required for fire & smoke detection, Junction boxes, response indicator, EOL resistance etc. Agency shall submit drawings and design. Quantity of various items such as detector, RI, hooter, MCP etc. as per approved design. This includes Supply of all items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 93565 | 8420.85 | 8420.85 | 110406.7 | 110406.7 | Neulapoi 27.35 |  | 110406.7 | 0
6.35 | Provision of false ceiling in the control room building (Control room, Office space, Cabins, rest rooms, Communication room, ACDC room & lobby) as per specification mentioned in the civil section & approved drawings including, relay panel room, office room, SAS room, conference room, rest room etc as per direction of the engineer in charge. | Lot | 1 | 250000 | 22500 | 22500 | 295000 | 295000 | Neulapoi 27.36 |  | 295000 | 0
7 | MAIN GATE, WICKET GATE & SECURITY SHED: The Main gate, wicket gate and the Secirity shed shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation shall be designed as per actual site soil condition and shall be constructed as per approved drawing. | [9 empty] | 0 | 0
7.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 35532.43 | 3197.9187 | 3197.9187 | 41928.2674 | 41928.2674 | Badakusthasthali 6.1 |  | 41928.2674 | 0
7.2 | Providing and lying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 30322.32 | 2729.0088 | 2729.0088 | 35780.3376 | 35780.3376 | Badakusthasthali 6.2 |  | 35780.3376 | 0
7.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 443372.68 | 39903.5412 | 39903.5412 | 523179.7624 | 523179.7624 | Badakusthasthali 6.3 |  | 523179.7624 | 0
7.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 565359.94 | 50882.3946 | 50882.3946 | 667124.7292 | 667124.7292 | Badakusthasthali 6.4 |  | 667124.7292 | 0
7.5 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 90680.42 | 8161.2378 | 8161.2378 | 107002.8956 | 107002.8956 | Badakusthasthali 6.5 |  | 107002.8956 | 0
7.6 | Providing 12 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 14705.25 | 1323.4725 | 1323.4725 | 17352.195 | 17352.195 | Badakusthasthali 6.6 |  | 17352.195 | 0
7.7 | Providing 16mm thick cement plaste ( 1:6) finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 16080.99 | 1447.2891 | 1447.2891 | 18975.5682 | 18975.5682 | Badakusthasthali 6.7 |  | 18975.5682 | 0
7.8 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 8988.68 | 808.9812 | 808.9812 | 10606.6424 | 10606.6424 | Badakusthasthali 6.8 |  | 10606.6424 | 0
7.9 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 8613.92 | 775.2528 | 775.2528 | 10164.4256 | 10164.4256 | Badakusthasthali 6.9 |  | 10164.4256 | 0
7.10 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 2071.9 | 186.471 | 186.471 | 2444.842 | 2444.842 | Badakusthasthali 6.10 |  | 2444.842 | 0
7.11 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 2782.87 | 250.4583 | 250.4583 | 3283.7866 | 3283.7866 | Badakusthasthali 6.11 |  | 3283.7866 | 0
7.12 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 6003.88 | 540.3492 | 540.3492 | 7084.5784 | 7084.5784 | Badakusthasthali 6.12 |  | 7084.5784 | 0
7.13 | Providing and fixing of 35mm thick WPC Door Shutter(Solid) with teak edge leaping to the periphery of the shutter with pilishing as per detailed drawing with including, all hardwares & fixtures, SS tower bolt(150mm), Door stopper, SS aldrop(250mm), SS handle(200mm length), ss handle (150mm length) & SS Butt hinges -125mm x 65mm x2.12mm .including cost, conveyance, loading, T&P required for the work etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 12476.16 | 1122.8544 | 1122.8544 | 14721.8688 | 14721.8688 | Badakusthasthali 6.13 |  | 14721.8688 | 0
7.14 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge ( W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 | 136012.19 | 12241.0971 | 12241.0971 | 160494.3842 | 160494.3842 | Badakusthasthali 6.14 |  | 160494.3842 | 0
7.15 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | [9 empty] | 0 | 0
7.15.1 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 36222.67 | 3260.0403 | 3260.0403 | 42742.7506 | 42742.7506 | Badakusthasthali 6.15.1 |  | 42742.7506 | 0
7.15.2 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 14163.64 | 1274.7276 | 1274.7276 | 16713.0952 | 16713.0952 | Badakusthasthali 6.15.2 |  | 16713.0952 | 0
7.15.3 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 5032.84 | 452.9556 | 452.9556 | 5938.7512 | 5938.7512 | Badakusthasthali 6.15.3 |  | 5938.7512 | 0
7.16 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 14502.83 | 1305.2547 | 1305.2547 | 17113.3394 | 17113.3394 | Badakusthasthali 6.16 |  | 17113.3394 | 0
7.17 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 6770.36 | 609.3324 | 609.3324 | 7989.0248 | 7989.0248 | Badakusthasthali 6.17 |  | 7989.0248 | 0
7.18 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 26280 | 2365.2 | 2365.2 | 31010.4 | 31010.4 | Badakusthasthali 6.18 |  | 31010.4 | 0
7.19 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 24914.7 | 2242.323 | 2242.323 | 29399.346 | 29399.346 | Badakusthasthali 6.19 |  | 29399.346 | 0
7.20 | GFRC Letter: Manufacturing, providing and installation of GFRC mouldings (Glass Fiber Reinforced Concrete) of approved make of thickness 230mm±5mm with pattern, design and colour of approved make to be fixed on/beteween RCC/ block work column or structural work with dry fixing method with all required T & P , manpower and all other material as required for completion of work in all respect. | [9 empty] | 0 | 0
7.20.1 | Per Letter (450mm(h) x 40mm (d) x 50mm (w)) | Nos | 20 | 800 | 72 | 72 | 944 | 18880 | Badakusthasthali 6.20.1 |  | 18880 | 0
7.20.2 | OPTCL Logo | Nos | 1 | 1000 | 90 | 90 | 1180 | 1180 | Badakusthasthali 6.20.2 |  | 1180 | 0
7.21 | Provision of Electrical works the Security Shed & Main Gate Complex :- Provision of Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make), fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. The provision shall also be made for supply & installation of waterproof LED Gate lamp (70W) for main Gate. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 1 | 244423.62 | 21998.1258 | 21998.1258 | 288419.8716 | 288419.8716 | Badakusthasthali 6.21 |  | 288419.8716 | 0
7.22 | Supply of the following materials: a) First Aid Box - 1 set b) Shock Treatment Chart (Odia, Hindi & English) - 1 set c) Insulating mat - 6 sq. m. d) Danger Board - 1 set | Lot | 1 | 6015 | 541.35 | 541.35 | 7097.7 | 7097.7 | Badakusthasthali 6.22 |  | 7097.7 | 0
8 | SWITCHYARD GATE: Switchyard gates shall have RCC pillars on both sides having open or pile founfdation and the gate shall be of stainless steel of 304 grade. The main entrance gate to switchyard shall have a wicket gate made of the same material. The gates shall be as per the specification, approved drawing and instruction of engineer in charge. Provision of gate lights (Post top lantern type) on each pillar of the gate. It includes supply & fixing of light fixtures including LED Gate lamp (70 W), LV XLPE cables, switchgear etc required to complete works as per specification and approved drawings. | [9 empty] | 0 | 0
8.1 | Switchyard gate | Lot | 3 | 150000 | 13500 | 13500 | 177000 | 531000 | Neulapoi 19.1 |  | 531000 | 0
8.2 | Wicket gate | Lot | 1 | 50908.54 | 4581.7686 | 4581.7686 | 60072.0772 | 60072.0772 | Badakusthasthali 7.2 |  | 60072.0772 | 0
8 | BOUNDARY WALL (RCC structure, Brickwall type) | [6 empty] | 0 |  |  | 0 | 0
8.1 | BOUNDARY WALL: The boundary wall shall be constructed as per the drawing provided and technical specification, complete in all respect and as per instruction of Engineer in charge. The foundation for the boundary wall shall be designed as per actual site soil condition and shall be constructed as per approved drawing. | RM | 3000 | 10000 | 900 | 900 | 11800 | 35400000 | Neulapoi 29.1 |  | 35400000 | 0
8.1.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.3 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour, Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.4 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.5 | Providing Brick work with Fly ash bricks 25cm x 12cm x 8cm size having crushing strength not less than 75 kg/cm2 with dimensional tolerance +/ - 2 percent in cement mortar (1:6) ( 1 cement: 6 sand), with all necessary projection, splay cutting, circular moulding, corbelling, etc., including cost of all materials, labour, conveyance, loading ,and unloadining, royalties, scaffolding, watering, curing, sundries, tools and plants, etc., as per the direction of the Engineer-in-charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.6 | Providing 16 mm. thick cement plaster in all floors at all height with cement mortar of mix (1:6) with portland slag cement (PSC) finished smooth to inside rough surface of brick masonry walls after racking out joints including watering and curing rounding of corners etc. complete with cost, coveyance, loading and unloading, royalties and ,es of all materials and cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. (Inside) | Lot | 1 | [7 empty] | 0 | 0
8.1.7 | Painting to external building surface with weather coat two coats over a coat of primer of approved shade and quality of approved design after cleaning by watering & removing the dirts etc. to the surface to be painted including watering, curing, cost, conveyance of all materials, cost of all labour, brushes, T&P etc. and necessary scaffolding work complete as directed by the Engineer-in-charge. | Lot | 1 | [7 empty] | 0 | 0
8.1.8 | Supplying, fitting and fixing of M.S grills, grill gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railing ( as per I.S. specification and as per approved drawings ) in proper position in all floors and at all height including making holes to brick walls/ R.C.C structure/wood work etc. and making good to the damaged walls/ structures with cement concrete (1:2:4) with black hard crusher broken granite stone chips of 12mm to 20mm size ( 20mm size not to exceeds 25% ) including watering and curing etc. complete in all respect as directed by the Engineer in charge ( W.I. / M.S. windows grills, grill gates, collapsible gates with top and bottom rails, steel windows, steel doors, steel frames for doors and windows, staircase and parapet railings square bar along with required nos. of nails and screws and other required materials of approved quality and approved size shall be supplied by the contractor at his own cost.) | Lot | 1 | [7 empty] | 0 | 0
8.1.9 | Providing and painting two coats with synthetic enamel paint over a coat of primer to iron work of approved quality and approved shade confirmming to ISI on steel work to give an even shade in all floors at all height over a coat of primer of approved quality and shade including sand papering and making the surface smooth with cost, coveyance, loading and unloading, of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by Engineer-in-charge. | Lot | 1 | [7 empty] | 0 | 0
9 | Out door bay kiosks (2 nos for 400KV, 2nos for 220 kV Switchyard = Total 4 Nos.) : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The indicative drawing provided in the TS may be referred to. As per approved drawings and specification. The internal size of Switchyard kiosks shall be 8m x 5.5m x 3.3m. Doors shall be heat insulated and hinge type. The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. Total Quantity = 2 LOT(400KV KIOSK) +2 LOT (220 kV KIOSK) = 4 LOTs | [9 empty] | 0 | 0 | The internal size of Switchyard kiosks shall be 8m x 5.5m x 3.3m. There shall be one Kiosk for Two diameters of 400KV and two nos of kiosks for all 220KV bays. Total Qty shall be 4 nos. Accordingly the cost part may be revised on prorata basis
9.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil & rock as per drawing and technical specification complete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the surplus earth/unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. This includes cost, conveyance of all materials, all labour, T&P articles required for the work, stacking the useful materials separately, including shoring, shuttering, propping and dewatering if required etc. | Lot | 4 | 176000 | 15840 | 15840 | 207680 | 830720 |  |  | 830720 | 0 | 44 | 25 | 1.76
9.2 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (including, column, Beams and roofs etc) as per technical spec & approved drawings. | Lot | 4 | 528000 | 47520 | 47520 | 623040 | 2492160 |  |  | 2492160 | 0
9.3 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 4 | 264000 | 23760 | 23760 | 311520 | 1246080 |  |  | 1246080 | 0
9.4 | Flooring shall be with vitrified digital double charged tiles with dado as per technical spec & approved drawings. Provision of window blinders in the Panel room. | Lot | 4 | 264000 | 23760 | 23760 | 311520 | 1246080 |  |  | 1246080 | 0
9.5 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 4 | 176000 | 15840 | 15840 | 207680 | 830720 |  |  | 830720 | 0
9.6 | Provision of ceiling in the adjacent panel room area as per specification mentioned in the civil section & approved drawings. | Lot | 4 | 176000 | 15840 | 15840 | 207680 | 830720 |  |  | 830720 | 0
9.7 | Doors shall be of Hinge type with locking facility and shall be of heat insulated type. As per technical spec & approved drawing. | Lot | 4 | 88000 | 7920 | 7920 | 103840 | 415360 |  |  | 415360 | 0
9.8 | Internal concealed wiring (including supply of flexible copper FRLSH 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board, Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make) ,ceiling fans of 1400 sweep and regulators (including supply), exhaust fan (including supply). No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec/National Lighting Code/IS 6665 & fixing of the same rigidly on the suitable height either ceiling & wall as required. It includes supply of fixtures and lamps (LED) including D.C emergency lighting of reputed make (Phillips/Crompton/Bajaj/Havells/Wipro) with switch gear for succesful illumination of the area/rooms. As per approved drawing and direction of Engineer In charge. This includes Supply of all electrical items and its erection to complete the work as per spec & approved drawing. | Lot | 4 | 176000 | 15840 | 15840 | 207680 | 830720 |  |  | 830720 | 0
9.9 | Provision of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 4 | 176000 | 15840 | 15840 | 207680 | 830720 |  |  | 830720 | 0
10 | ROADS | [6 empty] | 0 |  |  | 0 | 0
10.1 | 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section (Inside the substation area) as per approved drawing. | Mtrs | 1200 | 9000 | 810 | 810 | 10620 | 12744000 | Neulapoi 7.1 |  | 12744000 | 0
10.2 | Approach Road: 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section (from the switch yard main gate to the govt road.) | Mtrs | 300 | 9000 | 810 | 810 | 10620 | 3186000 | Neulapoi 7.2 |  | 3186000 | 0
10.3 | 3.75 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 1200 | 5000 | 450 | 450 | 5900 | 7080000 | Neulapoi 7.3 |  | 7080000 | 0
11 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts,Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. All the drainage system shall be RCC type with M20 grade concrete. | [6 empty] | 0 |  |  | 0 | 0
11.1 | Storm water drain (RCC type) with slabs as per design above and subsequent approval [Wall thickness: 150 mm, Bed: 150 mm, Wall to wall distance : 1100mm, Slab thickness: 100 mm] | Mtrs | 1000 | 1500 | 135 | 135 | 1770 | 1770000 | Badakusthasthali 11.1 |  | 1770000 | 0
11.2 | Road side drains(RCC type)-on each side of the 3.75 mtr and 7 mtr concrete roads as per design above & subsequent apporval. | Mtrs | 2400 | 1000 | 90 | 90 | 1180 | 2832000 | Badakusthasthali 11.2 |  | 2832000 | 0
11.3 | Road-culverts, drain crossings | Lots | 1 | 312294.43 | 28106.4987 | 28106.4987 | 368507.4274 | 368507.4274 | Badakusthasthali 11.3 |  | 368507.4274 | 0
12 | Foundations for transformers, Reactors and NGRs :Design, engineering, supply of labour, material, equipments and construction of ICTs/Auto-transformer/Power Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road as per item under 4.2). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used in the Transformer foundation & other works. | [6 empty] | 0 |  |  | 0 | 0
12.1 | 500 MVA, 400/220KV ICT Total weight with oil and tank: 450 MT (appox) | Nos | 2 | 5277797.73 | 475001.8 | 475001.8 | 6227801.33 | 12455602.66 | Badakusthasthali 12.1 |  | 12455602.6428 | 0.0172
12.2 | All civil works related to NIFPES of 400/220KV, 500MVA ICT as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | Lot | 2 | 250000 | 22500 | 22500 | 295000 | 590000 | Badakusthasthali 12.2 |  | 590000 | 0
12.3 | 125 MVAr, 400 KV Reactor Total weight with oil and tank: 250 MT Approximately | Nos | 2 | 3427797.73 | 308501.8 | 308501.8 | 4044801.33 | 8089602.66 | Badakusthasthali 12.3 |  | 8089602.6428 | 0.0172
12.4 | All civil works related to NIFPES of 125MVAr, 400KV Reactor as per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | Lot | 2 | 200000 | 18000 | 18000 | 236000 | 472000 | Badakusthasthali 12.4 |  | 472000 | 0
12.5 | 80 MVAR, 400 KV Line Reactor Total weight with oil and tank: 200 MT Approximately | Nos | 2 | 3127797.73 | 281501.8 | 281501.8 | 3690801.33 | 7381602.66 | Badakusthasthali 12.5 |  | 7381602.6428 | 0.0172
12.6 | All civil works related to NIFPES 80MVAr, 400KV Reactoras per approved drawing including excavation in all type of soil, PCC, RCC, Steel , backfilling, compaction etc complete in all respect as per instruction of site in-charge. | Lot | 2 | 200000 | 18000 | 18000 | 236000 | 472000 | Badakusthasthali 12.6 |  | 472000 | 0
12.7 | STATION TRANSFORMER:Design, engineering, supply of labour & civil material including all associated works for construction of RCC foundation FOR TRANSFORMER ,DP structure foundation,Foundation for LT out door kiosk near transformers for station transformers 33/0.415 kV, 1000 KVA STN TRANSFORMER as per approved drawing and specification and as per instruction of Engineer In charge. | Nos | 2 | 139878.9 | 12589.101 | 12589.101 | 165057.102 | 330114.2 | Badakusthasthali 12.7 |  | 330114.204 | -0.004
12.8 | Foundations for NGRs for Line reactors :Design, engineering, supply of labour, material, equipments and construction of ICTs/Auto-transformer/Power Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,a | Nos | 2 | 139878.9 | 12589.101 | 12589.101 | 165057.102 | 330114.2 | Badakusthasthali 12.8 |  | 330114.204 | -0.004 | NGRs for Line Reactors
12.8 | OIL SUMP PIT(RCC) : (150% of tfr oil capacity of one transformer of each capacity): Design, engineering, supply of labour, material, equipments and construction of oil sump pit (RCC with ratio 1:1.5:3) including piling if any, all associated works & suitable connectivity oil collector pit provisioned near the transformer to the main oil sump pit and with provision of pump (suitable for handling transformer oil having capacity of 5 HP with auto level control , including cabling, fixing of control gear & provision of a pump shed of sufficient size to allow person to install, dismantle, make cable connection & maintain etc over the oil sump pit). This oil sump pit shall be as per CIGRE standard for the oil collection pit inorder to separate oil from the water. Other piping with necessary valves arrangement shall also be provided to remove water from the oil sump pit. As per spec and approved drawing.The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. This includes all supply for complete the work such as 5HP pump, cables etc). Oil capacity of each ICT in ltrs appox. | [9 empty] | 0 | 0
12.8.1 | a) 500 MVA, 400/220 KV: 150000 ltrs. | Nos | 1 | 196083.22 | 17647.49 | 17647.49 | 231378.2 | 231378.2 | Neulapi 10.3.1 |  | 231378.1996 | 0.0004
12.8.2 | b) 125MVAr Bus Reactor: 100000Ltrs | Nos | 1 | 196083.22 | 17647.49 | 17647.49 | 231378.2 | 231378.2 | Neulapi 10.3.2 |  | 231378.1996 | 0.0004
12.8.3 | b) 80MVAr Bus Reactor: 50000Ltrs | Nos | 1 | 196083.22 | 17647.49 | 17647.49 | 231378.2 | 231378.2 | Neulapi 10.3.3 |  | 231378.1996 | 0.0004
13 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:3:6 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | Cum | 3000 | 6058.56 | 545.2704 | 545.2704 | 7149.1008 | 21447302.4 | RC SS 3.20-i |  | 21447302.4 | 0
14 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | Cum | 4000 | 3316.26 | 298.4634 | 298.4634 | 3913.1868 | 15652747.2 | RC SS 5.10 |  | 15652747.2 | 0
15 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: As per site condition of the substation and approval of the gardening layout. The qty may vary as per the approved layout and instrcution of engineer in charge. | [6 empty] | 0 |  |  | 0 | 0
15.1 | Provision of gardens/ lawn area with garden grass in front of the control room building & other areas that can be developed as a garden as per the site Engineer's instruction. This include the all required work including the soil treatment for laying of the lawn grass. | sqm | 200 | 500 | 45 | 45 | 590 | 118000 | Badakusthasthali 15.1 |  | 118000 | 0
15.2 | Motorised fountain at a suitable location as per instrcution of Engineer in charge. | Nos | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Badakusthasthali 15.2 |  | 59000 | 0
15.3 | Sprinkler arrangement in the lawn to cover all the lawn area and water tap arrangement at different location to all areas of plantation. | Lot | 1 | 50000 | 4500 | 4500 | 59000 | 59000 | Badakusthasthali 15.3 |  | 59000 | 0
15.4 | Flowering plants (Rose, jasmine, hibiscus or as per instruction of Engineer in Charge at least 50 each | Nos | 400 | 50 | 4.5 | 4.5 | 59 | 23600 | Badakusthasthali 15.4 |  | 23600 | 0
15.5 | Fruit bering Non Fruit bearing Plants (Mango, guava, Neem, Acacia) as per instruction of Engineer in Charge. 25 nos of each type of trees to be plantedin the free areas immediately after the substation layout paln is finalised. It must be ensured that the plants survive till hand over. Therefore, proper care shall be taken by the contractor. | Nos | 200 | 50 | 4.5 | 4.5 | 59 | 11800 | Badakusthasthali 15.5 |  | 11800 | 0
15.6 | Decorative Plants for Lawn/garden (varieties of Hedge, thuja) as per instruction of Engineer in Charge | Nos | 200 | 50 | 4.5 | 4.5 | 59 | 11800 | Badakusthasthali 15.6 |  | 11800 | 0
15.7 | Decorative plants (foxtail palm of at least 5 ft height) for both side of the 7m road from the main gate as per instruction of the Engineer in charge. | Nos | 100 | 1100 | 99 | 99 | 1298 | 129800 | Badakusthasthali 15.7 |  | 129800 | 0
15.8 | Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags as per the direction of Engineer incharge. | Nos | 1 | 10000 | 900 | 900 | 11800 | 11800 | Badakusthasthali 15.8 |  | 11800 | 0
15.9 | Precasted bench 05nos (minimun 03 people can be seated) shall be provided for seating arrangement with RCC base. | Nos | 5 | 5000 | 450 | 450 | 5900 | 29500 |  |  | 29500 | 0
16 | RETAINING WALL, STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification. RCC retaing wall of 1:1.5:3 M-20 grade where required. | [9 empty] | 0 | 0
16.1 | Excavation of all type of soil for stone pitching & Toe wall | Cum | 200 | 289.77 | 26.08 | 26.08 | 341.93 | 68386 | RC-SS-1.00-ii |  | 68385.72 | 0.28
16.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 22 | 5907.71 | 531.69 | 531.69 | 6971.09 | 153363.98 | RC-SS-1.2-i |  | 153364.1516 | -0.1716
16.3 | RR Masonry (1:5) | Cum | 500 | 2933.92 | 264.05 | 264.05 | 3462.02 | 1731010 | RC-SS-1.30 |  | 1731012.8 | -2.8
16.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 10 | 7186 | 646.74 | 646.74 | 8479.48 | 84794.8 | RC-SS-1.10-i |  | 84794.8 | 0
16.5 | Excavation of all type of soil for Retaining wall | Cum | 2000 | 319.88 | 28.79 | 28.79 | 377.46 | 754920 | Badakushasthali |  | 754916.8 | 3.2
16.6 | P.C.C (1:3:6): Lean Concrete Grade M-10 for retaing wall | Cum | 150 | 5907.71 | 531.69 | 531.69 | 6971.09 | 1045663.5 | RC-SS-1.2-i |  | 1045664.67 | -1.17
16.7 | RCC (1:1.5:3) M-20 Grade | Cum | 1200 | 8533.36 | 768 | 768 | 10069.36 | 12083232 | RC-SS-1.4-i |  | 12083237.76 | -5.76
16.8 | Supply of Steel (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 ) of different size (as per design) with cutting, bending, binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under reem Pile) including supply of binding wire with supply of steel rod ( FE-500 as per BIS-1786 ) for retaining wall | MT | 200 | 63984.42 | 5758.6 | 5758.6 | 75501.62 | 15100324 | RC-SS-3.50 |  | 15100323.12 | 0.88
17 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing ( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick Masonry work with ratio mortar (cement and sand)1:5 and cement pointing of the joints, for the fencing upto a height of 350 mm from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing shall be as per specification. The fencing shall be continuous i.e. a GI flat of 50 x 6mm shall run continuous at top & at bottom all along the fence. The fencing shall be connected to the earth mat every 3 mtrs. | MTRS | 2000 | 2240 | 201.6 | 201.6 | 2643.2 | 5286400 | Neulapoi 18 |  | 5286400 | 0
18 | Fire wall (for 400KV ICT, Reactors): Design, engineering, procurement of labour, material including all associated works for construction of fire-walls (including the piling where required) as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant Fly ash Bricks).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. Painting of the walls as per direction of the Engineer in charge. | Nos | 3 | 200000 | 18000 | 18000 | 236000 | 708000 | Neulapoi 12 |  | 708000 | 0
19 | STORE SHED+OPEN STOCKYARD:Design, engineering, procurement of labour, material including all associated works for construction of store shed & open stockyard as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no store shed of floor size 10X10 mtr having Fly ash Brick walls and plastering with RCC roof. The flooring shall be of 75 mm thickness PCC (mix ratio1:2:4) over RR masonry works (as per standard practice of flooring). Provision of adequate nos of MS racks (proper paintings also to be done as per the direction of site in charge) for keeping the spare materials. The height of the shed shall be 4mtrs above the plinth. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Foundation shall be as per actual soil condition as per soil test, including piling where required. | Lot | 1 | 1100000 | 99000 | 99000 | 1298000 | 1298000 | Neulapoi 22 |  | 1298000 | 0
| Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.Store shed door shall have access control system which is sensor operated with key card for entry. Log of all the persons accessing the store shed with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment (including supply of FFE) at strategic location suitable for wall hanging as per direction of engineer in charge. The MS Rod ( FE-500 as per BIS-1786 ) to be used in the building. (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)} | [9 empty] | 0 | 0
20 | VEHICLE PARKING SHED: Design, engineering, construction of parking area shall be with the cost of all required material, procurement of labour, all T&P etc. This includes supply of all materials and all associated works for construction of vehicle parking shed, complete in all respect as per technical specification and enclosed drawing. This also includes, excavation in all type soil and rocks, backfilling and disposal of excavated soil, (cement, reinforcement steel, form work for) PCC, RCC (1:1.5:3), M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal), Fly ash Brick work with mortar 1:5, Plastering, Flooring, External and Internal Painting, all electrical works (Including but not limited to wires, conduits, GI boxes, switches, luminaires (Phillips/Crompton/Bajaj/Havells/Wipro), electrical fixtures and all other switchgear etc.)etc. and any other works required for completion of the work in all respect. Foundation shall be as per actual soil condition as per soil test, including piling where required. The provision is to be made for three cars and space for six wheelers (the indicative drawing is for two cars and spaces for six wheelers). The work includes Design, engineering, procurement of labour, material including all associated works, provision of LED luminaire of Philips/Bajaj/CG/Havells with required switchgears, conduits, wires. | Lot | 1 | 500000 | 45000 | 45000 | 590000 | 590000 | Neulapoi 23 |  | 590000 | 0
21 | BORE WELL with PUMP and associated switchgear For water supply to Switchyard Buildings, Switchyard with water tank: Design, engineering, procurement of labour, material (viz. pipes, plumbing fittings etc) including all associated works for construction of bore wells for water supply to switchyard buildings as per specification and approved drawing and instruction of Engineer in charge. This includes supply and fixing and commissioning of 5 HP submersible water pump with starter and other protection. The electrical starter units shall be placed at the control room building and at the transit house. This includes supply of materials,labours and T&P for dilling of borewells in all type of soils including rock and disposal of excess materials as per instruction of Engineer Incharge. Supply & laying of LV XLPE 3.5CX.35 sqmm cable from ACDB to srater unit and pump & earthing of the system etc to complete the scheme as per approved drawing & instruction of Engineer-in charge. | Nos | 3 | 650000 | 58500 | 58500 | 767000 | 2301000 | Badakushasthali 21 |  | 2301000 | 0
22 | Construction of special concrete (RCC) water tank( withstand the high pressure due to water) as per spec to be used for Fire Fighting purpose of the ICT's and Reactors and switchyard equipment.(It includes excavation,RCC M25, Pipes and as per CIGRE practice. The quantity of the water to be stored in the water tank is to be calculated considering the worst condition i.e, in case both the ICT and Reactors are caught Fire and fire fighting system (Hydrant and mulsifire system) to get the required water from the tank for successful completion of the process of complete fire fighting. | LOT | 1 | 5000000 | 450000 | 450000 | 5900000 | 5900000 | Badakushasthali 22 |  | 5900000 | 0 | Repaet item as in 23.10
23 | FIRE FIGHTING BUILDING:(one building).Design, engineering and construction of switchyard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge.As per approved drawings and specification. Area of the Fire Fighting pump house with portico at front side, stair case to the top of the building ,.The details of of building construction shall be as per the Tech spec. A) Area of the fire fighting Room Building: 10mtrX10 Mtrs(100 sq mtr). | [9 empty] | 0 | 0 | DG shed may be separated and Fire fighting pump house and water tak may be kept as on item
23.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000 |  |  | 236000 | 0
23.2 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 (for Pile foundation with cost of boring, Column ,Beams and roofs etc. ) as per technical spec & approved drawings. | Lot | 1 | 1474056.38 | 132665.07 | 132665.07 | 1739386.52 | 1739386.52 | Badakushasthali 23.1 |  | 1739386.5284 | -0.0084
23.3 | Brick masonry work in cement sand mortar 1: 6 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 616037.25 | 55443.35 | 55443.35 | 726923.95 | 726923.95 | Badakushasthali 23.2 |  | 726923.955 | -0.005
23.4 | Concrete Flooring to be provided on the floor l of the Fire Fighting room as per technical spec & approved drawings. | Lot | 1 | 273819.13 | 24643.72 | 24643.72 | 323106.57 | 323106.57 | Badakushasthali 23.3 |  | 323106.5734 | -0.0034
23.5 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint. Refer the specification. | Lot | 1 | 302037.25 | 27183.35 | 27183.35 | 356403.95 | 356403.95 | Badakushasthali 23.4 |  | 356403.955 | -0.005
23.6 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC with double layer glaze of 6mm & windows shall have aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 182019.13 | 16381.72 | 16381.72 | 214782.57 | 214782.57 | Badakushasthali 23.5 |  | 214782.5734 | -0.0034
23.7 | Provision of PHD and other fittings of reputed (Jaguar make) having ISI mark ,provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing & technical specification & as per instruction of Engg- in-Charge. It includes supply of all types of materials of reputed make, labour etc to complete the work. Doors shall be of solid heavy duty PVC type. | Lot | 1 | 82019.13 | 7381.72 | 7381.72 | 96782.57 | 96782.57 | Badakushasthali 23.6 |  | 96782.5734 | -0.0034
23.8 | Internal concealed wiring & supply & fixing of lighting fixtures(LED) ,fans and regulators(Electronic regulator) ,exhaust fan,D.C emergency lighting INCLUDING SUPPLY OF ALL ITEMS as per spec & approved drawing. | Lot | 1 | 244718.17 | 22024.64 | 22024.64 | 288767.45 | 288767.45 | Badakushasthali 23.7 |  | 288767.4406 | 0.0094
23.9 | Supply & installation of Fire Fiting :- Provision of smoke and fire detection system of the building. | Lot | 1 | 219079.72 | 19717.17 | 19717.17 | 258514.06 | 258514.06 | Badakushasthali 23.8 |  | 258514.0696 | -0.0096
23.11 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section). | Lot | 1 | 280460 | 25241.4 | 25241.4 | 330942.8 | 330942.8 | Badakushasthali 23.10 |  | 330942.8 | 0
24 | Anti-Weed Treatment :Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 8000 | 17.84 | 1.6056 | 1.6056 | 21.0512 | 168409.6 | Badakushasthali 24 |  | 168409.6 | 0
25 | PROVISION OF SAND BED:Design, engineering, procurement of labour, material including all associated works for construction of sand bed as per specification and approved drawing. This also includes excavation in all types of soil or rocks, back fillin ,and disposal of excess earth as per the direction of Engineer In charge. The sand bed size shall be of 10m x 5m constructed with bricks, plastered and the filled with river sand for storing of Transformer Bushings and other Insulators. | Lot | 1 | 100000 | 9000 | 9000 | 118000 | 118000 | Badakushasthali 25 |  | 118000 | 0
27 | COLOUR CODING, BAY MARKING Etc:Design, engineerimg, procurement of labour, material including all associated works for the followings.This should be as per direction of site In charge. a)Colur coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof stickering may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed.Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 200000 | 18000 | 18000 | 236000 | 236000 | Badakushasthali 26 |  | 236000 | 0
28 | RCC Foundations for Octagonal Lighting Poles: Design, engineering, procurement of labour, material including piling if any, all associated works for construction of foundations for octagonal lighting poles as per approved drawings (RCC ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. Pcc padding ratio (1:4:8). The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 to be used. | Nos | 50 | 10000 | 900 | 900 | 11800 | 590000 |  |  | 590000 | 0 | Qty of 100Nos have been considered in Supply. Hence the qty may be revised to 100
29 | TRANSIT HOUSE: Design, engineering and construction of switch yard buildings including excavation, construction of foundations (open cast or pile as per soil conditions), construction of RCC super structure, bick the cost of material, supply of labour, cement, reinforcement- steel and form work as per the enclosed drawing and technical specification ( The RCC structure frame and the foundations should be in the ratio 1:1.5:3). The indicative drawings of the building is provided and the foundation of the building shall be designed based on the actual soil condition. | [9 empty] | 0 | 0
29.1 | Earthwork excavation (for any work, open cast or pile foundations etc) in all kinds of soil as per drawing and technical specificationcomplete in all respect including backfilling of the usable soil, supplying & filling the foundation, plint with sand, compaction, carriage & disposal of the unsuable material as per requirement to complete the work in all respect and instruction of Engineer in Charge. | Lot | 1 | 301211.02 | 27108.99 | 27108.99 | 355429 | 355429 | Neulapoi, 30.1 |  | 355429.0036 | -0.0036
29.2 | Providing and laying Plain Cement Concrete of proportion (1:3:6) in foundation and floors using 4cm (1 1/2") 0 mm & down grade black hard crusher broken granite stone metal, washed and screened sharp sand of approved quality from approved quarry including hoisting, lowering, laying the concrete, ramming, watering and curing etc. complete to required thickness including cost of all materials, conveyance, loading, unloading,cost of labours, T&P, hire & running charges of concrete mixer, etc. all complete as per the direction of the Engineer -in -charge. | Lot | 1 | 260559.34 | 23450.34 | 23450.34 | 307460.02 | 307460.02 | Neulapoi, 30.2 |  | 307460.0212 | -0.0012
29.3 | Providing & laying Plain cement concrete (1:2:4) using 12mm size black hard crusher broken granite chips of approved quality from approved quarry including hoisting, lowering and laying concrete in layers, watering, curing etc. complete including cost, conveyance, royalties and taxes of all materials with labour, cess and T&P etc. required for the work complete. | Lot | 1 | 9942.65 | 894.84 | 894.84 | 11732.33 | 11732.33 | Neulapoi, 30.3 |  | 11732.327 | 0.003
29.4 | Providing and laying in position ready mixed M-25 grade concrete having compressive strength at 28 days test not less than 250 kg/ sq.cm for reinforced cement concrete work (foundations, columns, Beams, lintels, chhajas, roof slabs, stair case etc), using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work including pumping of R.M.C. from transit mixer to site of laying , including the cost of centering, shuttering finishing and excluding reinforcement including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, and hoisting, lowering, laying and compacting concrete, watering and curing and finishing the exposed surfaces smooth with cost, conveyance, royalties, of all materials with all labour,Labour cess and T&P required for the work improve workability without impairing strength and durability as per direction of the Engineer - in - charge. | Lot | 1 | 1676113.36 | 150850.2 | 150850.2 | 1977813.76 | 1977813.76 | Neulapoi, 30.4 |  | 1977813.7648 | -0.0048
29.5 | Cutting, straightening coiled or bent up M.S. rods, HYSD steel or Tor Steel (SAIL, RINL, TATA, Jindal) welding or jointing if necessary, bending, binding, tying the grills as required for RCC works, and hoisting, lowering and placing in proper position according to approved designs and drawings including cost, conveyance, loading, unloading, M.S. rods, HYSD steel or Tor steel and binding wires of 18 to 20 gauge required for the work and cost of all labour, sundries, T&P and scaffolding complete in all respect as directed by the Engineer-in-Charge. | Lot | 1 | 2232941.16 | 200964.7 | 200964.7 | 2634870.56 | 2634870.56 | Neulapoi, 30.5 |  | 2634870.5688 | -0.0088
29.6 | Fly Ash brick masonry using fly ash bricks of size 25 cm. x 12 cm. x 8 cm. having crushing strength not less than 75 kg. Per Sqr. Cm. in cement mortar of mix (1:6) for foundation and plinth and in cement mortar of mix (1:4) for other area in ground floor, first floor & head room with ordinary portland cement (OPC) and screened & washed sand for mortar after immersing the bricks for 6 (Six) hours in water before use including splays cutting, circular moulding, corbelling, chamfering and similar such type of works, watering and curing etc. including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, scaffolding, sundries, T&P required for the works etc. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 385242.08 | 34671.79 | 34671.79 | 454585.66 | 454585.66 | Badakusthasthali 29.6 |  | 454585.6544 | 0.0056
29.7 | Providing 16 mm. thick cement plaster (1:6) finished smooth to inside brick walls after racking out the joints including watering and curing with cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P, sundries and scaffolding required for the work etc. with providing grooves as directed by the Engineer in charge. | Lot | 1 | 177975.53 | 16017.8 | 16017.8 | 210011.13 | 210011.13 | Neulapoi, 30.7 |  | 210011.1254 | 0.0046
29.8 | Providing 18mm C.P. in two coats underlayer 12mm C.P. 1:5 and top layer 6mm thick C.P. 1:6 finished even and smooth on outside masonry walls including racking out joints, scrapping and cleaning the surface and finishing the plastered surface smooth to proper plumbs and levels and providing grooves as shown in the drawing including cost of all materials, labour, conveyance, loading and unloading, royalty, scaffolding, watering, curing, sundries, tools and plants, etc., complete excluding GST as per the direction of the Engineer-in-charge. | Lot | 1 | 104882.42 | 9439.42 | 9439.42 | 123761.26 | 123761.26 | Badakusthasthali 29.8 |  | 123761.2556 | 0.0044
29.9 | Providing 6mm thick cement plaster in cement mortar of (1:4) to RCC surfaces such as ceilings of roof slabs, stairs, landings, chajja, shelves, columns, beams and lofts etc. including roughening/chipping, scraping and cleaning and finishing the plastered surface smooth using wooden floats, bars, etc. only to proper plumbs and level, making grooves, beads and drip coarse to give required ornamental finish as per drawing including cost of all materials, conveyance, loading and unloading, royalties, cost of all labour, scaffolding, staging, watering before plastering and curing, sundries and T&P, etc. complete as per direction of the Engineer-in-charge. | Lot | 1 | 52842.74 | 4755.85 | 4755.85 | 62354.44 | 62354.44 | Neulapoi, 30.9 |  | 62354.4332 | 0.0068
29.10 | Providing vitrified tile flooring using Matt vitrified tiles having thickness of 8mm to 10mm conforming to IS 13756 of 600mm x 600mm Colour & Printed Series (homogeneous) of approved quality of Somany / Kajaria / Johnson in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with epoxy grout with required quantities of pigments of approved marks to match the shades of the vitrified tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work, complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 239188.36 | 21526.95 | 21526.95 | 282242.26 | 282242.26 | Neulapoi, 30.10 |  | 282242.2648 | -0.0048
29.11 | Supplying, fitting and Fixing Matt finish full body vitrified tile in dado /skirting of 10MM thick, size 600mm x 300mm with water absorption less than 0.3 % of Somany / Kajaria / Johnson of approved make having base price of the tile Rs. 90 / sqft confirming to I.S.15622 laid on 12mm thick cement mortar (1:3) (1 cement : 3 coarse sand) and filling joints with white cement of approved quality including cost of all materials, labour, T&P etc. required for the work all complete as per direction of Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 51802.87 | 4662.26 | 4662.26 | 61127.39 | 61127.39 | Neulapoi, 30.11 |  | 61127.3866 | 0.0034
29.12 | Providing, fitting & fixing anti-skid ceramic floor tiles in flooring in toilets using special plain/ printed series anti-skid ceramic floor tile of premium grade (having minimum thickness 7 mm to 8 mm & size 300 mm x 300 mm confirming to IS 13755 of approved quality and shade of Somany/ Kajaria / Johnson on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened & washed sharp river sand for mortar ceramic floor tiles with neat white cement slurry, mixed with required (tiles are to be immersed in the water for required time before use) quantities of pigments of approved marks to match the shades of the anti-skid ceramic floor tiles if required including cost, conveyance, loading, unloading, stacking, royalties of all material, cost of all labour, sundries, T&P required for the work, watering, complete in all respect as per specification excluding GST as per specification as directed by Engineer-in-charge. (Note- sample of tiles shall be approved before procurement and use) | Lot | 1 | 12140.52 | 1092.65 | 1092.65 | 14325.82 | 14325.82 | Neulapoi, 30.12 |  | 14325.8136 | 0.0064
29.13 | Providing & Fixing tiles of size 30cm x 45 cm glazed ceramic wall tiles (All Toilet walls) of premium grade of approved quality and shade having thickness 8mm to 10mm confirming to IS 13755 in dados skirting and risers of steps on 12mm thick cement plaster (1:3) to proper slope, line and level including cutting to required size and shape, fixing at corners and splays etc including filling the joints with neat white cement slurry mixed with pigments to match the shade of the tiles including cost, Conveyance, loading, unloading, stacking, royalities of all materials, cost of all labour,T&P, sundries, watering and curing for the required period for the work complete in all respect excluding GST as directed by the Engineer-in-charge.(Note- Sample of tiles shall be approved before procurement and use.) | Lot | 1 | 65578.7 | 5902.08 | 5902.08 | 77382.86 | 77382.86 | Badakusthasthali 29.13 |  | 77382.866 | -0.006
29.14 | Providing Granite stone prepolished 20mm thick of area above 0.40 Sqm in flooring of approved quality, colour and size in floors, treads on steps and landings in all floors at all height on 20mm thick bed of cement mortar of mix (1:4) laid in proper slope and gradient with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. Providing edge moulding to 18 mm thick granite stone counters, Vanities, steps etc., including machine polishing to edge to give high gloss finish including making three nos of groove over tread etc. complete including cost, coveyance, loading and unloading and ,royalties of all materials, cost of all labour, sundries, T&P, scaffolding etc. required for the work and complete in all respect as directed by the Engineer in charge. | Lot | 1 | 123268.36 | 11094.15 | 11094.15 | 145456.66 | 145456.66 | Badakusthasthali 29.14 |  | 145456.6648 | -0.0048
29.15 | Providing Granite stone prepolished 10mm thick in dado of approved quality, colour and size in dado, riser of steps and dado of landings in all floors at all height on 12mm thick bed of cement mortar of mix (1:3) with screened and washed sharp sand for mortar and grouted with neat white cement slurry jointing the tile with neat white cement slurry mixed with required quantities of pigments of approved marks to match the shades of the granite tile if required watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties of all materials, cost of all labour, T&P required for the work etc. complete in all respect as per specification and direction of Engineer-in-charge. | Lot | 1 | 19217.93 | 1729.61 | 1729.61 | 22677.15 | 22677.15 | Badakusthasthali 29.15 |  | 22677.1574 | -0.0074
29.16 | Providing,Fixing 16m thick Kota stone in floors treads or steps and landing on 20mm thick cement mortar (1:4) (1cement : 4 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. Providing,Fixing 16m thick Kota stone in dado ,riser on 12mm thick cement mortar (1:3) (1cement : 3 course and) and filling joints with of approved quality including cost, conveyance, taxes, cost of all labour etc. complete. | Lot | 1 | 44895.68 | 4040.61 | 4040.61 | 52976.9 | 52976.9 | Badakusthasthali 29.16 |  | 52976.9024 | -0.0024
29.17 | Providing and fixing in position wood plastic composite door frame with appropriate length of ETA Approved carbon steel galvanized (minimum 5 microns) double threaded 6.8 grade Polyamide PA 6 grade sleeve HRD C 10 anchor suitable for fastenings both on concrete & masonary/aerated blocks including cost of all materials, labours, T & P etc required for the work. complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 125157.9 | 11264.21 | 11264.21 | 147686.32 | 147686.32 | Badakusthasthali 29.17 |  | 147686.322 | -0.002
29.18 | Providing , fitting & fixing of 32mm thick flush door shutter with 32mm thick BWP block board and pasting 1 mm thick laminate to both sides with adhesive including fitting & fixing of all fixtures like godrej make ofice lock haveing model. No. 6548. Godrej make door clouser having model no- 2701. including cost of all materials, all labour, all T&P etc. required for the work complete in all respect as per the direction of the Engineer-in-Charge excluding G.S.T. | Lot | 1 | 448363.08 | 40352.68 | 40352.68 | 529068.44 | 529068.44 | Badakusthasthali 29.18 |  | 529068.4344 | 0.0056
29.19 | Supplying, fitting and fixing of M.S grills, Grill window ( as per I.S. specification and as per approved drawings ) in proper position in all floorsas per TS, approved drawing, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 91241.08 | 8211.7 | 8211.7 | 107664.48 | 107664.48 | Badakusthasthali 29.19 |  | 107664.4744 | 0.0056
29.20 | Painting: Preparation of the birck wall, concrete and steel surfaces as per specification to receive painting including scaffolding, cleaning the surfaces, curing, cost conveyance, labour, supply of putty, primer, paint & other materials/T & P required for painting, complete in all respect as directed by the Engineer In charge. | Lot | [6 empty] | Badakusthasthali 29.20 |  | 0 | 0
29.21 | Inside walls: application of two coats of wall putty (water based) on the prepared surface, application of one coat of cement primer (oil bound) and three coats of oil bound distemper/emulsifier paint of approved quality and shade. | Lot | 1 | 280619.13 | 25255.72 | 25255.72 | 331130.57 | 331130.57 | Badakusthasthali 29.21 |  | 331130.5734 | -0.0034
29.22 | Outside walls: application of one coat of cement primer (oil bound) and two coats of weather seal coat of approve quality and shade on the prepared surfaces. | Lot | 1 | 65795.51 | 5921.6 | 5921.6 | 77638.71 | 77638.71 | Badakusthasthali 29.22 |  | 77638.7018 | 0.0082
29.23 | Steel work: application of one coat of primer on the prepared steel surfaces and two coats of synthetic enamel paint of approved quality and shade. | Lot | 1 | 607.66 | 54.69 | 54.69 | 717.04 | 717.04 | Badakusthasthali 29.23 |  | 717.0388 | 0.0012
29.24 | Providing 2.5 cm thick grading concrete(1:2:2) on roof slab using 6mm size hard granite chips as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 71130.56 | 6401.75 | 6401.75 | 83934.06 | 83934.06 | Badakusthasthali 29.24 |  | 83934.0608 | -0.0008
29.25 | Providing & applying of pre constructional anti-termite treatment as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 44317.83 | 3988.6 | 3988.6 | 52295.03 | 52295.03 | Badakusthasthali 29.25 |  | 52295.0394 | -0.0094
29.26 | Providing and fixing of UPVC sliding windows in the Transit house as per TS, complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 424584 | 38212.56 | 38212.56 | 501009.12 | 501009.12 | Badakusthasthali 29.26 |  | 501009.12 | 0
29.27 | Waterproofing to the roof slab as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 122196.6 | 10997.69 | 10997.69 | 144191.98 | 144191.98 | Badakusthasthali 29.27 |  | 144191.988 | -0.008
29.28 | Water proofing to the sunken slab including providing and filling it with 40mm size brick bat as per TS complete in all respect as per approved drawing and instruction of Engineer in Charge. | Lot | 1 | 3348 | 301.32 | 301.32 | 3950.64 | 3950.64 | Badakusthasthali 29.28 |  | 3950.64 | 0
29.29 | Providing and laying tactile tile (for vision impaired persons as per standards) of size 300x300x9.8 mm having with water absorption less than 0.5% and conforming to IS:15622 of approved make in all colours and shades in for outdor floors such as footpath, courtyard, multi modals location etc., laid on 20mm thick base of cement mortar 1:4 (1 cement : 4 coarse sand) in all shapes & patterns including grouting the joints with white cement mixed with matching pigments etc. complete as per direction of Engineer-in-Charge | Lot | 1 | 21505.13 | 1935.46 | 1935.46 | 25376.05 | 25376.05 | Badakusthasthali 29.29 |  | 25376.0534 | -0.0034
29.30 | Supplying, fitting and fixing in position 16mm thick chequred tile of approved make and quality, colour and size in all floors at all height on 25mm thick bed of cement mortar of mix (1:1) laid in proper slope and gradient with screened and washed sharp sand for mortar and with Portland Slag Cement (PSC) grouted with neat white cement slurry with required quantities of pigments of approved marks watering and curing for 21 days, including cost, conveyance, loading, unloading, royalties and taxes of all materials, cost of all labour, sundries, T&P required for the work complete in all respect as directed by the Engineer-in-charge | Lot | 1 | 15829.76 | 1424.68 | 1424.68 | 18679.12 | 18679.12 | Badakusthasthali 29.30 |  | 18679.1168 | 0.0032
29.31 | Plinth Potection for Transit house as per the provided drawing and as per sepcification in TS. | Lot | 1 | 71707.51 | 6453.68 | 6453.68 | 84614.87 | 84614.87 | Badakusthasthali 29.31 |  | 84614.8618 | 0.0082
29.32 | Construction of covered drain for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 257416.05 | 23167.44 | 23167.44 | 303750.93 | 303750.93 | Badakusthasthali 29.32 |  | 303750.939 | -0.009
29.33 | Provision of PH work for the Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 570758.62 | 51368.28 | 51368.28 | 673495.18 | 673495.18 | Badakusthasthali 29.33 |  | 673495.1716 | 0.0084
29.34 | Construction of septic tank and soak pit for Transit house as per the provided drawing and as per specification in TS. | Lot | 1 | 255823.4 | 23024.11 | 23024.11 | 301871.62 | 301871.62 | Badakusthasthali 29.34 |  | 301871.612 | 0.008
29.35 | Provision of Electrical works the Transit house as per the provided drawing and as per specification in TS. This also includes supply of all electrical materials (of specified manufacturer as indicated in the TS) to complete the work as as per description provided in the relevant section of TS. | Lot | 1 | 467669.25 | 42090.23 | 42090.23 | 551849.71 | 551849.71 | Badakusthasthali 29.35 |  | 551849.715 | -0.005
29.36 | Furnishings for Transit House: Supply and installation of the following items- 1. 55 inch Full HD LED TV set of Sony/LG/Samsung make with supply of Set up Box for the television unit with 1 year recharge from the date of commissioning (1set) 2.Durian/Godrej Sofa set (3+1+1) with center table for lobby (1 set) 3. King size cot with mattress & all other amenities like study table with 2 chair (Godrej) in all the bed rooms, bed sheets, pillow etc (Bombay Dyeing/Raymond Home) make. 2 Person wardrobe (Godrej Interio), hangers for hanging cloths in each room for storage of Baggages and Cloths etc. Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) - Total 4 sets for 4 guest rooms 4. Geyser-3 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make (4 set) 5. Dining table with 6 chairs of Durian/Godrej make (1 set) 6. Modular kitchen with exhaust chimney system, gas stove, and required utensils (1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons at a stretch) 7. RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make (1 set) 8. 3 star inverter compressor frost free Refrigerator of 230 Ltr or above capacity, double door type (LG/Samsung/Whirlpool/Godrej/Panasonic Make) (1 set) | LOT | 1 | 2000000 | 180000 | 180000 | 2360000 | 2360000 | Badakusthasthali 29.36 |  | 2360000 | 0
30 | DG Shed: Design, engineering and construction of DG shed for rain/sun protection including the cost of material, supply of labour, T&P, etc. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth, PCC, RCC, reinforcement steel MS rods (FE-500-TATA/ RINL/ Sail/JINDAL), brick work as per the direction of Enginer In charge. As per approved drawings and specification. The RCC foundation and Plinth to be in the ratio 1:1.5:3. including piling where required. DG shed shall be Steel fame structure type with channels, I beams etc (HDG 610 g/sqm) with top canopy - colour coated corrugated galvalume (TATA blue scope/JSW make). Canopy shall be 2 way - open gable sloped for discharge of rainwater. This incluses all other associated works viz. painting, illumination for DG set etc to complete the work in full shape. The Plinth area of the D.G shed shall be atleast 36 sq mtrs (9mtrsX4 mtrs) or as per the size of the DG set whichever is higher. | LOT | 1 | 300000 | 27000 | 27000 | 354000 | 354000 | Neulapoi33 |  | 354000 | 0 | DG Shed: Design, engineering and construction of DG shed for rain/sun protection including the cost of material, supply of labour, T&P, etc. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth, PCC, RCC, reinforcement steel MS rods (FE-500-TATA/ RINL/ Sail/JINDAL), brick work as per the direction of Enginer In charge. As per approved drawings and specification. The RCC foundation and Plinth to be in the ratio 1:1.5:3. including piling where required. DG shed shall be Steel fame structure type with channels, I beams etc (HDG 610 g/sqm) with top canopy - colour coated corrugated galvalume (TATA blue scope/JSW make). Canopy shall be 2 way - open gable sloped for discharge of rainwater. This incluses all other associated works viz. painting, illumination for DG set etc to complete the work in full shape. The Plinth area of the D.G shed shall be atleast 36 sq mtrs (9mtrsX4 mtrs) or as per the size of the DG set whichever is higher.
| TOTAL OF (Civil Work) (PART-B)_SUBSTATION_2C | [6 empty] | 435716747.5746 |  |  | 435716753.1024 | -5.5278

## Pandiabili Spare (hidden)
ODISHA POWER TRANSMISSION CORPORATION LIMITED
NAME OF THE WORK:- Design, Engineering, Supply, Erection and Commissioning of 02 Nos 400KV AIS feeder bay extension with SAS (to be integrated with the existing SAS) & its control (One dia) at 400KV Pandiabili gird sub-station for connectivity with proposed GIS S/S Berhampur at Sindhaba
SUPPLY_SUBSTATION MANDATORY SPARES
Sl. No. | SUPPLY OF MANDATORY SPARES FOR 400 KV BAY-EXTENSION AT PANDIABILI SUB-STATION | UNITS | Qty | Unit Price in Rs | Total Price in Rs excluding GST
1 | 2 | 3 | 4 | 5 | 6 = 4 x 5
1 | 420 KV,2000-1000-500A,63KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 1 | #REF! | #REF!
2 | 420 KV,2000A,63KA,ISOLATORS
2.1 | MALE & FEMALE CONTACTS | SET | 2 | 24318.75 | 48637.5
2.2 | POWER CONTACTOR, RELAYS, MCBs, SWITCHES, FUSES, PUSH BUTTONS, RESISTORS ETC AS PER APPROVED SCHEMATIC. | SET | 1 | 17510 | 17510
2.3 | LIMIT SWITCH | SET | 2 | 3891 | 7782
2.4 | MOTOR WITH GEAR ASSEMBLY & BEVEL GEAR ASSEMBLY COMPLETE. | SET | 1 | 17510 | 17510
2.5 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1 | 4864 | 4864
2.6 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1 | 38910 | 38910
2.7 | HINGE PINS,TERMINAL CONNECTOR,TERMINAL PAD | SET | 1 | 10862 | 10862
3 | 420KV,4000A,63KA,SF6,CIRCUIT BREAKER
3.1 | CLOSING COIL | NOS | 10 | 1526.7 | 15267
3.2 | TRIPPING COIL | NOS | 10 | 1526.7 | 15267
3.3 | SF6 GAS FILLING DEVICE | NOS | 1 | 25441.7 | 25441.7
3.4 | SET OF GASKETS ,"O" RINGS,SEALS PER CIRCUIT BREAKER | SET | 1 | 11194.59 | 11194.59
4 | 390 KV,METAL OXIDE, 10 KA, CLASS III SURGE ARRESTOR COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 1 | #REF! | #REF!
5 | 400 KV Bus Post Insulators | NOS | 2 | #REF! | #REF!
A | TOTAL OF SUPPLY OF MANDATORY SPARES FOR 400 KV BAY-EXTENSION SUB-STATION |  |  |  | #REF!