## CBA
COST BENEFIT ANALYSIS
A. BENEFITS DUE TO ADDITIONAL SALE OF ENERGY ON ACCOUNT OF CONSTRUCTION OF 400/220 KV Grid Sub-Station at Baisinga
1 | Transformation Capacity considered for revenue calculation considering n-1 criterion | 500
2 | Power factor (PF) | 0.9
3 | Diversity factor | 1.43
4 | Load factor | 0.6
5 | Additional Avg. power available for sale on account of construction of 2X500 MVA, 400/220KV Grid substation at Baisinga. | 188.8112 | 750 | 0.9: power factor 1.3: Diversity factor
6 | Additional energy available for sale in LU | 16539.8601 |  | Due to industrial GSS 0.7 LF is considered
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 16043.6643 |  | TL of 3% is approved for FY 25-26
8 | Anticipated revenue at a cost of Rs.0.24/ Unit in Lakhs | 3850.4794
B. BENEFITS OF THE SCHEME DUE TO REDUCTION IN LOSSES
1 | Total losses before implementation of the scheme in MW | 1204.4373
2 | Total losses after implementation of the scheme in MW | 1183.2365 |  | Loss reduction from Load flow study
3 | Total reduction in losses in MW | 21.2008
4 | Load factor | 0.6
5 | Loss load factor (0.8 LF2 + 0.2 LF) | 0.408
6 | The energy available for sale per year in LU | 757.7325
7 | With 3% transmission losses in the Grid, the energy available for sale per annum in LU | 735.0005
8 | Anticipated revenue due to reduction in losses in lakhs @ Rs. 0.24/Unit | 176.4001
C. CALCULATION OF REVENUE RETURN
1 | Anticipated revenue due to reduction in losses [Rs. Lakhs] | 176.4001
2 | Anticipated revenue due to sale of additional energy [Rs. Lakhs] | 3850.4794
3 | Total anticipated annual revenue [Rs. Cr.] | 40.2688
4 | Estimated Cost [Rs. Cr.] | 361.74
5 | Average Annual Rate of Return in % | 11.132
6 | Internal Rate of Return in % | 11.19%

## IRR_BAISINGA
Calculation of NPV and IRR : For 2X500 MVA, 400/220KV Sub-Station at Baisinga, Mayurbhanj
CoC (%) = | 70% | x | 8.03 | + | 30% | x | 15.5 | Average | 6.58 |  |  | RoI on Loan P.a |  |  | = | 7.75 |  | IRR = | 11.19% | [16 empty] | (Rs. in Crores)
Particulars | Constuction Period |  |  | Benefits Period | [34 empty] | Total
Financial Year | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
Cash Inflow (CI)
Equity | 32.56 | 32.56 | 43.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.53
Loan(Principal) | 75.97 | 75.97 | 101.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.23
Loan (Interest) | 6.1 | 12.2 | 20.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.63
Revenue | 0 | 0 | 0 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 1409.4078
Salvage Value | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.039 | 40.039
Total (CI) - (A) | 114.63 | 120.73 | 165.03 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 40.2688 | 80.3078 | 1849.8368
Cash Outflow (CO)
CWIP | 108.53 | 108.53 | 144.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 361.76
IDC | 6.1 | 12.2 | 20.33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38.63
Loan Repayment | 0 | 0 | 0 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291.86
Interest on Loan | 0 | 0 | 0 | 22.46 | 20.51 | 18.55 | 16.6 | 14.65 | 12.69 | 10.74 | 8.79 | 6.84 | 4.88 | 2.93 | 0.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.62
R&M exp. @ 3 % PC | 0 | 0 | 0 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 420.35
Total (CO) - (B) | 114.63 | 120.73 | 165.03 | 58.7917 | 56.8417 | 54.8817 | 52.9317 | 50.9817 | 49.0217 | 47.0717 | 45.1217 | 43.1717 | 41.2117 | 39.2617 | 37.3117 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 12.01 | 1253.22 | IRR
Net Cash Inflow (A-B) | 0 | 0 | 0 | -18.5229 | -16.5729 | -14.6129 | -12.6629 | -10.7129 | -8.7529 | -6.8029 | -4.8529 | -2.9029 | -0.94287 | 1.0071 | 2.9571 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 28.2588 | 68.2978 | 596.6168 | 11.19%
DF @ CoC | 1 | 0.938 | 0.88 | 0.826 | 0.775 | 0.727 | 0.682 | 0.64 | 0.601 | 0.564 | 0.529 | 0.496 | 0.465 | 0.437 | 0.41 | 0.384 | 0.361 | 0.338 | 0.318 | 0.298 | 0.28 | 0.262 | 0.246 | 0.231 | 0.217 | 0.203 | 0.191 | 0.179 | 0.168 | 0.158 | 0.148 | 0.139 | 0.13 | 0.122 | 0.115 | 0.107 | 0.101 | 0.095
Net Present value(NPV) | 0 | 0 | 0 | -15.3 | -12.84 | -10.62 | -8.64 | -6.86 | -5.26 | -3.84 | -2.57 | -1.44 | -0.44 | 0.44 | 1.21 | 10.85 | 10.2 | 9.55 | 8.99 | 8.42 | 7.91 | 7.4 | 6.95 | 6.53 | 6.13 | 5.74 | 5.4 | 5.06 | 4.75 | 4.46 | 4.18 | 3.93 | 3.67 | 3.45 | 3.25 | 3.02 | 2.85 | 6.49 | 73.02
NPV at IRR | 0 | 0 | 0 | -13.47 | -10.84 | -8.59 | -6.7 | -5.1 | -3.75 | -2.62 | -1.68 | -0.9 | -0.26 | 0.25 | 0.67 | 5.76 | 5.17 | 4.66 | 4.18 | 3.76 | 3.39 | 3.05 | 2.74 | 2.46 | 2.2 | 2.01 | 1.78 | 1.61 | 1.44 | 1.3 | 1.16 | 1.05 | 0.96 | 0.85 | 0.76 | 0.68 | 0.62 | 1.37 | -0.03
**
CoC - Cost of Capital
IDC- Interest During Construction
CWIP- Capital Work in Progress
DF- Discounting Factor
IRR- Internal Rate of Return
ARR- Average Annual Rate of Return
Opening Balance |  |  | 291.86 | 267.5383 | 243.2167 | 218.895 | 194.5733 | 170.2517 | 145.93 | 121.6083 | 97.2867 | 72.965 | 48.6433 | 24.3217
Repayment |  |  | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217 | 24.3217
Closing Balance |  |  | 267.5383 | 243.2167 | 218.895 | 194.5733 | 170.2517 | 145.93 | 121.6083 | 97.2867 | 72.965 | 48.6433 | 24.3217 | 3.5527e-14
Agerage Loan |  |  | 279.6992 | 255.3775 | 231.0558 | 206.7342 | 182.4125 | 158.0908 | 133.7692 | 109.4475 | 85.1258 | 60.8042 | 36.4825 | 12.1608
Interest |  |  | 22.4598 | 20.5068 | 18.5538 | 16.6008 | 14.6477 | 12.6947 | 10.7417 | 8.7886 | 6.8356 | 4.8826 | 2.9295 | 0.97651
|  |  | -0.00015692 | -0.0031868 | 0.0037834 | 0.00075358 | -0.0022762 | 0.0046939 | 0.0016641 | -0.0013657 | -0.0043956 | 0.0025746 | -0.00045525 | -0.0034851

## Data sheet
| Expenditure in Cr.: | 361.74
| Year: | 2025-26 | 2026-27 | 2027-28
| % of Expenditure: | 30% | 30% | 40%
| Year wise expenditure: | 108.522 | 108.522 | 144.696
Loan | 70% | 75.97 | 75.97 | 101.29
Equity | 30% | 32.56 | 32.56 | 43.41
Total | 100% | 108.53 | 108.53 | 144.7