Panikoili Grid Substation:

A Technical study for new proposed Grid Substation of 220/132/33kV at Panikoili area considering the Load demand and low voltage issues in the command area.

Proposal of DISCOM:

- 132/33 kV Chadheidhara Grid substation

- 132/33kV  Bari Grid substation

Issues in the Command area

- Low voltage issue at Chadheidhara, Kabatbandh, Aruha, Panikoili, Bari etc

- OPTCL at present operating radially to meet the following Grid load as 132kV Duburi – Jajpur Road D/c line loaded upto – 140 MW.

| Sl No | Grid Substation | Voltage | Existing capacity | Peak Load |
| --- | --- | --- | --- | --- |
| 1 | Chandikhol | 132/33kV | 3x20MVA = 60 MVA | 55 MW |
| 2 | Jajpur Town | 132/33kV | 2x40+1x20 MVA=100 MVA | 65MW |
| 3 | Jajpur Road | 132/33kV | 3x40MVA = 120 MVA | 74 MW |

Previous proposals of OPTCL

220/33kV GSS at Chittalo:

- Change in Power scenario after commissioning of ongoing new 400/220kV GSS at Ersama. Paradeep area become power surplus which can cater the enhanced load growth in Kendrapada and Jajpur area.

- Considering the power scenario in that command area a new 132kV connectivity to existing OPTCL GSS is required for optimal load distribution and enhance reliability in that area.

- Lack of acquisition of suitable land parcel that can accommodate 220 and 132kV Grid substation in Chittalo area.

Connectivity of Panikoili GSS:

In order to meet above constraints a 220/132/33kV GSS at Panikoili has been proposed with following connectivity.

- 2x160+2x50 MVA, 220/132/33kV GSS, Panikoili

- LILO of 220kV New Duburi – Paradeep D/c line

- LILO of 132kV Jajpur Road – Kendrapada   D/c line

Benefit after commissioning of Panikoili GSS:

- Mitigation of low voltage issues at Chadheidhara, Kabatbandh, Aruha, Panikoili, Bari etc.

- With this, their feeder overloading problem (33kV Kabatabandha and 33 kV Bari respectively, along with rest feeders) will be solved.

- It can cater additional 50 MVA load considering the future load growth.

- N-1 connectivity at 33kV to Kuakhia and Panikoili area

- Shifting of load from overloaded GSS like Jajpur Town & Chandikhol.

- 132kV System strengthening in Jajpur area.

- A 220kV Substation improve system reliability with additional load handling capacity.