## Summarry
1st BOQ Amendment Proposal
Project Name: “Design, Engineering, Supply, Erection and commissioning of (i) 400 KV DC line using Wind-Zone-VI (55 mtrs/sec) Lattice Towers from Loc. No.1 (dead end tower of 400/220 KV AIS at New Duburi) to Loc no.182 (before birupa River Crossing towards 400 KV Proposed GIS Grid S/s at Ersama) (Approx. line length-67.814 Kms); (ii) 220 KV DC line using Wind-Zone-VI (55 mtrs/sec) Lattice Towers from proposed GIS at Ersama, Paradeep to existing 220/132/33 KV Grid S/S at Pratapsasan(Approx. line length- 61.19 Kms.); (iii) 2 Nos. 220 KV feeder bay extension (AIS) at existing 220/132/33KV Grid S/S, Pratapsasan for connectivity with proposed GIS S/S at Ersama, Paradeep on Turnkey contract basis”.
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Name of the agency: TRANSRAIL LIGHTING LIMITED
| Sr. No. | Description | Original Order Value |  |  |  |  | Total Order Value After Amendment |  |  | Differential Value Inclusive of GST(Between Original BOQ And Ammended BOQ) | % increase
|  |  | Ex-Works Price with Freight in INR | Total GST in INR (18%) | Total in INR | Actual as per LOA Rates |  | Total Revised Price | Total GST in INR (18%) | Total in INR
[6 empty] | Amount | Deviation Percentage
| 1 | Schedule - VIIA - Part-I Supply Component of the Works Contract for SS & Line | 1264215620.7683 | 227558811.7383 | 1491774432.5065 | 1289572873.0747 | 0.020058 | 1289013844.343 | 232022491.9817 | 1521036336.3247 | 29261903.8182 | 1.962%
| 2 | Schedule - VIIB - Part-II Erection Component of the Works Contract for SS & Line | 119529433.586 | 21515298.0455 | 141044731.6315 | 131798999.562 | 0.10265 | 129787637.6622 | 23361774.7792 | 153149412.4414 | 12104680.8099 | 8.582%
| 3 | Schedule - VIIC - Part-III Civil Work Component of the Works Contract for SS & Line | 685266447.1 | 123347960.478 | 808614407.578 | 1146810857.8092 | 0.67353 | 1046526766.739 | 188374818.013 | 1234901584.7521 | 426287177.1741 | 52.72%
| TOTAL CONTRACT PRICE |  | 2069011501.4543 | 372422070.2618 | 2441433571.716 | 2568182730.4458 | 0.24126 | 2465328248.7442 | 443759084.774 | 2909087333.5181 | 467653761.8021 | 19.15%

## S_Bay
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
SUPPLY - 220kV BAY
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment |  | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | Cost Data Rate | Least Cost | Amount
1 | 245 KV,1200-600-300A,40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER(4 PS Cl & 1 0.2s Cl) | NOS | 353144 | 6 | 2118864 | 381395.52 | 2500259.52 | 6 | 2118864 | 0 | 0% | 6 | 2118864 | 0 |  | 0 | 0 | 2118864 | 381395.52 | 2500259.52 | 0 |  | A
2 | 245 KV,2000A,40KA,ISOLATORS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | S/I WITH OUT EARTH SWITCH | NOS | 420830 | 6 | 2524980 | 454496.4 | 2979476.4 | 6 | 2524980 | 0 | 0% | 6 | 2524980 | 0 |  | 0 | 0 | 2524980 | 454496.4 | 2979476.4 | 0 |  | A
2.2 | S/I WITH SINGLE EARTH SWITCH | NOS | 515000 | 2 | 1030000 | 185400 | 1215400 | 2 | 1030000 | 0 | 0% | 2 | 1030000 | 0 |  | 0 | 0 | 1030000 | 185400 | 1215400 | 0 |  | A
2.3 | BEAM MOUNTED S/I WITHOUT EARTH SWITCH | NOS | 320772 | 2 | 641544 | 115477.92 | 757021.92 | 2 | 641544 | 0 | 0% | 2 | 641544 | 0 |  | 0 | 0 | 641544 | 115477.92 | 757021.92 | 0 |  | A
3 | 245 KV, 4400pF, 3CORE, SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS | 164800 | 6 | 988800 | 177984 | 1166784 | 6 | 988800 | 0 | 0% | 6 | 988800 | 0 |  | 0 | 0 | 988800 | 177984 | 1166784 | 0 |  | A
4 | 245KV, 3150A, 40KA, SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 1353715 | 2 | 2707430 | 487337.4 | 3194767.4 | 2 | 2707430 | 0 | 0% | 2 | 2707430 | 0 |  | 0 | 0 | 2707430 | 487337.4 | 3194767.4 | 0 |  | A
5 | 216KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 216KV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 55091 | 6 | 330546 | 59498.28 | 390044.28 | 6 | 330546 | 0 | 0% | 6 | 330546 | 0 |  | 0 | 0 | 330546 | 59498.28 | 390044.28 | 0 |  | A
6 | 220 KV Post Insulators | NOS | 20600 | 16 | 329600 | 59328 | 388928 | 16 | 329600 | 0 | 0% | 16 | 329600 | 0 |  | 0 | 0 | 329600 | 59328 | 388928 | 0 |  | A
7 | BUS BAR & CIRCUIT MATERIALS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1 | LONG ROD ANTIFOG TYPE PORCELAIN INSULATOR |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1.1 | 160 KN INSULATOR | NOS | 13774 | 50 | 688700 | 123966 | 812666 | 42 | 578508 | -8 | -16% | 42 | 578508 | 0 |  | 0 | 0 | 578508 | 104131.44 | 682639.44 | -130026.56 |  | B
7.1.2 | 90 KN INSULATOR | NOS | 9895 | 25 | 247375 | 44527.5 | 291902.5 | 24 | 237480 | -1 | -4% | 24 | 237480 | 0 |  | 0 | 0 | 237480 | 42746.4 | 280226.4 | -11676.1 |  | B
7.2 | ACSR MOOSE CONDUCTOR | KMS | 412000 | 0.7 | 288400 | 51912 | 340312 | 1.125 | 463500 | 0.425 | 60.71% | 0.875 | 360500 | 0.25 | 409923 | 409923 | 102480.75 | 462980.75 | 83336.535 | 546317.285 | 206005.285 | Increse of quantity as per the approved layout. | B
7.3 | IPS 4" ALUMINIUM TUBES(114.2 mm OD, & 8.51mm Thickness) for equipment to equipment connection in 220 KV side. | MTRS | 2884 | 250 | 721000 | 129780 | 850780 | 184.25 | 531377 | -65.75 | -26.3% | 184.25 | 531377 | 0 |  | 0 | 0 | 531377 | 95647.86 | 627024.86 | -223755.14 |  | B
8 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
8.1 | 220 KV Double Tension( 160KN) H/W fitting for twin moose ACSR | NOS | 4321 | 12 | 51852 | 9333.36 | 61185.36 | 12 | 51852 | 0 | 0% | 12 | 51852 | 0 |  | 0 | 0 | 51852 | 9333.36 | 61185.36 | 0 |  | A
8.2 | 220 KV Single Tension(160KN) H/W fitting for single moose ACSR | NOS | 2331 | 24 | 55944 | 10069.92 | 66013.92 | 18 | 41958 | -6 | -25% | 18 | 41958 | 0 |  | 0 | 0 | 41958 | 7552.44 | 49510.44 | -16503.48 |  | B
8.3 | 220 KV Double Suspension(90 KN)H/W fitting for twin mose ACSR | NOS | 3532 | 6 | 21192 | 3814.56 | 25006.56 | 6 | 21192 | 0 | 0% | 6 | 21192 | 0 |  | 0 | 0 | 21192 | 3814.56 | 25006.56 | 0 |  | A
8.4 | 220 KV Single Suspension(90 KN)H/W fitting for single mose ACSR | NOS | 1484 | 12 | 17808 | 3205.44 | 21013.44 | 12 | 17808 | 0 | 0% | 12 | 17808 | 0 |  | 0 | 0 | 17808 | 3205.44 | 21013.44 | 0 |  | A
8.5 | T- clamp for ACSR ZEBRA run to ACSR MOOSE drop | NOS | 766 | 20 | 15320 | 2757.6 | 18077.6 | 30 | 22980 | 10 | 50% | 25 | 19150 | 5 | 766 | 766 | 3830 | 22980 | 4136.4 | 27116.4 | 9038.8 | Increse of quantity as per the approved layout. | B
8.6 | T-Clamp for single Moose -Single Moose ACSR | NOS | 778 | 10 | 7780 | 1400.4 | 9180.4 | 24 | 18672 | 14 | 140% | 13 | 10114 | 11 | 778 | 778 | 8558 | 18672 | 3360.96 | 22032.96 | 12852.56 | Increse of quantity as per the approved layout. | B
8.7 | T-Clamp for twin Moose run -Single Moose drop ACSR | NOS | 1585 | 12 | 19020 | 3423.6 | 22443.6 | 12 | 19020 | 0 | 0% | 12 | 19020 | 0 |  | 0 | 0 | 19020 | 3423.6 | 22443.6 | 0 |  | A
8.8 | 220 KV PI clamp | NOS | 637 | 16 | 10192 | 1834.56 | 12026.56 | 16 | 10192 | 0 | 0% | 16 | 10192 | 0 |  | 0 | 0 | 10192 | 1834.56 | 12026.56 | 0 |  | A
8.9 | Spacer for Moose ACSR | NOS | 526 | 50 | 26300 | 4734 | 31034 | 50 | 26300 | 0 | 0% | 50 | 26300 | 0 |  | 0 | 0 | 26300 | 4734 | 31034 | 0 |  | A
8.10 | 220 KV Isolator pad clamp | NOS | 707 | 60 | 42420 | 7635.6 | 50055.6 | 60 | 42420 | 0 | 0% | 60 | 42420 | 0 |  | 0 | 0 | 42420 | 7635.6 | 50055.6 | 0 |  | A
8.11 | 220 KV LA Clamp | NOS | 707 | 6 | 4242 | 763.56 | 5005.56 | 6 | 4242 | 0 | 0% | 6 | 4242 | 0 |  | 0 | 0 | 4242 | 763.56 | 5005.56 | 0 |  | A
8.12 | 220 KV CB Clamp | NOS | 707 | 12 | 8484 | 1527.12 | 10011.12 | 12 | 8484 | 0 | 0% | 12 | 8484 | 0 |  | 0 | 0 | 8484 | 1527.12 | 10011.12 | 0 |  | A
8.13 | 220 KV CVT Clamp | NOS | 902 | 6 | 5412 | 974.16 | 6386.16 | 6 | 5412 | 0 | 0% | 6 | 5412 | 0 |  | 0 | 0 | 5412 | 974.16 | 6386.16 | 0 |  | A
8.14 | 220 KV CT Clamp | NOS | 902 | 6 | 5412 | 974.16 | 6386.16 | 12 | 10824 | 6 | 100% | 8 | 7216 | 4 | 902 | 902 | 3608 | 10824 | 1948.32 | 12772.32 | 6386.16 | Cosidered for 6 nos. of CT | B
8.15 | PG Clamp for ACSR Moose | NOS | 539 | 20 | 10780 | 1940.4 | 12720.4 | 20 | 10780 | 0 | 0% | 20 | 10780 | 0 |  | 0 | 0 | 10780 | 1940.4 | 12720.4 | 0 |  | A
9 | SUBSTATION EARTHING SYSTEMS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
9.1 | EARTHING CONDUCTOR FOR BURRIAL : 75X10 mm GI Flat for laying (spacing maximum 5m both way) | MT | 82400 | 8.1875 | 674650 | 121437 | 796087 | 7.657 | 630936.8 | -0.5305 | -6.479% | 7.657 | 630936.8 | 0 |  | 0 | 0 | 630936.8 | 113568.624 | 744505.424 | -51581.576 |  | B
9.2 | EARTHING CONDUCTOR: 50X6 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MT | 82400 | 5.1 | 420240 | 75643.2 | 495883.2 | 4.72 | 388928 | -0.38 | -7.451% | 4.72 | 388928 | 0 |  | 0 | 0 | 388928 | 70007.04 | 458935.04 | -36948.16 |  | B
9.3 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos. | 1767 | 30 | 53010 | 9541.8 | 62551.8 | 25 | 44175 | -5 | -16.67% | 25 | 44175 | 0 |  | 0 | 0 | 44175 | 7951.5 | 52126.5 | -10425.3 |  | B
9.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | Nos. | 2090 | 30 | 62700 | 11286 | 73986 | 30 | 62700 | 0 | 0% | 30 | 62700 | 0 |  | 0 | 0 | 62700 | 11286 | 73986 | 0 |  | A
10 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 796 | 500 | 398000 | 71640 | 469640 | 190 | 151240 | -310 | -62% | 190 | 151240 | 0 |  | 0 | 0 | 151240 | 27223.2 | 178463.2 | -291176.8 |  | B
10.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 618 | 500 | 309000 | 55620 | 364620 | 95 | 58710 | -405 | -81% | 95 | 58710 | 0 |  | 0 | 0 | 58710 | 10567.8 | 69277.8 | -295342.2 |  | B
10.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 416 | 200 | 83200 | 14976 | 98176 | 378 | 157248 | 178 | 89% | 250 | 104000 | 128 | 416 | 416 | 53248 | 157248 | 28304.64 | 185552.64 | 87376.64 | Incresed as per the approved layout & cable schedule | B
10.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 82400 | 1 | 82400 | 14832 | 97232 | 1 | 82400 | 0 | 0% | 1 | 82400 | 0 |  | 0 | 0 | 82400 | 14832 | 97232 | 0 |  | A
11 | SUB STATION SWITCYARD BMK,AC CONSOLE & OTHER MARSHALLING BOXES (The boxes shall be 3mm thick Al. Alloy) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
11.1 | BAY MARSHALLING KIOSK (01 nos on 220 kV bay ) | NOS | 58858 | 1 | 58858 | 10594.44 | 69452.44 | 1 | 58858 | 0 | 0% | 1 | 58858 | 0 |  | 0 | 0 | 58858 | 10594.44 | 69452.44 | 0 |  | A
11.2 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 no in 220 kV bay ) | NOS | 41200 | 1 | 41200 | 7416 | 48616 | 1 | 41200 | 0 | 0% | 1 | 41200 | 0 |  | 0 | 0 | 41200 | 7416 | 48616 | 0 |  | A
11.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 KV BAY) | NOS | 17658 | 1 | 17658 | 3178.44 | 20836.44 | 1 | 17658 | 0 | 0% | 1 | 17658 | 0 |  | 0 | 0 | 17658 | 3178.44 | 20836.44 | 0 |  | A
11.4 | CONSOLE BOX FOR CT, PT, CVT | NOS | 8830 | 4 | 35320 | 6357.6 | 41677.6 | 4 | 35320 | 0 | 0% | 4 | 35320 | 0 |  | 0 | 0 | 35320 | 6357.6 | 41677.6 | 0 |  | A
12 | SWITCH YARD STRUCTURES (LATTICE TYPE) FOR TOWER COLUMNS WITH SPIKES & BEAMS & FOR ALL EQUIPMENTS FOR 220 KV CLASS INCLUDING FOUNDATION BOLTS & NUTS. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.1 | DIFFERENT TYPES OF COLUMNS WITH DETAILS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.1.1 | P1S-220 KV (NOMINAL UNIT WT- 4.5 MT) (07 NOS.) | MT |  | 31.5 | 0 | 0 | 0 |  | 0 | -31.5 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.2 | DIFFERENT TYPE OF BEAMS WITH DETAILS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.2.1 | Q1-220KV (NOMINAL UNIT WT- 1.5 MT) (06 NOS.) | MT |  | 9 | 0 | 0 | 0 |  | 0 | -9 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.2.2 | Q3-220KV (NOMINAL UNIT WT-2.5 MT) (02 NOS.) | MT |  | 5 | 0 | 0 | 0 |  | 0 | -5 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 82938 | 45.5 | 3773679 | 679262.22 | 4452941.22 | 35.38 | 2934346.44 | -10.12 | -22.24% | 35.38 | 2934346.44 | 0 |  | 0 | 0 | 2934346.44 | 528182.3592 | 3462528.7992 | -990412.4208 |  | B
12.4 | EQUIPMENT SUPPORT STRUCTURES (LATTICE TYPE) FOR ALL 220KV, 132 KV & 33KV EQUIPMENTS INCLUDING FOUNDATION BOLTS & NUTS. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.1 | ISOLATORS-220KV ( SI with E/S -02 Nos.) | MT |  | 2.542 | 0 | 0 | 0 |  | 0 | -2.542 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.2 | ISOLATORS-220KV ( SI without E/S -06 Nos.) | MT |  | 7.626 | 0 | 0 | 0 |  | 0 | -7.626 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.3 | CTS-220 KV (06 nos.) | MT |  | 1.35 | 0 | 0 | 0 |  | 0 | -1.35 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.4 | CVTS-220 KV (06 nos.) | MT |  | 1.476 | 0 | 0 | 0 |  | 0 | -1.476 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.5 | Surge Arrester-220 KV ( 06 nos.) | MT |  | 1.7526 | 0 | 0 | 0 |  | 0 | -1.7526 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.4.6 | BPI-220 KV (16 nos.) | MT |  | 4.6848 | 0 | 0 | 0 |  | 0 | -4.6848 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
12.5 | TOTAL WEIGHT OF EQUIPMENT STRUCTURE | MT | 82938 | 19.4314 | 1611601.4532 | 290088.2616 | 1901689.7148 | 20.912 | 1734399.456 | 1.4806 | 7.62% | 20.912 | 1734399.456 | 0 |  | 0 | 0 | 1734399.456 | 312191.9021 | 2046591.3581 | 144901.6433 |  | B
12.6 | Total weight of GI Nuts and bolts for Columns, Beams & Equipment Structures | MT | 100058 | 3.2466 | 324845.3011 | 58472.1542 | 383317.4553 | 3.2466 | 324845.3011 | 0 | 0% | 3.2466 | 324845.3011 | 0 |  | 0 | 0 | 324845.3011 | 58472.1542 | 383317.4553 | 0 |  | A
13 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
13.1 | POWER CABLES,1.1KV,XLPE & PVC ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
13.1.1 | PVC 3.5 CX70 mm2 | MTR | 295 | 250 | 73750 | 13275 | 87025 | 260 | 76700 | 10 | 4% | 260 | 76700 | 0 |  | 0 | 0 | 76700 | 13806 | 90506 | 3481 |  | B
13.1.2 | PVC 3.5 C X 35 mm2 | MTR | 165 | 250 | 41250 | 7425 | 48675 | 250 | 41250 | 0 | 0% | 250 | 41250 | 0 |  | 0 | 0 | 41250 | 7425 | 48675 | 0 |  | A
13.1.3 | PVC 4 CX 16 mm2 | MTR | 110 | 1000 | 110000 | 19800 | 129800 |  | 0 | -1000 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -129800 |  | B
13.1.4 | PVC 4CX 6 sqmm | MTR | 78 | 1000 | 78000 | 14040 | 92040 | 1500 | 117000 | 500 | 50% | 1250 | 97500 | 250 | 78 | 78 | 19500 | 117000 | 21060 | 138060 | 46020 | As per the approved cable schedule | B
13.1.5 | PVC 2CX 6 sqmm | MTR | 62 | 250 | 15500 | 2790 | 18290 | 150 | 9300 | -100 | -40% | 150 | 9300 | 0 |  | 0 | 0 | 9300 | 1674 | 10974 | -7316 |  | B
13.2 | CONTROL CABLES,1.1 KV, PVC,FRLS STRANDED COPPER, ARMOURED (As per specification) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
13.2.1 | 2 CX 2.5 mm2 | MTR | 83 | 1000 | 83000 | 14940 | 97940 | 330 | 27390 | -670 | -67% | 330 | 27390 | 0 |  | 0 | 0 | 27390 | 4930.2 | 32320.2 | -65619.8 |  | B
13.2.2 | 4 CX 2.5 mm2 | MTR | 130 | 2500 | 325000 | 58500 | 383500 |  | 0 | -2500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -383500 |  | B
13.2.3 | 5 CX 2.5 mm2 | MTR | 157 | 2500 | 392500 | 70650 | 463150 | 350 | 54950 | -2150 | -86% | 350 | 54950 | 0 |  | 0 | 0 | 54950 | 9891 | 64841 | -398309 |  | B
13.2.4 | 7CX 2.5 mm2 | MTR | 209 | 2000 | 418000 | 75240 | 493240 | 130 | 27170 | -1870 | -93.5% | 130 | 27170 | 0 |  | 0 | 0 | 27170 | 4890.6 | 32060.6 | -461179.4 |  | B
13.2.5 | 10 CX 2.5 mm2 | MTR | 277 | 2500 | 692500 | 124650 | 817150 | 2400 | 664800 | -100 | -4% | 2400 | 664800 | 0 |  | 0 | 0 | 664800 | 119664 | 784464 | -32686 |  | B
13.2.6 | 12 CX 2.5 mm2 | MTR | 319 | 1500 | 478500 | 86130 | 564630 | 700 | 223300 | -800 | -53.33% | 700 | 223300 | 0 |  | 0 | 0 | 223300 | 40194 | 263494 | -301136 |  | B
13.2.7 | 16 CX 2.5 mm2 | MTR | 425 | 1500 | 637500 | 114750 | 752250 | 600 | 255000 | -900 | -60% | 600 | 255000 | 0 |  | 0 | 0 | 255000 | 45900 | 300900 | -451350 |  | B
13.2.8 | 19 CX 2.5 mm2 | MTR | 486 | 1500 | 729000 | 131220 | 860220 | 500 | 243000 | -1000 | -66.67% | 500 | 243000 | 0 |  | 0 | 0 | 243000 | 43740 | 286740 | -573480 |  | B
13.2.9 | 4 CX 4 mm2 | MTR | 187 | 500 | 93500 | 16830 | 110330 |  | 0 | -500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -110330 |  | B
13.2.10 | 7 CX 4 mm2 | MTR | 308 | 250 | 77000 | 13860 | 90860 |  | 0 | -250 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -90860 |  | B
13.2.11 | 12 CX 4 mm2 | MTR | 531 | 250 | 132750 | 23895 | 156645 |  | 0 | -250 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -156645 |  | B
14 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
14.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (150W LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | SET | 10089 | 15 | 151335 | 27240.3 | 178575.3 | 15 | 151335 | 0 | 0% | 15 | 151335 | 0 |  | 0 | 0 | 151335 | 27240.3 | 178575.3 | 0 |  | A
14.2 | STREET LIGHTING, IT INCLUDES SUPPLY OF GI TUBULAR POLE, WITH 100WATT LED LIGHTING FIXTURES WITH LAMPS of reputed make (Philips/CGL/Bajaj)(TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | SET | 18835 | 5 | 94175 | 16951.5 | 111126.5 | 5 | 94175 | 0 | 0% | 5 | 94175 | 0 |  | 0 | 0 | 94175 | 16951.5 | 111126.5 | 0 |  | A
15 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM, EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-INST TO BIDDER BEFORE DESIGN-SL NO 16-ANNEXURE - I) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
15.1 | FOAM TYPE-9 LTRS | NOS | 3238 | 2 | 6476 | 1165.68 | 7641.68 | 2 | 6476 | 0 | 0% | 2 | 6476 | 0 |  | 0 | 0 | 6476 | 1165.68 | 7641.68 | 0 |  | A
15.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 19424 | 2 | 38848 | 6992.64 | 45840.64 | 2 | 38848 | 0 | 0% | 2 | 38848 | 0 |  | 0 | 0 | 38848 | 6992.64 | 45840.64 | 0 |  | A
15.3 | DRY POWDER TYPE - 5 KGS | NOS | 14127 | 2 | 28254 | 5085.72 | 33339.72 | 2 | 28254 | 0 | 0% | 2 | 28254 | 0 |  | 0 | 0 | 28254 | 5085.72 | 33339.72 | 0 |  | A
15.4 | CO2 - 4.5 KGS | NOS | 7535 | 4 | 30140 | 5425.2 | 35565.2 | 4 | 30140 | 0 | 0% | 4 | 30140 | 0 |  | 0 | 0 | 30140 | 5425.2 | 35565.2 | 0 |  | A
15.5 | CO2 - 9 KGS | NOS | 7535 | 4 | 30140 | 5425.2 | 35565.2 | 4 | 30140 | 0 | 0% | 4 | 30140 | 0 |  | 0 | 0 | 30140 | 5425.2 | 35565.2 | 0 |  | A
15.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 25898 | 2 | 51796 | 9323.28 | 61119.28 | 2 | 51796 | 0 | 0% | 2 | 51796 | 0 |  | 0 | 0 | 51796 | 9323.28 | 61119.28 | 0 |  | A
15.7 | 9 litre water type | Nos. | 2179 | 2 | 4358 | 784.44 | 5142.44 | 2 | 4358 | 0 | 0% | 2 | 4358 | 0 |  | 0 | 0 | 4358 | 784.44 | 5142.44 | 0 |  | A
15.8 | 50 Litres Mechanical Foam type | Nos. | 7652 | 2 | 15304 | 2754.72 | 18058.72 | 2 | 15304 | 0 | 0% | 2 | 15304 | 0 |  | 0 | 0 | 15304 | 2754.72 | 18058.72 | 0 |  | A
15.9 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 560 | 2 | 1120 | 201.6 | 1321.6 | 2 | 1120 | 0 | 0% | 2 | 1120 | 0 |  | 0 | 0 | 1120 | 201.6 | 1321.6 | 0 |  | A
16 | 220 KV SIDE AUTOMATION , PROTECTION & OTHER PANELS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
| SUBSTATION AUTOMATION SYSTEM: Supply of the following 220 kV level consisting of Panels, Bay control Units, DP Relays, Numerical O/C & E/F Relays, DC Supervision relays, Trip Circuit Supervision, Trip Relay ,Test Block, Differential and REF, Overfluxing, High impednce REF, Numerical O/C & E/F relay,Transformer trouble relay etc. Station level consisting of Industrial Computer with accessories, PC with accessories, laser printer, UPS, GPS System & Numerical bay control unit etc. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
16.1 | Sub-Station Automation (in PRP as per the indicative drg ) system (for 02 nos. 220 KV side line feeder bays ),other accessories ( Relays,auxiliary system, Ethernet Switches ,FO Patch cords, LIU,Multimode glass fibre Doublle jacket armoured optical cables, Red boxes etc . (i) Line Interface Unit(LIU) - as per requirement (for 220KV side),(ii)Managed Ethernet switch IEC 61850-3, IEEE1588v2 as per requirement,(iii) Multimode glass fibre optical cord Double Jacketted armoured, rodent sillient of required length,(iv) HDPE pipes for laying of FO cable of required length in all respect to integrate with the existing SAS system. | LS | 2191840 | 1 | 2191840 | 394531.2 | 2586371.2 | 1 | 2191840 | 0 | 0% | 1 | 2191840 | 0 |  | 0 | 0 | 2191840 | 394531.2 | 2586371.2 | 0 |  | A
16.2 | 220 KV SIDE PROTECTION & OTHER PANELS for SAS and Bus Bar protn. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
16.2.1 | BCU based FEEDER PROTECTION RELAY PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Numerical Bay control unit (BCU) (48DI, 32DO, IEC 61850 protocol with PRP ) for substation automation system. | Nos. | 825178 | 2 | 1650356 | 297064.08 | 1947420.08 | 2 | 1650356 | 0 | 0% | 2 | 1650356 | 0 |  | 0 | 0 | 1650356 | 297064.08 | 1947420.08 | 0 |  | A
16.2.2 | Bus Bar Protection system in all respect to integrate with the existing system for above two nos 220 KV Line Feeders (including supply of relays,auxiliary relays,switches,FO cables,Managed Switches etc). | Nos. | 492047 | 2 | 984094 | 177136.92 | 1161230.92 | 2 | 984094 | 0 | 0% | 2 | 984094 | 0 |  | 0 | 0 | 984094 | 177136.92 | 1161230.92 | 0 |  | A
17 | Switch Yard AC Kiosk for 220 KV Switchyards :5000 mm (L)x4000mm (W)x 3300mm (H) with Air Conditioning as per the Specification; | Nos. | 706287 | 1 | 706287 | 127131.66 | 833418.66 | 1 | 706287 | 0 | 0% | 1 | 706287 | 0 |  | 0 | 0 | 706287 | 127131.66 | 833418.66 | 0 |  | A
18 | WALKIE TALKIE SET | SET | 35315 | 1 | 35315 | 6356.7 | 41671.7 | 1 | 35315 | 0 | 0% | 1 | 35315 | 0 |  | 0 | 0 | 35315 | 6356.7 | 41671.7 | 0 |  | A
19 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NO | 8830 | 4 | 35320 | 6357.6 | 41677.6 | 4 | 35320 | 0 | 0% | 4 | 35320 | 0 |  | 0 | 0 | 35320 | 6357.6 | 41677.6 | 0 |  | A
20 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
20.1 | 24 fibre optic approach cable along with installation hardware including HDPE pipes | KM | 176572 | 1 | 176572 | 31782.96 | 208354.96 | 1 | 176572 | 0 | 0% | 1 | 176572 | 0 |  | 0 | 0 | 176572 | 31782.96 | 208354.96 | 0 |  | A
20.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 306058 | 2 | 612116 | 110180.88 | 722296.88 | 2 | 612116 | 0 | 0% | 2 | 612116 | 0 |  | 0 | 0 | 612116 | 110180.88 | 722296.88 | 0 |  | A
20.3 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 111830 | 1 | 111830 | 20129.4 | 131959.4 | 1 | 111830 | 0 | 0% | 1 | 111830 | 0 |  | 0 | 0 | 111830 | 20129.4 | 131959.4 | 0 |  | A
A | SUPPLY COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION-220 KV BAY EXTENSION |  |  |  | 32199184.7543 | 5795853.2558 | 37995038.01 |  | 28213265.9971 |  | 0% |  | 28021521.9971 |  |  |  | 191224.75 | 28212746.7471 | 5078294.4145 | 33291041.1615 | -4703996.8485

## S_220kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
SUPPLY - 220kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment |  | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | Cost Data Rate | Least Cost | Amount
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats, different type of G.I HT Nuts & Bolts, washer, spring washer for the towers, hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specificationand designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). Note: Weight as indicated are tentative |  |  |  | 0 |  |  |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | A
1.1 | STUBS & CLEATS |  |  |  | 0 |  |  |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.1 | OA TYPE(NOMINAL UNIT WEIGHT 0.232 MT) | Nos |  | 146 | 0 | 0 | 0 | 142 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.2 | OB TYPE (NOMINAL UNIT WEIGHT 0.437 MT) | Nos |  | 50 | 0 | 0 | 0 | 48 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.3 | OC TYPE (NOMINAL UNIT WEIGHT 0.776 MT) | Nos |  | 24 | 0 | 0 | 0 | 32 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4 | UR TYPE (NOMINAL UNIT WEIGHT 0.697 MT) | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2 | TOWER SUPER STRUCTURES |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.242 MT) | Nos |  | 146 | 0 | 0 | 0 | 142 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.2 | +3 EXTENSION (NOMINAL UNIT WEIGHT 0.725MT) | Nos |  | 30 | 0 | 0 | 0 | 26 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.3 | +6 EXTENSION (NOMINAL UNIT WEIGHT 1.448 MT) | Nos |  | 2 | 0 | 0 | 0 | 11 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.4 | OB TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 6.343 MT) | Nos |  | 50 | 0 | 0 | 0 | 48 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.5 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.242 MT) | Nos |  | 4 | 0 | 0 | 0 | 13 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.6 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.597 MT) | Nos |  | 0 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.7 | OC TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.01MT) | Nos |  | 24 | 0 | 0 | 0 | 32 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.8 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.474MT) | Nos |  | 2 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.9 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.597 MT) | Nos |  | 5 | 0 | 0 | 0 | 10 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.10 | UR TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 12.474 MT) | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.11 | UR+6 EXTENSION (NOMINAL UNIT WEIGHT 4.148 MT) | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3 | TEMPLATES (Hot dip galvanised) Note: Weight as indicated are tentative |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.1 | OA (NOMINAL UNIT WEIGHT 0.579 MT) | Nos |  | 15 | 0 | 0 | 0 | 15 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.2 | OB (NOMINAL UNIT WEIGHT 0.815 MT) | Nos |  | 5 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.3 | OC (NOMINAL UNIT WEIGHT 0.984 MT) | Nos |  | 5 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.4 | UR+6 (NOMINAL UNIT WEIGHT 1.510 MT) | Nos |  | 1 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.4 | WEIGHT OF THE STRUCTURES & Tempates including Tower Stub | MT | 89153 | 1326.443 | 118256372.779 | 21286147.1002 | 139542519.8792 | 1993.8708 | 177759565.2155 | 667.4278 | 50.32% | 1658.0538 | 147820465.9737 | 335.8171 | 88000 | 88000 | 29551902.16 | 177372368.1337 | 31927026.2641 | 209299394.3978 | 69756874.5186 | For considerartion of Wind Zone-6 instead of Wind Zone-5 considered in estimate | B
1.5 | Weight of different type G.I Nuts and Bolts | MT | 103831 | 66.322 | 6886279.582 | 1239530.3248 | 8125809.9068 | 91.4837 | 9498841.5108 | 25.1617 | 37.94% | 82.9025 | 8607849.4775 | 8.5812 | 115450 | 103831 | 890992.0333 | 9498841.5108 | 1709791.472 | 11208632.9828 | 3082823.076 |  | B
1.6 | Conducting type test on designed Transmission line towers suitable for Wind Zone-VI: a) Preparation of Structural drawings, fabrication drawing, Shop floor drawings, proto-corrected structural & shop floor drawings and Bill of material with Single line diagram of Tower; b) Fabrication, galvanization and proto-assembly of Steel tower structures as per approved structural drawings. c) Transportation of Tower Structures including BOM verification at the Tower testing beds of Testing Lab. d) In case of pre-mature failure (major/minor) the following activities are required to be carried out by the manufacturer: • Modification in structural drawings, shop drawings and BOM as per revision of the tower design • Fabrication, galvanization, transportation of the modified members to the testing agency Laboratories. e) Lifting back the scrap tower material after completion of tests including loading and transportation from Testing Agency Laboratories. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.6.1 | OA type Tower | Nos | 1414040 | 1 | 1414040 | 254527.2 | 1668567.2 | 1 | 1414040 | 0 | 0% | 1 | 1414040 | 0 |  | 0 | 0 | 1414040 | 254527.2 | 1668567.2 | 0 |  | A
1.6.2 | OB Type Tower | Nos | 1702620 | 1 | 1702620 | 306471.6 | 2009091.6 | 1 | 1702620 | 0 | 0% | 1 | 1702620 | 0 |  | 0 | 0 | 1702620 | 306471.6 | 2009091.6 | 0 |  | A
1.6.3 | OC Type Tower | Nos | 2135489 | 1 | 2135489 | 384388.02 | 2519877.02 | 1 | 2135489 | 0 | 0% | 1 | 2135489 | 0 |  | 0 | 0 | 2135489 | 384388.02 | 2519877.02 | 0 |  | A
1.6.4 | UR Type Tower | Nos | 2712649 | 1 | 2712649 | 488276.82 | 3200925.82 | 0 | 0 | -1 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -3200925.82 |  | B
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | EARTHING DEVICE | Nos. | 2556 | 298 | 761688 | 137103.84 | 898791.84 | 237 | 605772 | -61 | -20.47% | 237 | 605772 | 0 |  | 0 | 0 | 605772 | 109038.96 | 714810.96 | -183980.88 |  | B
2.2 | DANGER BOARD | Nos. | 188 | 222 | 41736 | 7512.48 | 49248.48 | 231 | 43428 | 9 | 4.054% | 231 | 43428 | 0 |  | 0 | 0 | 43428 | 7817.04 | 51245.04 | 1996.56 |  | B
2.3 | NUMBER PLATE | Nos. | 188 | 222 | 41736 | 7512.48 | 49248.48 | 231 | 43428 | 9 | 4.054% | 231 | 43428 | 0 |  | 0 | 0 | 43428 | 7817.04 | 51245.04 | 1996.56 |  | B
2.4 | PHASE PLATE | Nos. | 95 | 1332 | 126540 | 22777.2 | 149317.2 | 1384 | 131480 | 52 | 3.904% | 1384 | 131480 | 0 |  | 0 | 0 | 131480 | 23666.4 | 155146.4 | 5829.2 |  | B
2.5 | BIRD GUARD | Nos. | 503 | 876 | 440628 | 79313.04 | 519941.04 | 890 | 447670 | 14 | 1.598% | 890 | 447670 | 0 |  | 0 | 0 | 447670 | 80580.6 | 528250.6 | 8309.56 |  | B
2.6 | ANTICLIMBING DEVICE | Nos. | 5657 | 222 | 1255854 | 226053.72 | 1481907.72 | 231 | 1306767 | 9 | 4.054% | 231 | 1306767 | 0 |  | 0 | 0 | 1306767 | 235218.06 | 1541985.06 | 60077.34 |  | B
2.7 | CIRCUIT PLATE | Nos. | 95 | 444 | 42180 | 7592.4 | 49772.4 | 461 | 43795 | 17 | 3.829% | 461 | 43795 | 0 |  | 0 | 0 | 43795 | 7883.1 | 51678.1 | 1905.7 |  | B
3 | Supply of following POWER CONDUCTORS in the proposed 220kV lines including provision for sag and wastage as per the technical specification and as per the instruction of the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | ACSR Zebra (54/7/3.18mm) | Kms. | 311234 | 373 | 116090282 | 20896250.76 | 136986532.76 | 375 | 116712750 | 2 | 0.5362% | 375 | 116712750 | 0 |  | 0 | 0 | 116712750 | 21008295 | 137721045 | 734512.24 |  | B
4 | POWER CONDUCTOR ACESSORIES |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | For ACSR ZEBRA |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1.1 | VIBRATION DAMPER | Nos. | 1148 | 2664 | 3058272 | 550488.96 | 3608760.96 | 3757 | 4313036 | 1093 | 41.03% | 3330 | 3822840 | 427 | 746.8 | 746.8 | 318883.6 | 4141723.6 | 745510.248 | 4887233.848 | 1278472.888 | As per the requirement in line, calculation enclosed | B
4.1.2 | MID SPAN JOINT | Nos. | 1461 | 50 | 73050 | 13149 | 86199 | 50 | 73050 | 0 | 0% | 50 | 73050 | 0 |  | 0 | 0 | 73050 | 13149 | 86199 | 0 |  | A
4.1.3 | Repair Sleeve | Nos. | 264 | 50 | 13200 | 2376 | 15576 | 50 | 13200 | 0 | 0% | 50 | 13200 | 0 |  | 0 | 0 | 13200 | 2376 | 15576 | 0 |  | A
5 | Supply of the following Type Long Rod Porcelain insulators as per the technical specification and as per the instruction of the Engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | 160 KN Long Rod Antifog PORCELAIN INSULATOR | Nos. | 6011.55 | 2435 | 14638124.25 | 2634862.365 | 17272986.615 | 2460 | 14788413 | 25 | 1.027% | 2460 | 14788413 | 0 |  | 0 | 0 | 14788413 | 2661914.34 | 17450327.34 | 177340.725 |  | B
5.2 | 90 KN Long Rod Antifog PORCELAIN INSULATOR | Nos. | 4641 | 2074 | 9625434 | 1732578.12 | 11358012.12 | 1947 | 9036027 | -127 | -6.123% | 1947 | 9036027 | 0 |  | 0 | 0 | 9036027 | 1626484.86 | 10662511.86 | -695500.26 |  | B
6 | Supply of the following hard ware fittings suitable for following conductors as per the technical specification. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1 | For ACSR ZEBRA |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1.1 | Single suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set | 1333 | 756 | 1007748 | 181394.64 | 1189142.64 | 887 | 1182371 | 131 | 17.33% | 887 | 1182371 | 0 |  | 0 | 0 | 1182371 | 212826.78 | 1395197.78 | 206055.14 |  | B
6.1.2 | Double suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set | 3172 | 120 | 380640 | 68515.2 | 449155.2 | 43 | 136396 | -77 | -64.17% | 43 | 136396 | 0 |  | 0 | 0 | 136396 | 24551.28 | 160947.28 | -288207.92 |  | B
6.1.3 | Single tension Hard wares fittings, suitable for 160 KN Long Rod insulator. | Set | 2094 | 662 | 1386228 | 249521.04 | 1635749.04 | 791 | 1656354 | 129 | 19.49% | 791 | 1656354 | 0 | - | 0 | 0 | 1656354 | 298143.72 | 1954497.72 | 318748.68 |  | B
6.1.4 | Double tension Hard wares fittings, suitable for 160 KN Log Rod insulator. | Set | 3880 | 250 | 970000 | 174600 | 1144600 | 216 | 838080 | -34 | -13.6% | 216 | 838080 | 0 |  | 0 | 0 | 838080 | 150854.4 | 988934.4 | -155665.6 |  | B
7 | “D” Shackle | Nos. | 264 | 912 | 240768 | 43338.24 | 284106.24 | 936 | 247104 | 24 | 2.632% | 936 | 247104 | 0 |  | 0 | 0 | 247104 | 44478.72 | 291582.72 | 7476.48 |  | B
8 | Hanger | Nos. | 582 | 876 | 509832 | 91769.76 | 601601.76 | 847 | 492954 | -29 | -3.311% | 847 | 492954 | 0 |  | 0 | 0 | 492954 | 88731.72 | 581685.72 | -19916.04 |  | B
9 | U'-Bolt. | Nos | 212 | 60 | 12720 | 2289.6 | 15009.6 | 43 | 9116 | -17 | -28.33% | 43 | 9116 | 0 |  | 0 | 0 | 9116 | 1640.88 | 10756.88 | -4252.72 |  | B
10 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.1 | 24Fibre(DWSM) OPGW fibre Optic cable | KM | 174930.5 | 62 | 10845691 | 1952224.38 | 12797915.38 | 62 | 10845691 | 0 | 0% | 62 | 10845691 | 0 |  | 0 | 0 | 10845691 | 1952224.38 | 12797915.38 | 0 |  | A
10.2 | OPGW hardwarw set like suspension assembly, Tension assembly(Dead end assembly, Pass through assembly), Vibration damper, Down Lead clamp Assemblies for 24F, 48 fibre(DWSM) OPGW, Joint box | KM | 52711 | 62 | 3268082 | 588254.76 | 3856336.76 | 62 | 3268082 | 0 | 0% | 62 | 3268082 | 0 |  | 0 | 0 | 3268082 | 588254.76 | 3856336.76 | 0 |  | A
B | SUPPLY COMPONENT OF THE WORKS CONTRACT FOR 220 KV TRANSMISSION LINE-PRATAPSASAN-ERSAMA |  |  |  | 297937883.611 | 53628819.05 | 351566702.661 |  | 358745519.7263 |  | 0% |  | 327425232.4512 |  |  |  | 30761777.7933 | 358187010.2446 | 64473661.844 | 422660672.0886 | 71093969.4276

## S_400kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
SUPPLY - 400kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | Cost Data Rate | Least Cost | Amount
1 | SUPPLY of Following type tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the towers ,hanger and all accessories, tower super structure complete including step bolts. Supply of black bituminous paint for three coats up to a height of 500mm above the cooping(legs & bracing members). All Supply should confirm to the Technical Specification and the structures are to be designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec.(As per BIS 802). (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). Note:Weight as indicated are tentative. |  |  |  | 0 |  |  |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1.1 | TOWER STRUCTURES |  |  |  | 0 |  |  |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.1 | DA TYPE (SUSPENSION ) TOWERS (Nominal unit weight 11.884 MT) | Nos. |  | 100 | 0 | 0 | 0 | 97 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.2 | +3 EXTENSION (Nominal unit weight 2.085 MT) | Nos. |  | 31 | 0 | 0 | 0 | 46 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.3 | +6 EXTENSION (Nominal unit weight 2.958MT) | Nos. |  | 6 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4 | +9 EXTENSION (Nominal unit weight 3.988MT) | Nos. |  | 4 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4.1 | +15 EXTENSION (Nominal unit weight 3.988MT) | Nos. |  | 0 | 0 | 0 | 0 | 3 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.5 | DB TYPE (15 deg ANGLE ) TOWERS (Nominal unit weight 19.337MT) | Nos. |  | 20 | 0 | 0 | 0 | 20 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.6 | +3 EXTENSION (Nominal unit weight 3.04 MT) | Nos. |  | 4 | 0 | 0 | 0 | 6 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.7 | +6 EXTENSION (Nominal unit weight 4.791 MT) | Nos. |  | 3 | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.8 | +9 EXTENSION (Nominal unit weight 6.295 MT) | Nos. |  | 3 | 0 | 0 | 0 | 1 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.9 | DC TYPE (30 deg ANGLE ) TOWERS (Nominal unit weight 22.895 MT) | Nos. |  | 14 | 0 | 0 | 0 | 14 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.10 | +3 EXTENSION (Nominal unit weight 3.531 MT) | Nos. |  | 2 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.11 | +6 EXTENSION (Nominal unit weight 5.432 MT) | Nos. |  | 1 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.12 | DD TYPE (60 deg angle)TOWER (Nominal unit weight 33.658 MT) | Nos. |  | 48 | 0 | 0 | 0 | 51 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.13 | +3 EXTENSION (Nominal unit weight 5.437 MT) | Nos. |  | 8 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.14 | +6 EXTENSION (Nominal unit weight 8.084 MT) | Nos. |  | 5 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.15 | +9 EXTENSION (Nominal unit weight 10.844 MT) | Nos. |  | 7 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.15.1 | +12 EXTENSION (Nominal unit weight 10.844 MT) | Nos. |  | 0 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.16 | +18 TO DD TYPE TOWER (Nominal unit weight 22.857 MT) | Nos. |  | 10 | 0 | 0 | 0 | 16 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.17 | +25 TO DD TYPE TOWER (Nominal unit weight 33.042 MT) | Nos. |  | 7 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.18 | DD(DEAD END) AT NEW DUBURI END (Nominal unit weight 33.658MT) | Nos. |  | 4 | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2 | TEMPLATES (Hot dip galvanised) Note: Weight as indicated are tentative |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.1 | DA (Nominal unit weight 1.526 MT) | Nos. |  | 5 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.2 | DB (Nominal unit weight 1.85 MT) | Nos. |  | 2 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.3 | DC (Nominal unit weight 2.053 MT) | Nos. |  | 2 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.2.4 | DD (Nominal unit weight 2.85 MT) | Nos. |  | 2 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3 | WEIGHT OF THE STRUCTURES (including Tower stubs, Templates & Foundation Nut and Bolts) | MT | 89153 | 4446.701 | 396436734.253 | 71358612.1655 | 467795346.4185 | 4484.415 | 399799054.0611 | 37.714 | 0.8481% | 4484.415 | 399799054.0611 | 0 |  | 0 | 0 | 399799054.0611 | 71963829.731 | 471762883.7921 | 3967537.3736 | As per the approved structure drawing | B
1.4 | Weight of different type G.I Nuts and Bolts | MT | 103831 | 178 | 18481918 | 3326745.24 | 21808663.24 | 183.5888 | 19062204.5396 | 5.5888 | 3.14% | 183.5888 | 19062204.5396 | 0 |  | 0 | 0 | 19062204.5396 | 3431196.8171 | 22493401.3567 | 684738.1167 | As per the approved structure drawing | B
1.5 | Conducting type test on designed Transmission line towers suitable for Wind Zone-VI: a) Preparation of Structural drawings, fabrication drawing, Shop floor drawings, proto-corrected structural & shop floor drawings and Bill of material with Single line diagram of Tower; b) Fabrication, galvanization and proto-assembly of Steel tower structures as per approved structural drawings. c) Transportation of Tower Structures including BOM verification at the Tower testing beds of Testing Lab. d) In case of pre-mature failure (major/minor) the following activities are required to be carried out by the manufacturer: • Modification in structural drawings, shop drawings and BOM as per revision of the tower design • Fabrication, galvanization, transportation of the modified members to the testing agency Laboratories. e) Lifting back the scrap tower material after completion of tests including loading and transportation from Testing Agency Laboratories. |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.5.1 | DA type Tower | Nos | 2568359 | 1 | 2568359 | 462304.62 | 3030663.62 | 1 | 2568359 | 0 | 0% | 1 | 2568359 | 0 |  | 0 | 0 | 2568359 | 462304.62 | 3030663.62 | 0 |  | A
1.5.2 | DB Type Tower | Nos | 4011257 | 1 | 4011257 | 722026.26 | 4733283.26 | 1 | 4011257 | 0 | 0% | 1 | 4011257 | 0 |  | 0 | 0 | 4011257 | 722026.26 | 4733283.26 | 0 |  | A
1.5.3 | DC Type Tower | Nos | 4588417 | 1 | 4588417 | 825915.06 | 5414332.06 | 1 | 4588417 | 0 | 0% | 1 | 4588417 | 0 |  | 0 | 0 | 4588417 | 825915.06 | 5414332.06 | 0 |  | A
1.5.4 | DD Type Tower | Nos | 6175605 | 1 | 6175605 | 1111608.9 | 7287213.9 | 1 | 6175605 | 0 | 0% | 1 | 6175605 | 0 |  | 0 | 0 | 6175605 | 1111608.9 | 7287213.9 | 0 |  | A
2 | Supply of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | EARTHING DEVICE | Nos. | 2556 | 272 | 695232 | 125141.76 | 820373.76 | 196 | 500976 | -76 | -27.94% | 196 | 500976 | 0 |  | 0 | 0 | 500976 | 90175.68 | 591151.68 | -229222.08 |  | B
2.2 | DANGER BOARD | Nos. | 188 | 186 | 34968 | 6294.24 | 41262.24 | 182 | 34216 | -4 | -2.151% | 182 | 34216 | 0 |  | 0 | 0 | 34216 | 6158.88 | 40374.88 | -887.36 |  | B
2.3 | NUMBER PLATE | Nos. | 188 | 186 | 34968 | 6294.24 | 41262.24 | 182 | 34216 | -4 | -2.151% | 182 | 34216 | 0 |  | 0 | 0 | 34216 | 6158.88 | 40374.88 | -887.36 |  | B
2.4 | PHASE PLATE | Nos. | 95 | 1116 | 106020 | 19083.6 | 125103.6 | 1092 | 103740 | -24 | -2.151% | 1092 | 103740 | 0 |  | 0 | 0 | 103740 | 18673.2 | 122413.2 | -2690.4 |  | B
2.5 | BIRD GUARD | Nos. | 503 | 600 | 301800 | 54324 | 356124 | 594 | 298782 | -6 | -1% | 594 | 298782 | 0 |  | 0 | 0 | 298782 | 53780.76 | 352562.76 | -3561.24 |  | B
2.6 | ANTICLIMBING DEVICE | Nos. | 5657 | 186 | 1052202 | 189396.36 | 1241598.36 | 182 | 1029574 | -4 | -2.151% | 182 | 1029574 | 0 |  | 0 | 0 | 1029574 | 185323.32 | 1214897.32 | -26701.04 |  | B
2.7 | Circuit plate | Nos. | 95 | 372 | 35340 | 6361.2 | 41701.2 | 364 | 34580 | -8 | -2.151% | 364 | 34580 | 0 |  | 0 | 0 | 34580 | 6224.4 | 40804.4 | -896.8 |  | B
3 | Supply of following POWER CONDUCTORS in the proposed 400 kV lines with 1.5% provision for sag and wastage as per the technical specification and as per the instruction of the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | ACSR Moose(54/7/3.53 mm) | Kms. | 407218 | 854 | 347764172 | 62597550.96 | 410361722.96 | 830 | 337990940 | -24 | -2.81% | 830 | 337990940 | 0 |  | 0 | 0 | 337990940 | 60838369.2 | 398829309.2 | -11532413.76 |  | B
4 | POWER CONDUCTOR ACESSORIES |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | For ACSR Moose( 400KV DC line) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1.1 | 4R VIBRATION DAMPER FOR SUSPENSION | Nos. | 856 | 2400 | 2054400 | 369792 | 2424192 | 2424 | 2074944 | 24 | 1% | 2424 | 2074944 | 0 |  | 0 | 0 | 2074944 | 373489.92 | 2448433.92 | 24241.92 |  | B
4.1.2 | 4R VIBRATION DAMPER FOR TENSION | Nos. | 856 | 4128 | 3533568 | 636042.24 | 4169610.24 | 4176 | 3574656 | 48 | 1.163% | 4176 | 3574656 | 0 |  | 0 | 0 | 3574656 | 643438.08 | 4218094.08 | 48483.84 |  | B
4.1.3 | MID SPAN JOINT | Nos. | 952 | 400 | 380800 | 68544 | 449344 | 360 | 342720 | -40 | -10% | 360 | 342720 | 0 |  | 0 | 0 | 342720 | 61689.6 | 404409.6 | -44934.4 |  | B
4.1.4 | Repair Sleeve | Nos. | 326 | 150 | 48900 | 8802 | 57702 | 137 | 44662 | -13 | -8.667% | 137 | 44662 | 0 |  | 0 | 0 | 44662 | 8039.16 | 52701.16 | -5000.84 |  | B
4.1.5 | Line Spacer | set | 678 | 15624 | 10593072 | 1906752.96 | 12499824.96 | 7160 | 4854480 | -8464 | -54.17% | 7160 | 4854480 | 0 |  | 0 | 0 | 4854480 | 873806.4 | 5728286.4 | -6771538.56 |  | B
4.1.6 | Rigid Spacer | set | 348 | 2064 | 718272 | 129288.96 | 847560.96 | 2006 | 698088 | -58 | -2.81% | 2006 | 698088 | 0 |  | 0 | 0 | 698088 | 125655.84 | 823743.84 | -23817.12 |  | B
5 | Supply of the following Long Rod Porcelain insulators as per the technical specification and as per the instruction of the Engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | 160 KN Long Rod PORCELAIN INSULATOR (taking 5% extra towards wastage) | Nos. | 6019.55 | 8770 | 52791453.5 | 9502461.63 | 62293915.13 | 6452 | 38838136.6 | -2318 | -26.43% | 6452 | 38838136.6 | 0 |  | 0 | 0 | 38838136.6 | 6990864.588 | 45829001.188 | -16464913.942 |  | B
5.2 | 120 KN Long Rod PORCELAIN INSULATOR (taking 5% extra towards wastage) | Nos. | 5030.15 | 6451 | 32449497.65 | 5840909.577 | 38290407.227 | 4987 | 25085358.05 | -1464 | -22.69% | 4987 | 25085358.05 | 0 |  | 0 | 0 | 25085358.05 | 4515364.449 | 29600722.499 | -8689684.728 |  | B
6 | Supply of the following hard ware fittings suitable for ACSR Moose conductors as per the technical specification. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1 | For ACSR MOOSE (400KV DC line) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1.1 | Single suspension Hard wares (AGS type) fittings for pilot insulator. | set | 25257 | 330 | 8334810 | 1500265.8 | 9835075.8 | 402 | 10153314 | 72 | 21.82% | 402 | 10153314 | 0 |  | 0 | 0 | 10153314 | 1827596.52 | 11980910.52 | 2145834.72 |  | B
6.1.2 | Double suspension Hard wares fittings.(AGS type) for ACSR Moose. | set | 10255 | 603 | 6183765 | 1113077.7 | 7296842.7 | 606 | 6214530 | 3 | 0.4975% | 606 | 6214530 | 0 |  | 0 | 0 | 6214530 | 1118615.4 | 7333145.4 | 36302.7 |  | B
6.1.3 | Double tension Hard wares fittings suitable for ACSR Moose. | set | 12950 | 1044 | 13519800 | 2433564 | 15953364 | 1044 | 13519800 | 0 | 0% | 1044 | 13519800 | 0 |  | 0 | 0 | 13519800 | 2433564 | 15953364 | 0 |  | A
7 | D SACKLE(SUITABLE FOR 20MM DIA, 75MM LONG) | Nos. | 264 | 600 | 158400 | 28512 | 186912 | 1044 | 275616 | 444 | 74% | 750 | 198000 | 294 | 264 | 264 | 77616 | 275616 | 49610.88 | 325226.88 | 138314.88 | As per tower requirement | B
8 | U' Bolt | Nos. | 212 | 200 | 42400 | 7632 | 50032 | 101 | 21412 | -99 | -49.5% | 101 | 21412 | 0 |  | 0 | 0 | 21412 | 3854.16 | 25266.16 | -24765.84 |  | B
9 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
9.1 | 24Fibre(DWSM) OPGW fibre Optic cable | KM | 174930.5 | 68 | 11895274 | 2141149.32 | 14036423.32 | 68.193 | 11929035.5865 | 0.193 | 0.2838% | 68.193 | 11929035.5865 | 0 |  | 0 | 0 | 11929035.5865 | 2147226.4056 | 14076261.9921 | 39838.6721 |  | B
9.2 | OPGW hardwarw set like suspension assembly, Tension assembly(Dead end assembly, Pass through assembly), Vibration damper, Down Lead clamp Assemblies for 24F, 48 fibre(DWSM) OPGW, Joint box | KM | 52711 | 68 | 3584348 | 645182.64 | 4229530.64 | 68.193 | 3594521.223 | 0.193 | 0.2838% | 68.193 | 3594521.223 | 0 |  | 0 | 0 | 3594521.223 | 647013.8201 | 4241535.0431 | 12004.4031 |  | B
10 | Supply of the GI earth wire of size 7/3.66 mm as per the technical specification, with 1.5% provision for Sag & Wastage and as per the direction of Engineer in charge. | Kms. | 63208 | 71 | 4487768 | 807798.24 | 5295566.24 | 69.2159 | 4374998.2912 | -1.7841 | -2.513% | 69.2159 | 4374998.2912 | 0 |  | 0 | 0 | 4374998.2912 | 787499.6924 | 5162497.9836 | -133068.2564 |  | B
11 | EARTH CONDUCTOR ACESSORIES |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
11.1 | VIBRATION DAMPER | Nos. | 647 | 544 | 351968 | 63354.24 | 415322.24 | 550 | 355850 | 6 | 1.103% | 550 | 355850 | 0 |  | 0 | 0 | 355850 | 64053 | 419903 | 4580.76 |  | B
11.2 | FLEXIBLE EARTH BOND for 7/3.66mm earth wire | Nos. | 794 | 548 | 435112 | 78320.16 | 513432.16 | 275 | 218350 | -273 | -49.82% | 275 | 218350 | 0 |  | 0 | 0 | 218350 | 39303 | 257653 | -255779.16 |  | B
11.3 | SUSPENSION CLAMP for 7/3.66mm earth wire | Nos. | 741 | 100 | 74100 | 13338 | 87438 | 101 | 74841 | 1 | 1% | 101 | 74841 | 0 |  | 0 | 0 | 74841 | 13471.38 | 88312.38 | 874.38 |  | B
11.4 | TENSION CLAMP with terminal jumper for 7/3.66mm earth wire | Nos. | 741 | 172 | 127452 | 22941.36 | 150393.36 | 174 | 128934 | 2 | 1.163% | 174 | 128934 | 0 |  | 0 | 0 | 128934 | 23208.12 | 152142.12 | 1748.76 |  | B
11.5 | MID SPAN JOINT | Nos. | 264 | 100 | 26400 | 4752 | 31152 | 30 | 7920 | -70 | -70% | 30 | 7920 | 0 |  | 0 | 0 | 7920 | 1425.6 | 9345.6 | -21806.4 |  | B
C | TOTAL OF SUPPLY COMPONENT OF THE WORKS CONTRACT FOR 400 KV TRANSMISSION LINE-DUBURI-LOC-001 to LOC-182) |  |  |  | 934078552.403 | 168134139.4325 | 1102212691.8355 |  | 902614087.3513 |  | 0% |  | 902536471.3513 |  |  |  | 77616 | 902614087.3513 | 162470535.7232 | 1065084623.0746 | -37128068.761

## E_Bay
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
ERECTION - 220kV BAY
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
PART A | ELECTRICAL WORKS |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1 | ERECTION OF SUPERSTRUCTURE : |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1 | Supply of labour,T&P and other necessary arrangements for erection of Columns,Beams,Equipments supporting structures & Nuts and Bolts | MT | 6443 | 68.18 | 439283.74 | 79071.0732 | 518354.8132 | 59.5386 | 383607.0065 | -8.6414 | -12.67% | 59.5386 | 383607.0065 | 0 |  | 0 | 0 | 383607.0065 | 69049.2612 | 452656.2677 | -65698.5455 |  | B
2 | ERECTION OF EQUIPMENTS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
| Supply of all labour ,T&P and Transportation from the site store,erections as per specification and testing commissioning etc as per the instruction of the Engineer-in-charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | 245 KV,1200-600-300A,40KA,5CORE SINGLE PHASE CURRENT TRANSFORMER(4 PS Cl & 1 0.2s Cl) | NOS | 9665 | 6 | 57990 | 10438.2 | 68428.2 | 6 | 57990 | 0 | 0% | 6 | 57990 | 0 |  | 0 | 0 | 57990 | 10438.2 | 68428.2 | 0 |  | A
2.2 | 245 KV,2000A,40KA,ISOLATORS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.2.1 | S/I WITH OUT EARTH SWITCH | NOS | 10954 | 6 | 65724 | 11830.32 | 77554.32 | 6 | 65724 | 0 | 0% | 6 | 65724 | 0 |  | 0 | 0 | 65724 | 11830.32 | 77554.32 | 0 |  | A
2.2.2 | S/I WITH SINGLE EARTH SWITCH | NOS | 12242 | 2 | 24484 | 4407.12 | 28891.12 | 2 | 24484 | 0 | 0% | 2 | 24484 | 0 |  | 0 | 0 | 24484 | 4407.12 | 28891.12 | 0 |  | A
2.2.3 | BEAM MOUNTED S/I WITHOUT EARTH SWITCH | NOS | 10954 | 2 | 21908 | 3943.44 | 25851.44 | 2 | 21908 | 0 | 0% | 2 | 21908 | 0 |  | 0 | 0 | 21908 | 3943.44 | 25851.44 | 0 |  | A
2.3 | 245 KV,4400pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS | 9665 | 6 | 57990 | 10438.2 | 68428.2 | 6 | 57990 | 0 | 0% | 6 | 57990 | 0 |  | 0 | 0 | 57990 | 10438.2 | 68428.2 | 0 |  | A
2.4 | 245KV,3150A,40KA,SF6,CIRCUIT BREAKER WITH SUPPORTING STRUCTURE | NOS | 51546 | 2 | 103092 | 18556.56 | 121648.56 | 2 | 103092 | 0 | 0% | 2 | 103092 | 0 |  | 0 | 0 | 103092 | 18556.56 | 121648.56 | 0 |  | A
2.5 | 216KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 216KV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 8376 | 6 | 50256 | 9046.08 | 59302.08 | 6 | 50256 | 0 | 0% | 6 | 50256 | 0 |  | 0 | 0 | 50256 | 9046.08 | 59302.08 | 0 |  | A
2.6 | 220 KV Bus Post Insulators | NOS | 1933 | 16 | 30928 | 5567.04 | 36495.04 | 16 | 30928 | 0 | 0% | 16 | 30928 | 0 |  | 0 | 0 | 30928 | 5567.04 | 36495.04 | 0 |  | A
3 | BUS-BAR STRINGING |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | Supply of labour,T&P and other necessary arrangements for stringing of bus bar conductors,hoisting of single or double insulator strings,Single or Double Hard-wares Fittings, Clamp & connectors, as per requirements, Jumpers, connections to Equipments,testing,commissioning etc. as per the instruction of Engineer-in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1.1 | Single conductor/Phase/Mtr. | MTR | 599 | 750 | 449250 | 80865 | 530115 | 1125 | 673875 | 375 | 50% | 937.5 | 561562.5 | 187.5 | 143.62 | 143.62 | 26928.75 | 588491.25 | 105928.425 | 694419.675 | 164304.675 | As per the approved layout | B
3.1.2 | Twin Conductor /Phase/Mtr. | MTR | 599 | 150 | 89850 | 16173 | 106023 | 150 | 89850 | 0 | 0% | 150 | 89850 | 0 |  | 0 | 0 | 89850 | 16173 | 106023 | 0 |  | A
4 | SUBSTATION EARTHING SYSTEM |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | Substation earth-mat Design, engineering, supply inclusive of corrosion protection measures if any,laying of earth-mat conductors of Hot dip galvanized flats of size 75X10mm to the approval of Project Manager, excavation, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors along with risers (of size 50X6 mm GI flats) etc back filling and good compaction,grounding driven rods(40 mm MS solid rod),perforated GI pipes for treated earth pits(with details of treatment as per IS). The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. For provision of treated earth-pit and untreated earth pit, refer the specification for designing. Provision of water taps inside the switch yard areas and peripheral treated and un-treated earth pit are required to be provided for watering the treated earth pits. The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipments. This is as per approved drawing and specification. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1.1 | 75x10 MM GI FLAT | MTRS | 110 | 1250 | 137500 | 24750 | 162250 | 1300 | 143000 | 50 | 4% | 1300 | 143000 | 0 |  | 0 | 0 | 143000 | 25740 | 168740 | 6490 |  | B
4.1.2 | 50x6 MM GI FLAT | MTRS | 77 | 2000 | 154000 | 27720 | 181720 | 2000 | 154000 | 0 | 0% | 2000 | 154000 | 0 |  | 0 | 0 | 154000 | 27720 | 181720 | 0 |  | A
4.1.3 | 40 MM MS ROD FOR NON-TREATED EARTH PIT ELECTORDE | NOS | 4510 | 30 | 135300 | 24354 | 159654 | 30 | 135300 | 0 | 0% | 30 | 135300 | 0 |  | 0 | 0 | 135300 | 24354 | 159654 | 0 |  | A
4.1.4 | 50MM GI PIPE FOR TREATED EARTH PIT ELECTRORDE WITH CHAMBER AND COVER | NOS | 4510 | 30 | 135300 | 24354 | 159654 | 25 | 112750 | -5 | -16.67% | 25 | 112750 | 0 |  | 0 | 0 | 112750 | 20295 | 133045 | -26609 |  | B
5 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 103 | 500 | 51500 | 9270 | 60770 | 190 | 19570 | -310 | -62% | 190 | 19570 | 0 |  | 0 | 0 | 19570 | 3522.6 | 23092.6 | -37677.4 |  | B
5.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 90 | 500 | 45000 | 8100 | 53100 | 95 | 8550 | -405 | -81% | 95 | 8550 | 0 |  | 0 | 0 | 8550 | 1539 | 10089 | -43011 |  | B
5.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 64 | 200 | 12800 | 2304 | 15104 | 378 | 24192 | 178 | 89% | 250 | 16000 | 128 | 67.39 | 64 | 8192 | 24192 | 4354.56 | 28546.56 | 13442.56 | As per the approved layout & cable schedule | B
5.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 9665 | 1 | 9665 | 1739.7 | 11404.7 | 1 | 9665 | 0 | 0% | 1 | 9665 | 0 |  | 0 | 0 | 9665 | 1739.7 | 11404.7 | 0 |  | A
6 | SUB STATION SWITCYARD BMK,AC CONSOLE & OTHER MARSHALLING BOXES |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1 | BAY MARSHALLING KIOSK (01 nos on 220 kV bay ) | NOS | 5799 | 1 | 5799 | 1043.82 | 6842.82 | 1 | 5799 | 0 | 0% | 1 | 5799 | 0 |  | 0 | 0 | 5799 | 1043.82 | 6842.82 | 0 |  | A
6.2 | SWITCH YARD AC CONSOLE FOR LIGHTING (01 nos on 220 kV bay ) | NOS | 2577 | 1 | 2577 | 463.86 | 3040.86 | 1 | 2577 | 0 | 0% | 1 | 2577 | 0 |  | 0 | 0 | 2577 | 463.86 | 3040.86 | 0 |  | A
6.3 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 no on 220KV BAY ) | NOS | 2577 | 1 | 2577 | 463.86 | 3040.86 | 1 | 2577 | 0 | 0% | 1 | 2577 | 0 |  | 0 | 0 | 2577 | 463.86 | 3040.86 | 0 |  | A
7 | Laying of Power and Control Cable including fixing of cable with terminal connections both at equipments and control panels with supply of and fixing of lugs,Ferrules,clamps,connectors,glands,fixing of cable trays, including supply of N&B,Link plates,Cable Markers,PVC pipes Bends,Plaster of Paris, M-Seal compounds etc for sealing purpose and all necessary arrangements,laying of Earthing Flats,earthing ,laying of Cable trench slabs and chequered plate etc for the cable trench,Cable scheduled and cable diagram to be prepared by the contractor |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1 | POWER CABLES,1.1KV,XLPE & PVC ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1.1 | PVC 3.5 CX70 mm2 | MTR | 39 | 250 | 9750 | 1755 | 11505 | 260 | 10140 | 10 | 4% | 260 | 10140 | 0 |  | 0 | 0 | 10140 | 1825.2 | 11965.2 | 460.2 |  | B
7.1.2 | PVC 3.5 CX35 mm2 | MTR | 35 | 250 | 8750 | 1575 | 10325 | 250 | 8750 | 0 | 0% | 250 | 8750 | 0 |  | 0 | 0 | 8750 | 1575 | 10325 | 0 |  | A
7.1.3 | PVC 4 CX 16 mm2 | MTR | 32 | 1000 | 32000 | 5760 | 37760 | 0 | 0 | -1000 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -37760 |  | B
7.1.4 | PVC 4CX 6 sqmm | MTR | 32 | 1000 | 32000 | 5760 | 37760 | 1500 | 48000 | 500 | 50% | 1250 | 40000 | 250 | 122.52 | 32 | 8000 | 48000 | 8640 | 56640 | 18880 | As per the approved cable schedule | B
7.1.5 | PVC 2CX 6 sqmm | MTR | 32 | 250 | 8000 | 1440 | 9440 | 150 | 4800 | -100 | -40% | 150 | 4800 | 0 |  | 0 | 0 | 4800 | 864 | 5664 | -3776 |  | B
7.2 | CONTROL CABLES,1.1 KV, PVC,FRLS,STRANDED COPPER, ARMOURED (As per specification) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.2.1 | 2 CX 2.5 mm2 | MTR | 26 | 1000 | 26000 | 4680 | 30680 | 330 | 8580 | -670 | -67% | 330 | 8580 | 0 |  | 0 | 0 | 8580 | 1544.4 | 10124.4 | -20555.6 |  | B
7.2.2 | 4 CX 2.5 mm2 | MTR | 26 | 2500 | 65000 | 11700 | 76700 | 0 | 0 | -2500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -76700 |  | B
7.2.3 | 5 CX 2.5 mm2 | MTR | 26 | 2500 | 65000 | 11700 | 76700 | 350 | 9100 | -2150 | -86% | 350 | 9100 | 0 |  | 0 | 0 | 9100 | 1638 | 10738 | -65962 |  | B
7.2.4 | 7CX 2.5 mm2 | MTR | 26 | 2000 | 52000 | 9360 | 61360 | 130 | 3380 | -1870 | -93.5% | 130 | 3380 | 0 |  | 0 | 0 | 3380 | 608.4 | 3988.4 | -57371.6 |  | B
7.2.5 | 10 CX 2.5 mm2 | MTR | 26 | 2500 | 65000 | 11700 | 76700 | 2400 | 62400 | -100 | -4% | 2400 | 62400 | 0 |  | 0 | 0 | 62400 | 11232 | 73632 | -3068 |  | B
7.2.6 | 12 CX 2.5 mm2 | MTR | 26 | 1500 | 39000 | 7020 | 46020 | 700 | 18200 | -800 | -53.33% | 700 | 18200 | 0 |  | 0 | 0 | 18200 | 3276 | 21476 | -24544 |  | B
7.2.7 | 16 CX 2.5 mm2 | MTR | 26 | 1500 | 39000 | 7020 | 46020 | 600 | 15600 | -900 | -60% | 600 | 15600 | 0 |  | 0 | 0 | 15600 | 2808 | 18408 | -27612 |  | B
7.2.8 | 19 CX 2.5 mm2 | MTR | 26 | 1500 | 39000 | 7020 | 46020 | 500 | 13000 | -1000 | -66.67% | 500 | 13000 | 0 |  | 0 | 0 | 13000 | 2340 | 15340 | -30680 |  | B
7.2.9 | 4 CX 4 mm2 | MTR | 26 | 500 | 13000 | 2340 | 15340 | 0 | 0 | -500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -15340 |  | B
7.2.10 | 7 CX 4 mm2 | MTR | 26 | 250 | 6500 | 1170 | 7670 | 0 | 0 | -250 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -7670 |  | B
7.2.11 | 12 CX 4 mm2 | MTR | 26 | 250 | 6500 | 1170 | 7670 | 0 | 0 | -250 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -7670 |  | B
8 | Switch yard lighting: Design, engineering, procurement of labour, material including all associated works for construction of switch yard lightings as per technical specification and approved drawings. The Light fixture shall be of reputed make (Philips/CGL/Bajaj) and fixtures shall be LED type and proper cabling from the lighting outdoor distribution boards to the junction boxes and from junction boxes to the fixtures. The lighting fixtures are to be installed on the switch yard structures. The quantity of such fixtures are to be designed and to be ascertained. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
8.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES ERECTION OF FIXTURES AND LAMPS(LED type) | SET | 387 | 15 | 5805 | 1044.9 | 6849.9 | 15 | 5805 | 0 | 0% | 15 | 5805 | 0 |  | 0 | 0 | 5805 | 1044.9 | 6849.9 | 0 |  | A
8.2 | STREET LIGHTING, IT INCLUDES ERECTION OF GI TUBULAR POLE WITH LED LIGHTING FIXTURES WITH LAMPS.TO BE ERECTED IN & AROUND THE CONTROL ROOM BUILDING, A PORTION OF THE SWITCH YARD ALONG THE ROADS (APPROACH INSIDE YARD), COLONY QUARTERS AND OTHER ROADS. | SET | 1546 | 5 | 7730 | 1391.4 | 9121.4 | 5 | 7730 | 0 | 0% | 5 | 7730 | 0 |  | 0 | 0 | 7730 | 1391.4 | 9121.4 | 0 |  | A
9 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-INST TO BIDDER BEFORE DESIGN-SL NO 16-ANNEXURE - I) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
9.1 | FOAM TYPE-9 LTRS | NOS | 193 | 2 | 386 | 69.48 | 455.48 | 2 | 386 | 0 | 0% | 2 | 386 | 0 |  | 0 | 0 | 386 | 69.48 | 455.48 | 0 |  | A
9.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 966 | 2 | 1932 | 347.76 | 2279.76 | 2 | 1932 | 0 | 0% | 2 | 1932 | 0 |  | 0 | 0 | 1932 | 347.76 | 2279.76 | 0 |  | A
9.3 | DRY POWDER TYPE - 5 KGS | NOS | 644 | 2 | 1288 | 231.84 | 1519.84 | 2 | 1288 | 0 | 0% | 2 | 1288 | 0 |  | 0 | 0 | 1288 | 231.84 | 1519.84 | 0 |  | A
9.4 | CO2 - 4.5 KGS | NOS | 644 | 4 | 2576 | 463.68 | 3039.68 | 4 | 2576 | 0 | 0% | 4 | 2576 | 0 |  | 0 | 0 | 2576 | 463.68 | 3039.68 | 0 |  | A
9.5 | CO2 - 9 KGS | NOS | 644 | 4 | 2576 | 463.68 | 3039.68 | 4 | 2576 | 0 | 0% | 4 | 2576 | 0 |  | 0 | 0 | 2576 | 463.68 | 3039.68 | 0 |  | A
9.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 1546 | 2 | 3092 | 556.56 | 3648.56 | 2 | 3092 | 0 | 0% | 2 | 3092 | 0 |  | 0 | 0 | 3092 | 556.56 | 3648.56 | 0 |  | A
9.7 | 9 litre water type | Nos. | 1289 | 2 | 2578 | 464.04 | 3042.04 | 2 | 2578 | 0 | 0% | 2 | 2578 | 0 |  | 0 | 0 | 2578 | 464.04 | 3042.04 | 0 |  | A
9.8 | 50 Litres Mechanical Foam type | Nos. | 1933 | 2 | 3866 | 695.88 | 4561.88 | 2 | 3866 | 0 | 0% | 2 | 3866 | 0 |  | 0 | 0 | 3866 | 695.88 | 4561.88 | 0 |  | A
9.9 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 387 | 2 | 774 | 139.32 | 913.32 | 2 | 774 | 0 | 0% | 2 | 774 | 0 |  | 0 | 0 | 774 | 139.32 | 913.32 | 0 |  | A
10 | 220 KV SIDE AUTOMATION , PROTECTION & OTHER PANELS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
| SUBSTATION AUTOMATION SYSTEM: Supply of the following 220 kV level consisting of Panels, Bay control Units, DP Relays, Numerical O/C & E/F Relays, DC Supervision relays, Trip Circuit Supervision, Trip Relay ,Test Block, Differential and REF, Overfluxing, High impednce REF, Numerical O/C & E/F relay,Transformer trouble relay etc. Station level consisting of Industrial Computer with accessories, PC with accessories, laser printer, UPS, GPS System & Numerical bay control unit etc. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.1 | Sub-Station Automation (in PRP as per the indicative drg ) system (for 02 nos. 220 KV side line feeder bays ),other accessories ( Relays,auxiliary system, Ethernet Switches ,FO Patch cords, LIU,Multimode glass fibre Doublle jacket armoured optical cables, Red boxes etc . (i) Line Interface Unit(LIU) - as per requirement (for 220KV side),(ii)Managed Ethernet switch IEC 61850-3, IEEE1588v2 as per requirement,(iii) Multimode glass fibre optical cord Double Jacketted armoured, rodent sillient of required length,(iv) HDPE pipes for laying of FO cable of required length in all respect to integrate with the existing SAS system. | LS | 15464 | 1 | 15464 | 2783.52 | 18247.52 | 1 | 15464 | 0 | 0% | 1 | 15464 | 0 |  | 0 | 0 | 15464 | 2783.52 | 18247.52 | 0 |  | A
10.2 | 220 KV SIDE PROTECTION & OTHER PANELS for SAS and Bus Bar protn. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.2.1 | BCU based FEEDER PROTECTION RELAY PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Numerical Bay control unit (BCU) (48DI, 32DO, IEC 61850 protocol with PRP ) for substation automation system. | Nos. | 9665 | 2 | 19330 | 3479.4 | 22809.4 | 2 | 19330 | 0 | 0% | 2 | 19330 | 0 |  | 0 | 0 | 19330 | 3479.4 | 22809.4 | 0 |  | A
10.2.2 | Bus Bar Protection system in all respect to integrate with the existing system for above two nos 220 KV Line Feeders (including supply of relays,auxiliary relays,switches,FO cables,Managed Switches etc). | Nos. | 5799 | 2 | 11598 | 2087.64 | 13685.64 | 2 | 11598 | 0 | 0% | 2 | 11598 | 0 |  | 0 | 0 | 11598 | 2087.64 | 13685.64 | 0 |  | A
11 | Yard AC Kiosk for 220 KV Switchyards :5000 mm (L)x4000mm (W)x 3300mm (H) with Air Conditioning as per the Specification; | Nos. | 193299 | 1 | 193299 | 34793.82 | 228092.82 | 1 | 193299 | 0 | 0% | 1 | 193299 | 0 |  | 0 | 0 | 193299 | 34793.82 | 228092.82 | 0 |  | A
12 | COLOUR CODING, BAY MARKING Etc:Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. MS sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | SET | 5799 | 1 | 5799 | 1043.82 | 6842.82 | 1 | 5799 | 0 | 0% | 1 | 5799 | 0 |  | 0 | 0 | 5799 | 1043.82 | 6842.82 | 0 |  | A
13 | BEST QUALITY & APPROVED MAKE RUBBER MAT TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC. | NOS | 5799 | 4 | 23196 | 4175.28 | 27371.28 | 4 | 23196 | 0 | 0% | 4 | 23196 | 0 |  | 0 | 0 | 23196 | 4175.28 | 27371.28 | 0 |  | A
14 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
14.1 | Erection of 24 fibre(DWSM) optic approach cable along with hardware | KM | 32216 | 1 | 32216 | 5798.88 | 38014.88 | 1 | 32216 | 0 | 0% | 1 | 32216 | 0 |  | 0 | 0 | 32216 | 5798.88 | 38014.88 | 0 |  | A
14.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 10954 | 2 | 21908 | 3943.44 | 25851.44 | 2 | 21908 | 0 | 0% | 2 | 21908 | 0 |  | 0 | 0 | 21908 | 3943.44 | 25851.44 | 0 |  | A
14.3 | Installation & commissioning of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 10954 | 1 | 10954 | 1971.72 | 12925.72 | 1 | 10954 | 0 | 0% | 1 | 10954 | 0 |  | 0 | 0 | 10954 | 1971.72 | 12925.72 | 0 |  | A
PART-A | ERECTION COMPONENT OF THE WORKS CONTRACT FOR 220 KV Bay Extn-PRATAPSASAN |  |  |  | 2955640.74 | 532015.3332 | 3487656.0732 |  | 2746001.0065 |  | 0% |  | 2617496.5065 |  |  |  | 43120.75 | 2660617.2565 | 478911.1062 | 3139528.3627 | -348127.7105

## E_220kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
ERECTION - 220kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment |  | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA | Deviation quantity |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower without stubs and cleats including different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping legs & bracing members. All Erection should confirm to the Technical Specification laid there in the Tender Specification and designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec. |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1.1 | TOWER SUPER STRUCTURES |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.1 | OA TYPE (SUSPENSION) TOWERS (NOMINAL UNIT WEIGHT 4.242 MT) | Nos |  | 146 | 0 | 0 | 0 | 142 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.2 | +3 EXTENSION (NOMINAL UNIT WEIGHT 0.725MT) | Nos |  | 30 | 0 | 0 | 0 | 26 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.3 | +6 EXTENSION (NOMINAL UNIT WEIGHT 1.448 MT) | Nos |  | 2 | 0 | 0 | 0 | 11 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4 | OB TYPE (30 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 6.343 MT) | Nos |  | 50 | 0 | 0 | 0 | 48 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.5 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.242 MT) | Nos |  | 4 | 0 | 0 | 0 | 13 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.5.1 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.597 MT) | Nos | [5 empty] | 5 | 0 | [13 empty] | A
1.1.6 | OC TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 9.01MT) | Nos |  | 24 | 0 | 0 | 0 | 32 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.7 | +3 EXTENSION (NOMINAL UNIT WEIGHT 1.474MT) | Nos |  | 2 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.8 | +6 EXTENSION (NOMINAL UNIT WEIGHT 2.597 MT) | Nos |  | 5 | 0 | 0 | 0 | 10 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.9 | UR TYPE (60 deg ANGLE ) TOWERS (NOMINAL UNIT WEIGHT 12.474 MT) | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.10 | UR+6 EXTENSION (NOMINAL UNIT WEIGHT 4.148 MT) | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.11 | WEIGHT OF THE STRUCTURES | MT | 9364.5 | 1231.51 | 11532475.395 | 2075845.5711 | 13608320.9661 | 1874.7726 | 17556307.8254 | 643.2626 | 52.23% | 1539.3875 | 14415594.2438 | 335.3851 | 5744.84 | 5744.84 | 1926733.623 | 16342327.8667 | 2941619.016 | 19283946.8827 | 5675625.9166 | As per the approved structure drawing & route alignment | B
1.2 | Weight of different type G.I Nuts and Bolts | MT | 9364.5 | 61.58 | 576665.91 | 103799.8638 | 680465.7738 | 83.7266 | 784058.1203 | 22.1466 | 35.96% | 76.975 | 720832.3875 | 6.7516 | 5744.84 | 5744.84 | 38787.0915 | 759619.479 | 136731.5062 | 896350.9853 | 215885.2115 | As per approved structure drawing | B
1.3 | Fixing of of Templates & setting of stubs |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.1 | OA Type | Nos |  | 146 | 0 | 0 | 0 | 142 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.2 | OB Type | Nos |  | 50 | 0 | 0 | 0 | 48 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.3 | OC Type | Nos |  | 24 | 0 | 0 | 0 | 32 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.4 | UR Type | Nos |  | 2 | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.5 | Weight of Templates, Stubs & Clear, Foundation Nut and Bolts | MT | 11146 | 230.01 | 2563691.46 | 461464.4628 | 3025155.9228 | 391.4914 | 4363563.4565 | 161.4814 | 70.21% | 287.5125 | 3204614.325 | 103.9789 | 4961.45 | 4961.45 | 515886.2523 | 3720500.5773 | 669690.1039 | 4390190.6812 | 1365034.7584 | As per the approved structure drawing & route alignment | B
2 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | EARTHING DEVICE | Nos. | 3138 | 298 | 935124 | 168322.32 | 1103446.32 | 237 | 743706 | -61 | -20.47% | 237 | 743706 | 0 |  | 0 | 0 | 743706 | 133867.08 | 877573.08 | -225873.24 |  | B
2.2 | DANGER BOARD | Nos. | 252 | 222 | 55944 | 10069.92 | 66013.92 | 231 | 58212 | 9 | 4.054% | 231 | 58212 | 0 |  | 0 | 0 | 58212 | 10478.16 | 68690.16 | 2676.24 |  | B
2.3 | NUMBER PLATE | Nos. | 252 | 222 | 55944 | 10069.92 | 66013.92 | 231 | 58212 | 9 | 4.054% | 231 | 58212 | 0 |  | 0 | 0 | 58212 | 10478.16 | 68690.16 | 2676.24 |  | B
2.4 | PHASE PLATE | Nos. | 252 | 1332 | 335664 | 60419.52 | 396083.52 | 1384 | 348768 | 52 | 3.904% | 1384 | 348768 | 0 |  | 0 | 0 | 348768 | 62778.24 | 411546.24 | 15462.72 |  | B
2.5 | BIRD GUARD | Nos. | 502 | 876 | 439752 | 79155.36 | 518907.36 | 890 | 446780 | 14 | 1.598% | 890 | 446780 | 0 |  | 0 | 0 | 446780 | 80420.4 | 527200.4 | 8293.04 |  | B
2.6 | ANTICLIMBING DEVICE | Nos. | 3766 | 222 | 836052 | 150489.36 | 986541.36 | 231 | 869946 | 9 | 4.054% | 231 | 869946 | 0 |  | 0 | 0 | 869946 | 156590.28 | 1026536.28 | 39994.92 |  | B
2.7 | CIRCUIT PLATE | Nos. | 252 | 444 | 111888 | 20139.84 | 132027.84 | 461 | 116172 | 17 | 3.829% | 461 | 116172 | 0 |  | 0 | 0 | 116172 | 20910.96 | 137082.96 | 5055.12 |  | B
3 | Hoisting and fixing of insulators with required accessories, Hardwares etc., paying out of conductor ,jointing, stringing, sagging & Jumpering etc. of power conductor in the proposed lines and without earth wire with all required accessories including scaffolding for 33 KV,11 KV, LT , P&T lines, roads and using own required T&P and compression jointing machines etc. with 1.5% provision for Sag & Wastage and as per the direction of Engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | DOUBLE CIRCUIT(ACSR ZEBRA, SIX POWER CONDCTOR ) | RKM | 180751.2 | 61.19 | 11060165.928 | 1990829.867 | 13050995.795 | 61.556 | 11126320.8672 | 0.366 | 0.5981% | 61.556 | 11126320.8672 | 0 |  | 0 | 0 | 11126320.8672 | 2002737.7561 | 13129058.6233 | 78062.8283 |  | B
3.2 | Additional charges for stringing in river crossing towers | RKM | 251044 | 1.674 | 420247.656 | 75644.5781 | 495892.2341 | 1.74 | 436816.56 | 0.066 | 3.943% | 1.74 | 436816.56 | 0 |  | 0 | 0 | 436816.56 | 78626.9808 | 515443.5408 | 19551.3067 |  | B
3.3 | Additional charges for stringing above EHT lines/Railway/NH Crossings | RKM | 251044 | 0.204 | 51212.976 | 9218.3357 | 60431.3117 | 0.245 | 61505.78 | 0.041 | 20.1% | 0.245 | 61505.78 | 0 |  | 0 | 0 | 61505.78 | 11071.0404 | 72576.8204 | 12145.5087 |  | B
4 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | Erection of 24Fibre(DWSM) OPGW fibre Optic cable along with hardware | KM | 40167 | 62 | 2490354 | 448263.72 | 2938617.72 | 62 | 2490354 | 0 | 0% | 62 | 2490354 | 0 |  | 0 | 0 | 2490354 | 448263.72 | 2938617.72 | 0 |  | A
B | ERECTION COMPONENT OF THE WORKS CONTRACT FOR 220 KV TRANSMISSION LINE-PRATAPSASAN-ERSAMA |  |  |  | 31465181.325 | 5663732.6385 | 37128913.9635 |  | 39460722.6094 |  | 0% |  | 35097834.1635 |  |  |  | 2481406.9669 | 37579241.1303 | 6764263.4035 | 44343504.5338 | 7214590.5703

## E_400kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
ERECTION - 400kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
A | ELECTRICAL WORKS |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1 | ERECTION,TESTING & COMMISSIONING of Following tested Lattice type Galvanized steel tangent / Angle tower with stubs and cleats , different type of G.I HT Nuts & Bolts, washer, spring washer for the above type towers ,hanger and all accessories, tower super structure complete with tightening, punching of bolts including step bolts. All other left out portion of the bolts above bottom cross arm shall be riveted by using suitable hammer. Painting of black bituminous paints three coats shall be provided up to a height of 500mm above the cooping(legs & bracing members. All Erection should confirm to the Technical Specification laid there in the Tender Specification and designed for Wind Zone-6 i.e. Wind Speed of 55 Mtr/Sec. |  |  |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1.1 | TOWER STRUCTURES |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.1 | DA TYPE (SUSPENSION ) TOWERS (Nominal unit weight 11.884 MT) | Nos. |  | 100 | 0 | 0 | 0 | 97 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.2 | +3 EXTENSION (Nominal unit weight 2.085 MT) | Nos. |  | 31 | 0 | 0 | 0 | 46 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.3 | +6 EXTENSION (Nominal unit weight 2.958MT) | Nos. |  | 6 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4 | +9 EXTENSION (Nominal unit weight 3.988MT) | Nos. |  | 4 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.4.1 | +15 EXTENSION (Nominal unit weight 3.988MT) | Nos. | [5 empty] | 3 | [14 empty] | A
1.1.5 | DB TYPE (15 deg ANGLE ) TOWERS (Nominal unit weight 19.337MT) | Nos. |  | 20 | 0 | 0 | 0 | 20 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.6 | +3 EXTENSION (Nominal unit weight 3.04 MT) | Nos. |  | 4 | 0 | 0 | 0 | 6 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.7 | +6 EXTENSION (Nominal unit weight 4.791 MT) | Nos. |  | 3 | 0 | 0 | 0 |  | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.8 | +9 EXTENSION (Nominal unit weight 6.295 MT) | Nos. |  | 3 | 0 | 0 | 0 | 1 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.9 | DC TYPE (30 deg ANGLE ) TOWERS (Nominal unit weight 22.895 MT) | Nos. |  | 14 | 0 | 0 | 0 | 14 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.10 | +3 EXTENSION (Nominal unit weight 3.531 MT) | Nos. |  | 2 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.11 | +6 EXTENSION (Nominal unit weight 5.432 MT) | Nos. |  | 1 | 0 | 0 | 0 | 2 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.12 | DD TYPE (60 deg angle)TOWER (Nominal unit weight 33.658 MT) | Nos. |  | 48 | 0 | 0 | 0 | 51 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.13 | +3 EXTENSION (Nominal unit weight 5.437 MT) | Nos. |  | 8 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.14 | +6 EXTENSION (Nominal unit weight 8.084 MT) | Nos. |  | 5 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.15 | +9 EXTENSION (Nominal unit weight 10.844 MT) | Nos. |  | 7 | 0 | 0 | 0 | 5 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.15.1 | +12 EXTENSION (Nominal unit weight 10.844 MT) | Nos. | [5 empty] | 2 | [14 empty] | A
1.1.16 | +18 TO DD TYPE TOWER (Nominal unit weight 22.857 MT) | Nos. |  | 10 | 0 | 0 | 0 | 16 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.17 | +25 TO DD TYPE TOWER (Nominal unit weight 33.042 MT) | Nos. |  | 7 | 0 | 0 | 0 | 8 | 0 |  | 0% |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.18 | DD(DEAD END) AT NEW DUBURI END (Nominal unit weight 33.658MT) | Nos. |  | 4 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.19 | WEIGHT OF THE STRUCTURES | MT | 9365 | 4226.429 | 39580507.585 | 7124491.3653 | 46704998.9503 | 4400 | 41206000 | 173.571 | 4.107% | 4400 | 41206000 | 0 |  | 0 | 0 | 41206000 | 7417080 | 48623080 | 1918081.0497 | As per the approved structure drawing & route alignment | B
1.2 | Weight of different type G.I Nuts and Bolts | MT | 9365 | 178 | 1666970 | 300054.6 | 1967024.6 | 183.59 | 1719320.35 | 5.59 | 3.14% | 183.59 | 1719320.35 | 0 |  | 0 | 0 | 1719320.35 | 309477.663 | 2028798.013 | 61773.413 | As per approved structure drawing | B
1.3 | Fixing of templates and setting of stubs |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.1 | DA TYPE (SUSPENSION ) TOWERS | Nos. |  | 100 | 0 | 0 | 0 | 97 | 0 |  | 0% | 97 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.2 | DB TYPE (15 deg ANGLE ) TOWERS | Nos. |  | 20 | 0 | 0 | 0 | 20 | 0 |  | 0% | 20 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.3 | DC TYPE (30 deg ANGLE ) TOWERS | Nos. |  | 14 | 0 | 0 | 0 | 14 | 0 |  | 0% | 14 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.4 | DD TYPE (60 deg angle)TOWER | Nos. |  | 48 | 0 | 0 | 0 | 51 | 0 |  | 0% | 51 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.5 | DD(DEAD END) AT NEW DUBURI END | Nos. |  | 4 | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.3.6 | Weight of Templates, Stub & Cleat & Foundation Nut and Bolts | MT | 11146 | 594 | 6620724 | 1191730.32 | 7812454.32 | 625.0152 | 6966419.1963 | 31.0152 | 5.221% | 625.0152 | 6966419.1963 | 0 |  | 0 | 0 | 6966419.1963 | 1253955.4553 | 8220374.6516 | 407920.3316 | As per the approved structure drawing & route alignment | B
2 | Erection of the following tower accessories as per technical specification and as directed by the engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | EARTHING DEVICE | Nos. | 3138 | 272 | 853536 | 153636.48 | 1007172.48 | 196 | 615048 | -76 | -27.94% | 196 | 615048 | 0 |  | 0 | 0 | 615048 | 110708.64 | 725756.64 | -281415.84 |  | B
2.2 | DANGER BOARD | Nos. | 252 | 186 | 46872 | 8436.96 | 55308.96 | 182 | 45864 | -4 | -2.151% | 182 | 45864 | 0 |  | 0 | 0 | 45864 | 8255.52 | 54119.52 | -1189.44 |  | B
2.3 | NUMBER PLATE | Nos. | 252 | 186 | 46872 | 8436.96 | 55308.96 | 182 | 45864 | -4 | -2.151% | 182 | 45864 | 0 |  | 0 | 0 | 45864 | 8255.52 | 54119.52 | -1189.44 |  | B
2.4 | PHASE PLATE | Nos. | 252 | 1116 | 281232 | 50621.76 | 331853.76 | 1092 | 275184 | -24 | -2.151% | 1092 | 275184 | 0 |  | 0 | 0 | 275184 | 49533.12 | 324717.12 | -7136.64 |  | B
2.5 | BIRD GUARD | Nos. | 502 | 600 | 301200 | 54216 | 355416 | 594 | 298188 | -6 | -1% | 594 | 298188 | 0 |  | 0 | 0 | 298188 | 53673.84 | 351861.84 | -3554.16 |  | B
2.6 | ANTICLIMBING DEVICE | Nos. | 3766 | 186 | 700476 | 126085.68 | 826561.68 | 182 | 685412 | -4 | -2.151% | 182 | 685412 | 0 |  | 0 | 0 | 685412 | 123374.16 | 808786.16 | -17775.52 |  | B
2.7 | Circuit plate | Nos. | 252 | 372 | 93744 | 16873.92 | 110617.92 | 364 | 91728 | -8 | -2.151% | 364 | 91728 | 0 |  | 0 | 0 | 91728 | 16511.04 | 108239.04 | -2378.88 |  | B
2.8 | Counterpoise earthing including all materials | Mtrs | 126 | 1200 | 151200 | 27216 | 178416 | 1200 | 151200 | 0 | 0% | 1200 | 151200 | 0 |  | 0 | 0 | 151200 | 27216 | 178416 | 0 |  | A
3 | Hoisting and fixing of insulators with required accessories, Hardwares etc., paying out of conductor,GI Earth wire & its hardware ,jointing, stringing, sagging & Jumpering etc. of power conductor in the proposed lines and without earth wire with all required accessories including scaffolding for 33 KV,11 KV, LT , P&T lines, roads and using own required T&P and compression jointing machines etc. with 1.5% provision for Sag & Wastage and as per the direction of Engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 |  | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | ACSR Moose(54/7/3.53 mm) for 400kv lines | Route Kms. | 405184.8 | 67.82 | 27479633.136 | 4946333.9645 | 32425967.1005 | 68.001 | 27552971.5848 | 0.181 | 0.2669% | 68.001 | 27552971.5848 | 0 |  | 0 | 0 | 27552971.5848 | 4959534.8853 | 32512506.4701 | 86539.3696 |  | B
3.2 | Additional Charges for stringing in EHV LINE crossing/Railway/National Highway crossing. | Route Kms. | 251044 | 2 | 502088 | 90375.84 | 592463.84 | 2.756 | 691877.264 | 0.756 | 37.8% | 2.5 | 627610 | 0.256 | 77228.88 | 77228.88 | 19770.5933 | 647380.5933 | 116528.5068 | 763909.1001 | 171445.2601 | As per approved route alignment | B
3.3 | Additional Charges for stringing in river crossing tower | Route Kms. | 251044 | 2.5 | 627610 | 112969.8 | 740579.8 | 2.786 | 699408.584 | 0.286 | 11.44% | 2.786 | 699408.584 | 0 |  | 0 | 0 | 699408.584 | 125893.5451 | 825302.1291 | 84722.3291 | As per approved route alignment | B
3.4 | Additional Charges for stringing in tower placed in Hilly terrain | Route Kms. | 251044 | 1.5 | 376566 | 67781.88 | 444347.88 | 0 | 0 | -1.5 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -444347.88 |  | B
4 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine optd.), application of required zinc rich paints around the welding portion (two coats),fuel,lubricants,T&P and labours. | Nos. | 5 | 530100 | 2650500 | 477090 | 3127590 | 1083774 | 5418870 | 553674 | 104.4% | 662625 | 3313125 | 421149 | 8.57 | 5 | 2105745 | 5418870 | 975396.6 | 6394266.6 | 3266676.6 | As per the approved structure drawing | B
5 | Dismantling of existing 400KV D/C Line to M/s TATA (between loc. Loc. 02 & Loc. 04) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | Dismantling of tower super structure, delivery with stacking at nearest OPTCL store as per Instruction of Engineer in charge. | MT | 7498 | 34 | 254932 | 45887.76 | 300819.76 | 34 | 254932 | 0 | 0% | 34 | 254932 | 0 |  | 0 | 0 | 254932 | 45887.76 | 300819.76 | 0 |  | A
5.2 | Dismantling , delivery and stacking of strung conductor (Double Circuit AAAC/ACSR Double Moose with two earth wire/OPGW) at nearest OPTCL store as per the instruction of Engineer In charge. | Route Kms. | 356482 | 0.4 | 142592.8 | 25666.704 | 168259.504 | 0.4 | 142592.8 | 0 | 0% | 0.4 | 142592.8 | 0 |  | 0 | 0 | 142592.8 | 25666.704 | 168259.504 | 0 |  | A
6 | ERECTION OF ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1 | 24Fibre(DWSM) OPGW fibre Optic cable and OPGW hardwarw set like suspension assembly, Tension assembly(Dead end assembly, Pass through assembly), Vibration damper, Down Lead clamp Assemblies for 24F, 48 fibre(DWSM) OPGW, Joint box | KM | 40167 | 68 | 2731356 | 491644.08 | 3223000.08 | 68.001 | 2731396.167 | 0.001 | 0.001471% | 68.001 | 2731396.167 | 0 |  | 0 | 0 | 2731396.167 | 491651.3101 | 3223047.4771 | 47.3971 |  | B
C | TOTAL OF ERECTION COMPONENT OF THE WORKS CONTRACT FOR 400 KV TRANSMISSION LINE-DUBURI-LOC-001 to LOC-182 |  |  |  | 85108611.521 | 15319550.0738 | 100428161.5948 |  | 89592275.9461 |  | 0% |  | 87422263.6821 |  |  |  | 2125515.5933 | 89547779.2754 | 16118600.2696 | 105666379.5449 | 5238217.9501

## C_Bay
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
CIVIL - 220kV BAY
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
PART B | CIVIL WORKS |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1 | CONTOUR SURVEY,AND LEVELING, BACK FILLING |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1.1 | Contour survey and furnishing contour map including supply of all materials, Labour and T&P | SQ.MTRS. | 13 | 5000 | 65000 | 11700 | 76700 | 6000 | 78000 | 1000 | 20% | 6000 | 78000 | 0 |  | 0 | 0 | 78000 | 14040 | 92040 | 15340 | As per the site requirement | B
1.2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. | PER POINT | 27616 | 2 | 55232 | 9941.76 | 65173.76 | 0 | 0 | -2 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -65173.76 |  | B
2 | Excavation for OPEN CAST and PILE foundation and back filling of columns,Equipments foundations,including supply of all labours,T&P,and materials and as per the direction of the Engineer-in-Charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | Soft Soil/Loose Soil. | CUM | 229 | 450 | 103050 | 18549 | 121599 | 350 | 80150 | -100 | -22.22% | 350 | 80150 | 0 |  | 0 | 0 | 80150 | 14427 | 94577 | -27022 |  | B
2.2 | Hard/Dense Soil. | CUM | 310 | 150 | 46500 | 8370 | 54870 | 100 | 31000 | -50 | -33.33% | 100 | 31000 | 0 |  | 0 | 0 | 31000 | 5580 | 36580 | -18290 |  | B
2.3 | Muddy Soil. | CUM | 269 | 500 | 134500 | 24210 | 158710 | 100 | 26900 | -400 | -80% | 100 | 26900 | 0 |  | 0 | 0 | 26900 | 4842 | 31742 | -126968 |  | B
2.4 | Soft/Disintegrated Rock (not requiring blasting) | CUM | 727 | 50 | 36350 | 6543 | 42893 |  | 0 | -50 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -42893 |  | B
2.5 | Hard rock (requiring blasting/using breaker machinery) | CUM | 1401 | 50 | 70050 | 12609 | 82659 |  | 0 | -50 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -82659 |  | B
3 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | LEVELLING OF S/S AREA:Providing, neatly dressing up and levelling of substation area including switchyard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1.1 | CUTTING of substation area |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1.1.1 | [i]Soft/loose soil | CUM | 202 | 40 | 8080 | 1454.4 | 9534.4 | 40 | 8080 | 0 | 0% | 40 | 8080 | 0 |  | 0 | 0 | 8080 | 1454.4 | 9534.4 | 0 |  | A
3.2.1 | FILLING of substation area with borrowed earth with supply of all labour,T & P. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.2.1.1 | Beyond 100mtr lead | CUM | 400 | 10000 | 4000000 | 720000 | 4720000 | 12000 | 4800000 | 2000 | 20% | 12000 | 4800000 | 0 |  | 0 | 0 | 4800000 | 864000 | 5664000 | 944000 | As per the site requirement | B
4 | Anti-Weed Treatment |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treatment of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge. | Sq.Mtrs | 47 | 3200 | 150400 | 27072 | 177472 | 3200 | 150400 | 0 | 0% | 3200 | 150400 | 0 |  | 0 | 0 | 150400 | 27072 | 177472 | 0 |  | A
5 | PILE FOUNDATION (UNDER-REAM PILE) BORING &CONCRETE WORKS AND PILE RISER,CAPPING,PEDESTAL & TIE-BEAM CONCRETE WORKS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | Boring for under ream cast-in-Situ piling, with Manual Auger method or by using Motor driven Machinery,including supply of Bentonite required for stabilization bore of required diameter bore holes & approximate length of the bore is 10 Mtrs. with under reemed piles. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1.1 | 250MM DIA | Mtrs. | 674 | 50 | 33700 | 6066 | 39766 |  | 0 | -50 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -39766 |  | B
5.1.2 | 300MM DIA | Mtrs. | 943 | 70 | 66010 | 11881.8 | 77891.8 |  | 0 | -70 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -77891.8 |  | B
5.1.3 | 375MM DIA | Mtrs. | 977 | 1150 | 1123550 | 202239 | 1325789 | 670 | 654590 | -480 | -41.74% | 670 | 654590 | 0 |  | 0 | 0 | 654590 | 117826.2 | 772416.2 | -553372.8 |  | B
5.1.4 | 400MM DIA | Mtrs. | 1010 | 60 | 60600 | 10908 | 71508 |  | 0 | -60 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -71508 |  | B
5.1.5 | 450MM DIA | Mtrs. | 1078 | 100 | 107800 | 19404 | 127204 |  | 0 | -100 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -127204 |  | B
5.1.6 | 500MM DIA | Mtrs. | 1145 | 100 | 114500 | 20610 | 135110 |  | 0 | -100 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -135110 |  | B
5.2 | Supply of all materials like cement, all coarse aggregates, fine aggregates and making Under-reamed pile foundations (after pile boring as per required depth, basing on design), Pile riser (if required),capping, tie beams etc, required for foundation of columns, equipment etc. as per requirement including supply of all equipment with labours, proper curing of the foundations and T&P as per specification in the concrete ratio 1:1.5:3 (Grade M-20) in all type of soil & back filling and disposal of excess earth as per the direction of Engineer In Charge. | CUM | 8543 | 460 | 3929780 | 707360.4 | 4637140.4 | 350 | 2990050 | -110 | -23.91% | 350 | 2990050 | 0 |  | 0 | 0 | 2990050 | 538209 | 3528259 | -1108881.4 |  | B
5.3 | Supply of Steel of different size (as per design) with cutting, bending, binding in position of M.S.Rod for reinfocement of foundation concrete of Piles(Under reem Pile), Capping, Pile Risers and Tie Beams etc. including supply of binding wire (With supply of MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 ). | MT. | 78469 | 33 | 2589477 | 466105.86 | 3055582.86 | 15 | 1177035 | -18 | -54.55% | 15 | 1177035 | 0 |  | 0 | 0 | 1177035 | 211866.3 | 1388901.3 | -1666681.56 |  | B
6 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge including supply of all labour, T&P, materials. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 ),Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Fly ash brickwork with Fly ash brick ,plastering (!:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1 | Cable trench with covers |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
6.1.1 | Section 2- 2 | Mtrs | 22196 | 50 | 1109800 | 199764 | 1309564 |  | 0 | -50 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -1309564 |  | B
6.1.2 | Section 3-3 | Mtrs | 18497 | 200 | 3699400 | 665892 | 4365292 | 90 | 1664730 | -110 | -55% | 90 | 1664730 | 0 |  | 0 | 0 | 1664730 | 299651.4 | 1964381.4 | -2400910.6 |  | B
6.1.3 | Section 4-4 | Mtrs | 12417 | 75 | 931275 | 167629.5 | 1098904.5 | 180 | 2235060 | 105 | 140% | 93.75 | 1164093.75 | 86.25 | 12417 | 12417 | 1070966.25 | 2235060 | 402310.8 | 2637370.8 | 1538466.3 | As per approved layout | B
7 | Cable trench crossing:Design,engineering,construction including supply of labour, materials, cement, reinforcement steel, form box etc,and all associated works for construction of trench crossing as per technical specification and approved drawing. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1 | Road crossing for |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1.1 | Section 2- 2 & Section 3-3 | Nos | 131291 | 2 | 262582 | 47264.76 | 309846.76 | 2 | 262582 | 0 | 0% | 2 | 262582 | 0 |  | 0 | 0 | 262582 | 47264.76 | 309846.76 | 0 |  | A
8 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper levelling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area .After proper levelling of the switch yard area (after anti-weed treatment), spreading of plain cement concert with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area . As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge.This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge and approved drawing. | CUM | 6481 | 200 | 1296200 | 233316 | 1529516 | 200 | 1296200 | 0 | 0% | 200 | 1296200 | 0 |  | 0 | 0 | 1296200 | 233316 | 1529516 | 0 |  | A
9 | METAL SPREADING IN THE SWITCH-YARD |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
9.1 | Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8).The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 1572 | 300 | 471600 | 84888 | 556488 | 300 | 471600 | 0 | 0% | 300 | 471600 | 0 |  | 0 | 0 | 471600 | 84888 | 556488 | 0 |  | A
10 | Roads: Design, construction of roads and walkways/ shoulders within sub-station as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. Provision of drains on both the side of the roads for easy discharge of rain water. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.1 | 3.75 mtrs Concrete road with shoulder at both the side & shall have drain on both side of the road as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | MTRS | 20928 | 50 | 1046400 | 188352 | 1234752 | 50 | 1046400 | 0 | 0% | 50 | 1046400 | 0 |  | 0 | 0 | 1046400 | 188352 | 1234752 | 0 |  | A
10.2 | 7 mtrs wide Concrete roads with shoulder as per specification indicated in the civil section.( for main and approach roads).Shall have drain on both side of the road. | MTRS | 26765 | 50 | 1338250 | 240885 | 1579135 | 50 | 1338250 | 0 | 0% | 50 | 1338250 | 0 |  | 0 | 0 | 1338250 | 240885 | 1579135 | 0 |  | A
11 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. All the switcyard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. RCC type drainage system to be considered. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
11.1 | Storm water drain | MTRS | 9093 | 200 | 1818600 | 327348 | 2145948 | 200 | 1818600 | 0 | 0% | 200 | 1818600 | 0 |  | 0 | 0 | 1818600 | 327348 | 2145948 | 0 |  | A
11.2 | Road-culverts, drain crossings | MTRS | 12124 | 220 | 2667280 | 480110.4 | 3147390.4 | 220 | 2667280 | 0 | 0% | 220 | 2667280 | 0 |  | 0 | 0 | 2667280 | 480110.4 | 3147390.4 | 0 |  | A
11.3 | Cable trench crossing | MTRS | 6062 | 50 | 303100 | 54558 | 357658 | 50 | 303100 | 0 | 0% | 50 | 303100 | 0 |  | 0 | 0 | 303100 | 54558 | 357658 | 0 |  | A
12 | Switchyard fencing: Providing and fixing of G.I chain link(2.5mm dia) fencing( the posts and links shall be of HD Galvanised ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous RR masonary work with ratio 1:5 and cement pointing of the joints, for the fencing upto a height of 350mm from the finished ground level) .This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | MTRS | 7568 | 250 | 1892000 | 340560 | 2232560 | 250 | 1892000 | 0 | 0% | 250 | 1892000 | 0 |  | 0 | 0 | 1892000 | 340560 | 2232560 | 0 |  | A
13 | Retaining Wall of RCC(M20) along the bay corridor for protection from pulling of filled earth on the bay extended area as per approved drawing, and as per instruction of engineer in-charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
13.1 | Excavation in Soft & Loose Soil | Cum | 229 | 500 | 114500 | 20610 | 135110 |  | 0 | -500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -135110 |  | B
13.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 6473 | 50 | 323650 | 58257 | 381907 | 50 | 323650 | 0 | 0% | 50 | 323650 | 0 |  | 0 | 0 | 323650 | 58257 | 381907 | 0 |  | A
13.3 | R.C.C (1:1.5:3): Concrete Grade M-20 without supply of reinforcement | Cum | 5287 | 25 | 132175 | 23791.5 | 155966.5 |  | 0 | -25 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -155966.5 |  | B
13.4 | Supply of MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 ) of different size (as per design ) with cutting, bending, binding in position of M.S.Rod for reinfocement of foundation concret of Pile Risers including supply of binding wire (With supply of steel rod ) | MT. | 7195 | 2.5 | 17987.5 | 3237.75 | 21225.25 |  | 0 | -2.5 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -21225.25 |  | B
PART-A | CIVIL COMPONENT OF THE WORKS CONTRACT FOR 220 KV Bay Extn-PRATAPSASAN |  |  |  | 30119378.5 | 5421488.13 | 35540866.63 |  | 25315657 |  | 0% |  | 24244690.75 |  |  |  | 1070966.25 | 25315657 | 4556818.26 | 29872475.26 | -5668391.37
[11 empty] | 0% | [9 empty] | 0

## C_220kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
CIVIL - 220kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks |  | Open Cast | Pile | Total
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
1 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting | [9 empty] | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1.1 | Preliminary survey, Detail survey and resurvey (required for avoiding ROW problem) including but not limited to taking of levels, profile plotting, tower spotting ,marking of towers locations at site including showing P&T line, power line, Railway line, river crossing, roads and submission of route map and survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. | KM. | 30126 | 61.2 | 1843711.2 | 331868.016 | 2175579.216 | 2 | 60252 | -59.2 | -96.73% | 2 | 60252 | 0 |  | 0 | 0 | 60252 | 10845.36 | 71097.36 | -2104481.856 |  | B
1.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | KM. | 17134.65 | 61.2 | 1048640.58 | 188755.3044 | 1237395.8844 | 61.556 | 1054740.5154 | 0.356 | 0.5817% | 61.556 | 1054740.5154 | 0 |  | 0 | 0 | 1054740.5154 | 189853.2928 | 1244593.8082 | 7197.9238 |  | B
1.3 | Preparation of land schedule on revenue (if required) maps indicating alignment therein duly authenticated by Revenue Inspector & Tahasildar, enumeration of trees with the help of Forest officer and other prominent features required for alignment of the proposed 220 KV line. Final route to be plotted on 1:50000 topo sheet for approval. | KM. | 20084 | 61.2 | 1229140.8 | 221245.344 | 1450386.144 | 2 | 40168 | -59.2 | -96.73% | 2 | 40168 | 0 |  | 0 | 0 | 40168 | 7230.24 | 47398.24 | -1402987.904 |  | B
1.4 | Soil Testing in complete shape along with submission of report etc. up to the depth of 15 Mtrs. | Per Loc. | 87866 | 30 | 2635980 | 474476.4 | 3110456.4 | 30 | 2635980 | 0 | 0% | 30 | 2635980 | 0 |  | 0 | 0 | 2635980 | 474476.4 | 3110456.4 | 0 |  | A
1.5 | Soil Testing in complete shape along with submission of report etc. upto the depth of 30 mtrs for River bed pile. | Per Loc. | 200836 | 10 | 2008360 | 361504.8 | 2369864.8 | 4 | 803344 | -6 | -60% | 4 | 803344 | 0 |  | 0 | 0 | 803344 | 144601.92 | 947945.92 | -1421918.88 |  | B
2 | EXCAVATION WORKS FOR FOUNDATIONS: |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | Excavation for following type of soil and rocks and back filling (back filling shall be done in layers of 500mm sprinkling of water and compaction thereafter and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/morrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1.1 | Soft/Loose soil | CUM | 189 | 8075 | 1526175 | 274711.5 | 1800886.5 | 10775.8741 | 2036640.1973 | 2700.8741 | 33.45% | 10093.75 | 1907718.75 | 682.1241 | 195.85 | 189 | 128921.4473 | 2036640.1973 | 366595.2355 | 2403235.4329 | 602348.9329 | As per approved foundation drawing and site requirement | B | 4177.08 | 6085.6572 | 10262.7372
2.1.2 | Dense/Compact soil | CUM | 204 | 3000 | 612000 | 110160 | 722160 | 8645.894 | 1763762.3842 | 5645.894 | 188.2% | 3750 | 765000 | 4895.894 | 306.83 | 204 | 998762.3842 | 1763762.3842 | 317477.2291 | 2081239.6133 | 1359079.6133 | As per approved foundation drawing and site requirement | B | 4177.08 | 4057.1048 | 8234.1848
2.1.3 | Soft/Disintegrated rock(not requiring blasting) | CUM | 628 | 1500 | 942000 | 169560 | 1111560 | 0 | 0 | -1500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -1111560 |  | B | 0 | 0 | 0
2.1.4 | Hard rock (requiring blasting/using breaker machinery) | CUM | 1020 | 1000 | 1020000 | 183600 | 1203600 | 0 | 0 | -1000 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -1203600 |  | B | 0 | 0 | 0
2.1.5 | Fully submerged soil | CUM | 266 | 8000 | 2128000 | 383040 | 2511040 | 4568.6813 | 1215269.2125 | -3431.3187 | -42.89% | 4568.6813 | 1215269.2125 | 0 |  | 0 | 0 | 1215269.2125 | 218748.4583 | 1434017.6708 | -1077022.3292 |  | B | 4351.125 | 0 | 4351.125
2.1.6 | Partial Submerged soil | CUM | 235 | 11000 | 2585000 | 465300 | 3050300 | 4934.1758 | 1159531.3013 | -6065.8242 | -55.14% | 4934.1758 | 1159531.3013 | 0 |  | 0 | 0 | 1159531.3013 | 208715.6342 | 1368246.9355 | -1682053.0645 |  | B | 4699.215 | 0 | 4699.215
3.0 | FOUNDATION MATERIALS: Supply of all materials like cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1 | OPEN CAST AND PILE FOUNDATION .This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.1.1 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in tower foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 6031 | 650 | 3920150 | 705627 | 4625777 | 733.1643 | 4421713.8933 | 83.1643 | 12.79% | 733.1643 | 4421713.8933 | 0 |  | 0 | 0 | 4421713.8933 | 795908.5008 | 5217622.3941 | 591845.3941 | As per approved foundation drawing and site requirement | B | 255.14 | 411.373 | 666.513
3.1.2 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation and pile caping, riser and tie beam for under ream/DMC (500 mm dia) and reverbed pile (1000 mm dia) with supply of approved quality coarse aggregates(Nominal size 12mm to 20mm), fine aggregates, cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 7061 | 7600 | 53663600 | 9659448 | 63323048 | 8054.1934 | 56870659.5974 | 454.1934 | 5.976% | 8054.1934 | 56870659.5974 | 0 |  | 0 | 0 | 56870659.5974 | 10236718.7275 | 67107378.3249 | 3784330.3249 | As per approved foundation drawing and site requirement | B | 1773.8 | 5548.194 | 7321.994
3.1.3 | Design, Engineering and laying of reinforced cement concrete (RCC 1:1::2) of grade M25 for riverbed pile (1000 mm dia) foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The surrounding area shall be clear from materials, Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. | CUM | 10551 | 550 | 5803050 | 1044549 | 6847599 | 550 | 5803050 | 0 | 0% | 550 | 5803050 | 0 |  | 0 | 0 | 5803050 | 1044549 | 6847599 | 0 |  | A |  | 359.398 | 359.398
3.1.4 | Design, Engineering and laying of reinforced cement concrete (RCC 1:1.5:3) of grade M20 for under ream and DMC (500 mm dia) foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The surrounding area shall be clear from materials, Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. | CUM | 9610 | 4650 | 44686500 | 8043570 | 52730070 | 14794.936 | 142179334.96 | 10144.936 | 218.2% | 5812.5 | 55858125 | 8982.436 | 7870.43 | 7870.43 | 70695633.7675 | 126553758.7675 | 22779676.5781 | 149333435.3456 | 96603365.3456 | As per approved foundation drawing and site requirement | B |  | 14794.936 | 14794.936
3.1.5 | Cutting, bending, hooking, fixing and binding in poisition of MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 for rainforcement of foundation concrete of towers including supply of wire for binding (With supply of steel rod FE-500 as per BIS-1786 of different size(as per design). | MT | 67970 | 1010 | 68649700 | 12356946 | 81006646 | 1686.489 | 114630660.7285 | 676.489 | 66.98% | 1262.5 | 85812125 | 423.989 | 68623.36 | 67970 | 28818535.7285 | 114630660.7285 | 20633518.9311 | 135264179.6596 | 54257533.6596 | As per approved foundation drawing | B | 112.2307 | 1574.2584 | 1686.489
3.2 | Pile foundation: Boring for under ream cast in situ piling with bentonite sowing for stabilization of bore. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
3.2.1 | Boring for under reamed cast in situ piling with betonite showing for stabilisation of bore pile diameter (500mm) & approximate length of the bore is 10 Mtrs to 12 Mtrs with under reem in sandy and submerged soil | MTR | 791 | 23000 | 18193000 | 3274740 | 21467740 | 450 | 355950 | -22550 | -98.04% | 450 | 355950 | 0 |  | 0 | 0 | 355950 | 64071 | 420021 | -21047719 |  | B |  | 450 | 450
3.2.2 | Boring by DMC method piling with betonite showing for stabilisation of bore pile diameter (500mm) & approximate length of the bore is 10 Mtrs to 18 Mtrs in sandy and submerged soil | MTR | 1506 | 500 | 753000 | 135540 | 888540 | 0 | 0 | -500 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -888540 |  | B |  |  | 0
3.2.3 | Boring by DMC method piling with betonite showing for stabilisation of bore pile diameter (1000mm) & approximate length of the bore is 25 Mtrs to 30 Mtrs in river bed and river bank. | MTR | 8786 | 700 | 6150200 | 1107036 | 7257236 | 20876 | 183416536 | 20176 | 2882% | 875 | 7687750 | 20001 | 6462.95 | 6462.95 | 129265462.95 | 136953212.95 | 24651578.331 | 161604791.281 | 154347555.281 | As per approved soil investigation and site requirement | B |  | 20876 | 20876
3.2.4 | Supply and putting MS liner of nominal thickness 6/8 mm as per approved T.S and as per instructions of engineer in charge for river bed & river bank pile foundation. | MT | 99162 | 90 | 8924580 | 1606424.4 | 10531004.4 | 90 | 8924580 | 0 | 0% | 90 | 8924580 | 0 |  | 0 | 0 | 8924580 | 1606424.4 | 10531004.4 | 0 |  | A
4 | Supply of borrowed earth/morrum for back filling for foundation/revertment works |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
4.1 | (i) Up to 30 mtr lead | CUM | 1000 | 500 | 500000 | 90000 | 590000 | 500 | 500000 | 0 | 0% | 500 | 500000 | 0 |  | 0 | 0 | 500000 | 90000 | 590000 | 0 |  | A
4.2 | (ii) Beyond 30 mtr lead | CUM | 1000 | 500 | 500000 | 90000 | 590000 | 500 | 500000 | 0 | 0% | 500 | 500000 | 0 |  | 0 | 0 | 500000 | 90000 | 590000 | 0 |  | A
4.3 | (iii) beyond 100 mtr lead | CUM | 1000 | 500 | 500000 | 90000 | 590000 | 500 | 500000 | 0 | 0% | 500 | 500000 | 0 |  | 0 | 0 | 500000 | 90000 | 590000 | 0 |  | A
5 | SHORING & SHUTTERING- Required in wet/submerged or special locations of open cast/shallow type foundations with supply of all materials,T&P and Labour. | SQ.MTR. | 377 | 8000 | 3016000 | 542880 | 3558880 | 10000 | 3770000 | 2000 | 25% | 10000 | 3770000 | 0 |  | 0 | 0 | 3770000 | 678600 | 4448600 | 889720 | As per approved foundation drawing and site requirement | B
6 | Head-Loading of all types of foundation-materials, towers, structures, conductors, Insulators, Hard-wares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of site Engineer-In- Charge and approval of the General Manager of Concerned circle. | MT-Mtr | 3 | 500000 | 1500000 | 270000 | 1770000 | 750000 | 2250000 | 250000 | 50% | 625000 | 1875000 | 125000 | 11.1 | 3 | 375000 | 2250000 | 405000 | 2655000 | 885000 | As per site requirement | B
7 | DE-WATERING ( for water logged and open cast foundations) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1 | With Supply of all T&P, Fuel, Lubricant & electricity on HP Hour basis. | HP Hour | 50 | 15000 | 750000 | 135000 | 885000 | 18750 | 937500 | 3750 | 25% | 18750 | 937500 | 0 |  | 0 | 0 | 937500 | 168750 | 1106250 | 221250 | As per site requirement | B
8 | WELDING OF TOWER MEMBERS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
8.1 | Supply of all materials for continuous welding of bolts & nuts (around the bolts) up to top of tower without cross arm, including welding rods, welding generator machine (diesel engine operator), application of required zinc rich paints around the welding portion after welding (two coats), fuel, lubricants,T&P and labours and other arrangements etc. | Nos. | 5 | 360000 | 1800000 | 324000 | 2124000 | 548286 | 2741430 | 188286 | 52.3% | 450000 | 2250000 | 98286 | 8.57 | 5 | 491430 | 2741430 | 493457.4 | 3234887.4 | 1110887.4 | As per approved structure drawing | B
9 | PAINTING OF TOWER LEGS |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
9.1 | Supply and painting over tower structure by applying one coat of zinc phosphate primer of ASIAN/BERGER make, 2coats of Aluminium paint of ASIAN/BERGER make and applying one coat of black enamel paint over tower legs up to a height of 1mtr. Including cost of material, consumables, T&P and as per instruction of the engineer in charge.(Scrapping and washing of the structures are to be done prior to painting of towers) | SQ.MTR. | 1256 | 150 | 188400 | 33912 | 222312 | 187.5 | 235500 | 37.5 | 25% | 187.5 | 235500 | 0 |  | 0 | 0 | 235500 | 42390 | 277890 | 55578 | As per site requirement | B
10 | REVETMENT: (including Benching) Supply of all materials like cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. This includes supply of all labourers, T&P and dewatering (including Supply of all T&P, Fuel, Lubricant & electricity etc. as per Technical specification and instruction of Engineer In charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
10.1 | Excavation in all type of soil including rock & back filling including supply of sand with back filling. | CUM | 196 | 245 | 48020 | 8643.6 | 56663.6 | 245 | 48020 | 0 | 0% | 245 | 48020 | 0 |  | 0 | 0 | 48020 | 8643.6 | 56663.6 | 0 |  | A
10.2 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply of sand chips etc. | CUM | 7840 | 11 | 86240 | 15523.2 | 101763.2 | 11 | 86240 | 0 | 0% | 11 | 86240 | 0 |  | 0 | 0 | 86240 | 15523.2 | 101763.2 | 0 |  | A
10.3 | PCC in the ratio 1:2:4(Grade M-15) as above. | CUM | 9994 | 47 | 469718 | 84549.24 | 554267.24 | 47 | 469718 | 0 | 0% | 47 | 469718 | 0 |  | 0 | 0 | 469718 | 84549.24 | 554267.24 | 0 |  | A
10.4 | RR Massonary work in the ratio 1:5. | CUM | 7331 | 245 | 1796095 | 323297.1 | 2119392.1 | 245 | 1796095 | 0 | 0% | 245 | 1796095 | 0 |  | 0 | 0 | 1796095 | 323297.1 | 2119392.1 | 0 |  | A
11 | Railway, NHAI, Water,Gas/Oil pipeline, Power line and other statutory/government body clearances except Forest clearance (excluding payment of statutory fees) have to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 05 months of award of contract. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | LS | 502088 | 1 | 502088 | 90375.84 | 592463.84 | 1 | 502088 | 0 | 0% | 1 | 502088 | 0 |  | 0 | 0 | 502088 | 90375.84 | 592463.84 | 0 |  | A
12 | Forest clearances (excluding payment of statutory fees) has to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 05 months of award of contract. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hectare | 470707 | 2 | 941414 | 169454.52 | 1110868.52 | 2 | 941414 | 0 | 0% | 2 | 941414 | 0 |  | 0 | 0 | 941414 | 169454.52 | 1110868.52 | 0 |  | A
13 | Right of Way compensation (including land damage, crop damage & tree removal etc.) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
13.1 | Per location for foundation and erection of tower | Per Loc. | 147614 | 222 | 32770308 | 5898655.44 | 38668963.44 | 222 | 32770308 | 0 | 0% | 222 | 32770308 | 0 |  | 0 | 0 | 32770308 | 5898655.44 | 38668963.44 | 0 |  | A
13.2 | Per kilometer for stringing | Per Km. | 277403 | 61.19 | 16974289.57 | 3055372.1226 | 20029661.6926 | 61.556 | 17075819.068 | 0.366 | 0.5981% | 61.556 | 17075819.068 | 0 |  | 0 | 0 | 17075819.068 | 3073647.4322 | 20149466.5002 | 119804.8076 | As per approved route length | B
14 | PTCC approval has to be obtained by submitting the required documents to the concerned department through OPTCL & any other charges are to be borne by the bidders. The documents for PTCC clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 125522 | 1 | 125522 | 22593.96 | 148115.96 | 1 | 125522 | 0 | 0% | 1 | 125522 | 0 |  | 0 | 0 | 125522 | 22593.96 | 148115.96 | 0 |  | A
B | CIVIL COMPONENT OF THE WORKS CONTRACT FOR 220 KV TRANSMISSION LINE-PRATAPSASAN-ERSAMA |  |  |  | 290790882.15 | 52342358.787 | 343133240.937 |  | 592621826.8578 |  | 0% |  | 299759181.3379 |  |  |  | 230773746.2775 | 530532927.6153 | 95495926.9708 | 626028854.5861 | 282895613.6491

## C_400kV
TRANSRAIL LIGHTING LIMITED
BOQ Amendment Proposal - 1
CIVIL - 400kV T/L
Construction of (i) 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182 (ii) 220kV D/C line from Ersama, Paradeep to Pratapsasan along with (iii) 2 nos. 220 kV bay extension at existing 220/132/33 kV Grid S/S at Pratapsasan
LOA No: Sr.GM-CPC-I-Construction. - 400&220 KV Ersama-Pratapsasan Line — (Pkg- 36(III)/2020-21)-43/2020/1002 dated 24/12/2021.
Sl. No. | DESCRIPTION | UOM | Basic Price per Unit | LOA |  |  |  | 1st Amendment | 1st Amendment | Deviation quantity | Deviation Percentage | Within 25% deviation |  | Beyond 25% deviation |  |  |  | Total Revised Price | Total GST in INR (18%) | Total Revised Price (incl. GST) | Differential Amount (BOQ Amount & Amended Amount) including GST | Remarks |  | Open Cast | Pile | Total
|  |  |  | Qty | Amount | Total GST @18% | Total Amount Including GST | Qty | Amount as per LOA |  |  | Qty | Amount | Qty | RC Rate | Least Cost | Amount
B | CIVIL WORKS |  |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
1 | FOUNDATION MATERIALS: Supply of all materials like Cement, steel, all coarse aggregates, fine aggregates and making foundations of the required above mentioned type towers as per the direction laid down in the technical specification and the direction of the site- in charge.This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1 | Excavation in all type soil and rocks and back filling (back filling shall be done in layers and disposed of excess quantity of excavated soil at suitable place after back filling), & if required for filling the foundation, borrowed earth/murrum/sand shall be brought for filling and compaction, including supply of sand, all T&P, labour as required. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.1.1 | Soft/Loose Soil | CUM | 154 | 10828 | 1667512 | 300152.16 | 1967664.16 | 8012.339 | 1233900.1983 | -2815.661 | -26% | 8012.339 | 1233900.1983 | 0 | - | 0 | 0 | 1233900.1983 | 222102.0357 | 1456002.234 | -511661.926 |  | B | 5757.8 | 1872.999 | 7630.799
1.1.2 | Dense/Compact Soil | CUM | 167 | 32422 | 5414474 | 974605.32 | 6389079.32 | 13001.8329 | 2171306.0943 | -19420.1671 | -59.9% | 13001.8329 | 2171306.0943 | 0 |  | 0 | 0 | 2171306.0943 | 390835.097 | 2562141.1913 | -3826938.1287 |  | B | 8636.7 | 3745.998 | 12382.698
1.1.3 | Soft rock/Disintegrated rock (not requiring blasting) | CUM | 482 | 19464 | 9381648 | 1688696.64 | 11070344.64 | 18137.07 | 8742067.74 | -1326.93 | -6.817% | 18137.07 | 8742067.74 | 0 |  | 0 | 0 | 8742067.74 | 1573572.1932 | 10315639.9332 | -754704.7068 |  | B | 17273.4 | 0 | 17273.4
1.1.4 | Hard rock (requiring blasting/using breaker machinery) | CUM | 835 | 7000 | 5845000 | 1052100 | 6897100 | 6045.69 | 5048151.15 | -954.31 | -13.63% | 6045.69 | 5048151.15 | 0 |  | 0 | 0 | 5048151.15 | 908667.207 | 5956818.357 | -940281.643 |  | B | 5757.8 | 0 | 5757.8
1.1.5 | Fully submerged soil | CUM | 218 | 21400 | 4665200 | 839736 | 5504936 | 6373.4648 | 1389415.3319 | -15026.5352 | -70.22% | 6373.4648 | 1389415.3319 | 0 |  | 0 | 0 | 1389415.3319 | 250094.7597 | 1639510.0916 | -3865425.9084 |  | B | 5757.8 | 312.1665 | 6069.9665
1.1.6 | Partially submerged soil | CUM | 193 | 21808 | 4208944 | 757609.92 | 4966553.92 | 15441.9998 | 2980305.9662 | -6366.0002 | -29.19% | 15441.9998 | 2980305.9662 | 0 |  | 0 | 0 | 2980305.9662 | 536455.0739 | 3516761.0401 | -1449792.8799 |  | B | 14394.5 | 312.1665 | 14706.6665
1.2 | Design, Engineering, Providing and laying of plain Cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, Cement in tower foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 5437 | 1442 | 7840154 | 1411227.72 | 9251381.72 | 1593.896 | 8666012.552 | 151.896 | 10.53% | 1593.896 | 8666012.552 | 0 |  | 0 | 0 | 8666012.552 | 1559882.2594 | 10225894.8114 | 974513.0914 | As per approved drawing and site requirement | B | 906.08 | 249.28 | 1155.36
1.3 | Design, Engineering and laying of reinforced cement concrete (RCC1:1.5:3) of grade M20 for open cast foundation and pile caping, riser and tie beam for under ream/DMC (500 mm dia) and reverbed pile (1000 mm dia) with supply of approved quality coarse aggregates(Nominal size 12mm to 20mm), fine aggregates, cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample cement concrete cubes as per IS. The surrounding area shall be clear from materials. Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | CUM | 5960 | 14805 | 88237800 | 15882804 | 104120604 | 14718.7875 | 87723973.5 | -86.2125 | -0.5823% | 14718.7875 | 87723973.5 | 0 |  | 0 | 0 | 87723973.5 | 15790315.23 | 103514288.73 | -606315.27 |  | B | 7979.18 | 3795.85 | 11775.03
1.4 | Design, Engineering and laying of reinforced Cement concrete (RCC 1:1::2) of grade M25 for riverbed pile (1000 mm dia) foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, Cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample Cement concrete cubes as per IS. The surrounding area shall be clear from materials, Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. | CUM | 10551 | 850 | 8968350 | 1614303 | 10582653 | 2342.06 | 24711075.06 | 1492.06 | 175.5% | 1062.5 | 11210437.5 | 1279.56 | 8875.81 | 8875.81 | 11357131.4436 | 22567568.9436 | 4062162.4098 | 26629731.3534 | 16047078.3534 | For riverbed piling and as per approved pile foundation drawing | B |  | 2342.06 | 2342.06
1.5 | Design, Engineering and laying of reinforced Cement concrete (RCC 1:1.5:3) of grade M20 for under ream and DMC (500 mm dia) foundation with supply of approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, Cement in tower foundation and inclusive of labour charges for concrete mixing, supply and fixing of form boxes, curing, shoring, shuttering, testing of sample Cement concrete cubes as per IS. The surrounding area shall be clear from materials, Damage of land if any by the contractor shall be repaired before measurement. This includes supply of all labourers, T&P as per Technical specification and instruction of Engineer In charge. | CUM | 9610 | 1100 | 10571000 | 1902780 | 12473780 | 7115.346 | 68378475.06 | 6015.346 | 546.8% | 1375 | 13213750 | 5740.346 | 7870.43 | 7870.43 | 45178991.3688 | 58392741.3688 | 10510693.4464 | 68903434.8152 | 56429654.8152 | As per approved foundation drawing and site requirement | B |  | 6776.52 | 6776.52
1.6 | Cutting, bending, hooking, fixing and binding in poisition of MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL) as per BIS-1786 for rainforCement of foundation concrete of towers including supply of wire for binding (With supply of steel rod FE-500 as per BIS-1786 of different size(as per design). | MT | 61513 | 1600 | 98420800 | 17715744 | 116136544 | 1757.368 | 108100978.4606 | 157.368 | 9.836% | 1757.368 | 108100978.4606 | 0 |  | 0 | 0 | 108100978.4606 | 19458176.1229 | 127559154.5836 | 11422610.5836 | As per approved foundation drawing | B | 563.2798 | 1110.404 | 1673.6838
1.7 | Pile foundation: Boring for under ream cast in situ piling with bentonite sowing for stabilization of bore. |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
1.5.1 | Boring for under reamed cast in situ piling with betonite sowing for stabilisation of bore pile diameter (500mm) & approximate length of the bore is 10 Mtrs to 12 Mtrs with under reem in sandy and submerged soil | mtr length | 791 | 5508 | 4356828 | 784229.04 | 5141057.04 | 0 | 0 | -5508 | -100% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | -5141057.04 |  | B |  | 0 | 0
1.5.2 | Boring by DMC method piling with betonite sowing for stabilisation of bore pile diameter (1000mm) & approximate length of the bore is 25 Mtrs to 30 Mtrs in river bed and river bank. | mtr length | 8786 | 1080 | 9488880 | 1707998.4 | 11196878.4 | 12564 | 110387304 | 11484 | 1063% | 1350 | 11861100 | 11214 | 6462.95 | 6462.95 | 72475521.3 | 84336621.3 | 15180591.834 | 99517213.134 | 88320334.734 | As per approved soil test report and foundation drawing | B |  | 12564 | 12564
1.5.3 | Supply and putting of MS Liner 8mm (or as per approved drawing)for river bed & river bank pile foundation. | MT | 99162 | 154 | 15270948 | 2748770.64 | 18019718.64 | 193 | 19138266 | 39 | 25.32% | 192.5 | 19088685 | 0.5 | 68623.36 | 68623.36 | 34311.68 | 19122996.68 | 3442139.4024 | 22565136.0824 | 4545417.4424 | For riverbed pile foundation as per site requirement | B
2 | SURVEY OF LINE & PREPARATION LAND SCHEDULE: Supply of required T&P’s, Technical personnel’s, labours for conducting |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.1 | Preliminary survey :- Making walkover survey ascertaining feasible route and marking on Toposheet ,preparation of route alignment map. | RKms. | 30126 | 67.814 | 2042964.564 | 367733.6215 | 2410698.1855 | 8.504 | 256191.504 | -59.31 | -87.46% | 8.504 | 256191.504 | 0 |  | 0 | 0 | 256191.504 | 46114.4707 | 302305.9747 | -2108392.2108 |  | B
2.2 | Check survey including supply of all labour, T&P as per instruction of Engineer in Charge and as per the approved profile. | RKms. | 17135 | 67.814 | 1161992.89 | 209158.7202 | 1371151.6102 | 68.001 | 1165197.135 | 0.187 | 0.2758% | 68.001 | 1165197.135 | 0 |  | 0 | 0 | 1165197.135 | 209735.4843 | 1374932.6193 | 3781.0091 |  | B
2.3 | Detail survey with Preparation of Land Schedule:- Detail survey including taking of levels, profile plotting, tower spotting , marking of tower locations at site and preparation of tower schedule incluiding showing P&T, Power lines, Railway lines and river crossing, roads & submission of route map, profile & survey report etc. The P&T lines and railway lines for a minimum distance of 8 kms on either side of alignment shall be clearly indicated. It also includes preparation of land schedule with plot No., Mouza on Revenue map indicating alignment therein duly authenticated by Revenue inspector & Tehsildar, Enumeration of trees with the help of forest officers & other prominent features required for alignment of line. | Rkm | 20084 | 67.814 | 1361976.376 | 245155.7477 | 1607132.1237 | 8.504 | 170794.336 | -59.31 | -87.46% | 8.504 | 170794.336 | 0 |  | 0 | 0 | 170794.336 | 30742.9805 | 201537.3165 | -1405594.8072 |  | B
2.4 | Soil Investgation as per specification |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
2.4.1 | Normal foundation(Boring upto 3mtr,5 mtr, 7mtr depth.) | Per Mtr | 5020 | 1043 | 5235860 | 942454.8 | 6178314.8 | 198 | 993960 | -845 | -81.02% | 198 | 993960 | 0 |  | 0 | 0 | 993960 | 178912.8 | 1172872.8 | -5005442 |  | B
2.4.2 | For dis-integrated rock | per mtr | 8786 | 35 | 307510 | 55351.8 | 362861.8 | 27 | 237222 | -8 | -22.86% | 27 | 237222 | 0 |  | 0 | 0 | 237222 | 42699.96 | 279921.96 | -82939.84 |  | B
2.4.3 | River bed pile foundation( Boring to 30mtr depth) | per mtr | 6276 | 1140 | 7154640 | 1287835.2 | 8442475.2 | 434 | 2723784 | -706 | -61.93% | 434 | 2723784 | 0 |  | 0 | 0 | 2723784 | 490281.12 | 3214065.12 | -5228410.08 |  | B
3 | Shoring and Shuttering required in wet or special location with supply of all T & P and labour. | Sq m | 377 | 3054 | 1151358 | 207244.44 | 1358602.44 | 3054 | 1151358 | 0 | 0% | 3054 | 1151358 | 0 |  | 0 | 0 | 1151358 | 207244.44 | 1358602.44 | 0 |  | A
4 | Head-Loading of all types of foundation-materials, towers, structures, conductors, Insulators, Hard-wares for inaccessible Locations beyond 400 mtrs from the nearest approach road as per the recommendation of site Engineer-In- Charge and approval of the General Manager of Concerned circle. | MT-Mtr | 3 | 210500 | 631500 | 113670 | 745170 | 505200 | 1515600 | 294700 | 140% | 263125 | 789375 | 242075 | 11.1 | 3 | 726225 | 1515600 | 272808 | 1788408 | 1043238 | As per site requirement | B
5 | DE-WATERING ( for water logged and open cast foundations) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
5.1 | With Supply of all T&P, Fuel, Lubricant & electricity on HP Hour basis. | HP Hour | 50 | 3500 | 175000 | 31500 | 206500 | 4375 | 218750 | 875 | 25% | 4375 | 218750 | 0 |  | 0 | 0 | 218750 | 39375 | 258125 | 51625 | As per site requirement | B
6 | Painting of Tower Structures by applying one coat of zinc phosphate primer of ASIAN / BERGER make, 2 coats of Aluminium paint of ASIAN/BERGER make and applying one coat of black enamel paint over tower legs up to height of 1 mtr. including cost of material, consumables, T&P and as per the instruction of the Engineer in Charge (Scrapping and washing of structures are to be done prior to painting of towers) and applying | Per SQm | 1256 | 60 | 75360 | 13564.8 | 88924.8 | 60 | 75360 | 0 | 0% | 60 | 75360 | 0 |  | 0 | 0 | 75360 | 13564.8 | 88924.8 | 0 |  | A
7 | REVETMENT: (including Benching) Supply of all materials like Cement, Late-rite stone (stone masonry) all type aggregates, labours, & T&P for construction of revetment walls as per requirement to protect the towers, where felt unsafe and as per approved drawing and the direction of Engineer in charge. |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
7.1 | Excavation in all type of soil including rock & back filling including supply of sand with back filling. | CUM | 196 | 500 | 98000 | 17640 | 115640 | 500 | 98000 | 0 | 0% | 500 | 98000 | 0 |  | 0 | 0 | 98000 | 17640 | 115640 | 0 |  | A
7.2 | Lean Concrete in the ratio1:3:6(Grade M-10) including supply of sand chips etc. | CUM | 7840 | 25 | 196000 | 35280 | 231280 | 25 | 196000 | 0 | 0% | 25 | 196000 | 0 |  | 0 | 0 | 196000 | 35280 | 231280 | 0 |  | A
7.3 | PCC in the ratio 1:2:4(Grade M-15) as above. | CUM | 9994 | 100 | 999400 | 179892 | 1179292 | 100 | 999400 | 0 | 0% | 100 | 999400 | 0 |  | 0 | 0 | 999400 | 179892 | 1179292 | 0 |  | A
7.4 | RR Massonary work in the ratio 1:5. | CUM | 7331 | 500 | 3665500 | 659790 | 4325290 | 500 | 3665500 | 0 | 0% | 500 | 3665500 | 0 |  | 0 | 0 | 3665500 | 659790 | 4325290 | 0 |  | A
8 | PTCC approval has to be obtained by submitting the required documents to the concerned department through OPTCL & any other charges are to be borne by the bidders. The documents for PTCC clearance including required drawings etc has to be submitted by the contractor within 5 months of award of contract. Beyond the above period L.D as applicable & the amount shall be deducted as specified in the specification. | LS | 125522 | 1 | 125522 | 22593.96 | 148115.96 | 1 | 125522 | 0 | 0% | 1 | 125522 | 0 |  | 0 | 0 | 125522 | 22593.96 | 148115.96 | 0 |  | A
9 | Railway, NHAI, Water,Gas/Oil pipeline, Power line and other statutory/government body clearances except Forest clearance (excluding payment of statutory fees) have to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 05 months of award of contract. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | LS | 502088 | 1 | 502088 | 90375.84 | 592463.84 | 1 | 502088 | 0 | 0% | 1 | 502088 | 0 |  | 0 | 0 | 502088 | 90375.84 | 592463.84 | 0 |  | A
10 | Forest clearances (excluding payment of statutory fees) has to be obtained by submitting the required docuemnts to the concerned departments through OPTCL. The documents for above clearances including required drawings etc. have to be submitted by the contractor within 05 months of award of contract. Beyond the above period, L.D is applicable & the amount shall be deducted as specified in the specification. | Hectare | 470707 | 11 | 5177777 | 931999.86 | 6109776.86 | 14 | 6589898 | 3 | 27.27% | 13.75 | 6472221.25 | 0.25 |  | 470707 | 117676.75 | 6589898 | 1186181.64 | 7776079.64 | 1666302.78 | As per site requirement | B
11 | Right of Way compensation (including land damage, crop damage & tree removal etc.) |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0% | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | A
11.1 | Per location for foundation and erection of tower | Per Loc. | 191011 | 186 | 35528046 | 6395048.28 | 41923094.28 | 183 | 34955013 | -3 | -1.613% | 183 | 34955013 | 0 |  | 0 | 0 | 34955013 | 6291902.34 | 41246915.34 | -676178.94 |  | B
11.2 | Per kilometer for stringing | Per Km. | 360191 | 67.82 | 24428153.62 | 4397067.6516 | 28825221.2716 | 68.193 | 24562504.863 | 0.373 | 0.55% | 68.193 | 24562504.863 | 0 |  | 0 | 0 | 24562504.863 | 4421250.8753 | 28983755.7383 | 158534.4667 | As per approved route alignment | B
C | TOTAL OF CIVIL COMPONENT OF THE WORKS CONTRACT FOR 400 KV TRANSMISSION LINE-DUBURI-LOC-001 to LOC-182) |  |  |  | 364356186.45 | 65584113.561 | 429940300.011 |  | 528873373.9513 |  | 0% |  | 360788324.5813 |  |  |  | 129889857.5424 | 490678182.1237 | 88322072.7823 | 579000254.906 | 149059954.895
Note on I29: Ratul Ghosh: 76/0 - 82/0 & GTY - 7/0

## Sheet1
Percentage Increase/Decrease WRT Original LOA
SN | Description | LOA Price | 1st Revised BoQ Price(in INR) | Total Increase/Decrease wrt LOA | Percentage Increase/Decrease
| (Component of Works Contract) | (in INR) |  | (in INR) | WRT LOA
1 | 2 | 3 | 4 | 5=4-3 | 6=5/3%
A | 220kV Bay Extension
1 | Supply Component | 37995038.01 | 33291041.1615 | -4703996.8485 | -12.38%
2 | Electrical Component | 3487656.0732 | 3139528.3627 | -348127.7105 | -9.982%
3 | Civil Component | 35540866.63 | 29872475.26 | -5668391.37 | -15.95%
B | 220kV Line
1 | Supply Component | 351566702.661 | 422660672.0886 | 71093969.4276 | 20.22%
2 | Electrical Component | 37128913.9635 | 44343504.5338 | 7214590.5703 | 19.43%
3 | Civil Component | 343133240.937 | 626028854.5861 | 282895613.6491 | 82.44%
C | 400kV Line
1 | Supply Component | 1102212691.8355 | 1065084623.0746 | -37128068.761 | -3.369%
2 | Electrical Component | 100428161.5948 | 105666379.5449 | 5238217.9501 | 5.216%
3 | Civil Component | 429940300.011 | 579000254.906 | 149059954.895 | 34.67%
D | Total Project Cost | 2441433571.716 | 2909087333.5181 | 467653761.8021 | 19.15%

## Twr Qty-220kV
Name of Line: 220KV D/C PRATAPSASAN TO ERSAMA TRANSMISSION LINE (Wine Zone - 6)
Name of Execution Agency: M/s TRANSRAIL LIGHTING LIMITED
AS PER CHECK SURVEY
TYPE OF TOWER | +0 MTR EXT | +3 MTR EXT | +6 MTR EXT | +9 MTR EXT | TOTAL
OA TYPE | 105 | 26 | 11 | - | 142 | 145
OB TYPE | 30 | 13 | 5 | - | 48 | 48
OC TYPE | 14 | 8 | 10 | - | 32 | 29
UR TYPE | - | - | - | - | 0
|  |  |  | TOTAL | 222

## Wt Chart-220kV
TRANSRAIL LIGHTING LIMITED
TOWER & BOLT NUT WEIGHTS
G-487: | 220kV D/C line from Ersama, Paradeep to Pratapsasan Transmission Line
Type of Tower | Structure | Qty (Sets) | Unit Weight (Kg)
|  |  | HT | MS | Tower Parts | Bolt Nut | Total
OA | Stub | 142 | 331.24 |  | 331.24 | 10.52 | 341.76
OB | Stub | 48 | 429.4 |  | 429.4 | 10.81 | 440.21
OC | Stub | 32 | 507.48 |  | 507.48 | 10.81 | 518.29
OA | Template | 15 |  | 1135.04 | 1135.04 | 34.27 | 1169.31
OB | Template | 5 |  | 1446.28 | 1446.28 | 41.926 | 1488.206
OC | Template | 5 |  | 2190.92 | 2190.92 | 63.67 | 2254.59
Sub Total (MT) |  |  | 83.8866 | 35.2116 | 119.0982 | 3.4007 | 122.4989
OA | Normal Tower | 142 | 2729.55 | 3819.38 | 6548.93 | 302.94 | 6851.87
| +3MBE | 26 | 448.96 | 741.25 | 1190.21 | 47.99 | 1238.2
| +6MBE | 11 | 777 | 1483.28 | 2260.28 | 91.28 | 2351.56
OB | Normal Tower | 48 | 4872.59 | 3846.96 | 8719.55 | 385.14 | 9104.69
| +3MBE | 13 | 670.16 | 1053.14 | 1723.3 | 74.76 | 1798.06
| +6MBE | 5 | 1026.68 | 1692.52 | 2719.2 | 114.4 | 2833.6
OC | Normal Tower | 32 | 6049.76 | 5582.89 | 11632.65 | 510.21 | 12142.86
| +3MBE | 8 | 734.56 | 2145.65 | 2880.21 | 97.14 | 2977.35
| +6MBE | 10 | 1238.64 | 2680.58 | 3919.22 | 132.29 | 4051.51
Sub Total (MT) |  |  | 867.4011 | 1007.3715 | 1874.7726 | 83.7266 | 1958.4992
Grand Total (MT) |  |  | 951.2877 | 1042.5831 | 1993.8708 | 87.1273 | 2080.9981
Considering 5% B&N wastages |  |  |  |  | 1993.8708 | 91.4837 | 2085.3545

## Twr Qty-400kV
TOWER QUANTITY
| TYPE OF TOWER | +0 MTR EXT | +3 MTR EXT | +6 MTR EXT | +9 MTR EXT | +12 MTR EXT | +15 MTR EXT | +18 MTR EXT | +25 MTR EXT | TOTAL
| DA TYPE | 38 | 46 | 8 | 2 |  | 3 | - | - | 97
| DB TYPE | 13 | 6 |  | 1 |  | - | - | - | 20
| DC TYPE | 10 | 2 | 2 | - |  | - | - | - | 14
| DD TYPE | 7 | 8 | 5 | 5 | 2 | - | 16 | 8 | 51
[9 empty] | TOTAL | 182
DA | Basic Body | 38 | 46 | 8 | 2 |  | 3 |  |  | 97
| +0MBE | 38 |  | 8 | 2 |  | 3 |  |  | 51
| +3MBE |  | 46 | [6 empty] | 46
| +6MBE |  |  | 8 | [5 empty] | 8
| +9MBE |  |  |  | 2 |  |  |  |  | 2
| +15MBE | [5 empty] | 3 |  |  | 3
DB | Basic Body | 13 | 6 | 0 | 1 |  |  |  |  | 20
| +0MBE | 13 |  | 0 | 1 |  |  |  |  | 14
| +3MBE |  | 6 | [6 empty] | 6
| +6MBE |  |  | 0 | [5 empty] | 0
| +9MBE |  |  |  | 1 |  |  |  |  | 1
DC | Basic Body | 10 | 2 | 2 | - |  |  |  |  | 14
| +0MBE | 10 |  | 2 | - |  |  |  |  | 12
| +3MBE |  | 2 | [6 empty] | 2
| +6MBE |  |  | 2 | [5 empty] | 2
| +9MBE |  |  |  | - |  |  |  |  | 0
DD | Basic Body | 7 | 8 | 5 | 5 | 2 |  | 16 | 8 | 51
| +0MBE | 7 |  | 5 | 5 | 2 |  | 16 | 8 | 43
| +3MBE |  | 8 | [6 empty] | 8
| +6MBE |  |  | 5 | [5 empty] | 5
| +9MBE |  |  |  | 5 |  |  |  |  | 5
| +12MBE |  |  |  |  | 2 |  |  |  | 2
| +18MBE | [6 empty] | 16 |  | 16
| +25MBE | [7 empty] | 8 | 8

## Wt Chart-400kV
TRANSRAIL LIGHTING LIMITED
TOWER & BOLT NUT WEIGHTS
G-487: | 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182
Type of Tower | Structure | Qty (Sets) | Unit Weight (Kg)
|  |  | HT | MS | Tower Parts | Bolt Nut | Total
DA | Stub upto +9MBE | 97 | 564.16 |  | 564.16 | 13.55 | 577.71
DB | Stub upto +9MBE | 20 | 693 |  | 693 | 13.55 | 706.55
DC | Stub upto +9MBE | 14 | 844.08 |  | 844.08 | 17.97 | 862.05
DD | Stub upto +9MBE | 25 | 1231.84 |  | 1231.84 | 25.84 | 1257.68
DD | Stub for +12MBE | 2 | 1298.56 |  | 1298.56 | 26.08 | 1324.64
DD | Stub for +18/25MBE | 24 | 1298.56 |  | 1298.56 | 26.08 | 1324.64
DA | Template | 5 |  | 1860.45 | 1860.45 | 42.7 | 1903.15
DB | Template | 2 |  | 3066.76 | 3066.76 | 72.44 | 3139.2
DC | Template | 2 |  | 2349.89 | 2349.89 | 55.73 | 2405.62
DD | Template | 2 |  | 3738.52 | 3738.52 | 101.22 | 3839.74
Sub Total (MT) |  |  | 144.9592 | 27.6126 | 172.5718 | 3.8333 | 176.4051
DA | Basic Body | 97 | 5396.88 | 6259.47 | 11656.35 | 525.74 | 12182.09
| +0MBE | 51 | 1035.4 | 1753.53 | 2788.93 | 108.04 | 2896.97
| +3MBE | 46 | 1408.36 | 2592.95 | 4001.31 | 135.87 | 4137.18
| +6MBE | 8 | 1195.68 | 2596.76 | 3792.44 | 131.54 | 3923.98
| +9MBE | 2 | 1783.48 | 3335.45 | 5118.93 | 179.6 | 5298.53
| +15MBE | 3 | 7449 | 4011 | 11460 | 540 | 12000
DB | Basic Body | 20 | 9194.23 | 6365.9 | 15560.13 | 605.17 | 16165.3
| +0MBE | 14 | 1645.64 | 2225.56 | 3871.2 | 135.19 | 4006.39
| +3MBE | 6 | 2037.6 | 3242.36 | 5279.96 | 176.21 | 5456.17
| +6MBE | 0 | 1940.96 | 3000.68 | 4941.64 | 157.26 | 5098.9
| +9MBE | 1 | 2784.64 | 3477.77 | 6262.41 | 199.99 | 6462.4
DC | Basic Body | 14 | 11498.63 | 5928.17 | 17426.8 | 671.47 | 18098.27
| +0MBE | 12 | 2049.48 | 2425.25 | 4474.73 | 146.05 | 4620.78
| +3MBE | 2 | 2621 | 3421.98 | 6042.98 | 191.24 | 6234.22
| +6MBE | 2 | 1508.52 | 3985.52 | 5494.04 | 168.15 | 5662.19
| +9MBE | 0 | 2722.24 | 4346.33 | 7068.57 | 219.57 | 7288.14
DD | Basic Body | 51 | 13165.7 | 8021.65 | 21187.35 | 1042.58 | 22229.93
| +0MBE | 43 | 2665.92 | 2905.27 | 5571.19 | 227.33 | 5798.52
| +3MBE | 8 | 4061.8 | 3248.6 | 7310.4 | 278.83 | 7589.23
| +6MBE | 5 | 2298.52 | 4052.81 | 6351.33 | 227.04 | 6578.37
| +9MBE | 5 | 3254.36 | 5539.69 | 8794.05 | 317.91 | 9111.96
| +12MBE | 2 | 4515.68 | 7278.35 | 11794.03 | 410.24 | 12204.27
| +18MBE | 16 | 6690.48 | 14689.72 | 21380.2 | 720.86 | 22101.06
| +25MBE | 8 | 9632.92 | 19846.99 | 29479.91 | 823.18 | 30303.09
Sub Total (MT) |  |  | 2131.8206 | 2180.0226 | 4311.8432 | 179.7555 | 4491.5987
Grand Total (MT) |  |  | 2276.7798 | 2207.6352 | 4484.415 | 183.5888 | 4668.0038

## 400kV_Open
NAME OF LINE: 400KV D/C NEW DUBURI TO LOC 182 TOWARDS ERSAMA T/L (WIND ZONE -6)
CLIENT: ODISHA POWER TRANSMISSION CORPORATION LIMITED
AGENCEY: TRANSRAIL LIGHTING LTD
Sub: | VOLUME CHART
SL NO | TOT | CLASSIFN. | No. of Locs | EXCAVATION VOLUME (CuM) | FOUNDATION VOLUME (CuM ) |  | Stub weight incl N&B in kG | Reinforcement Steel (Kg)
[5 empty] | M10 (1:3:6) | M20 (1:1.5:3)
1 | DA+0 | WET | 9 | 265.1 | 3.87 | 31.17 | 577.71 | 1969.32
2 |  | PS | 7 | 330.8 | 4.9 | 39.31 | 577.71 | 2335.25
3 |  | FS | 3 | 424.8 | 6.38 | 49.35 | 577.71 | 2994.15
4 |  | WBC |  | 522.7 | 7.94 | 59.9 | 577.71 | 3866.11
5 |  | DFR | 3 | 142.7 | 3.04 | 25.55 | 577.71 | 1588.27
6 |  | WFR |  | 221.7 | 4.51 | 35.42 | 577.71 | 2329.65
7 | DA+3/6/9 | WET | 17 | 324.5 | 4.8 | 37.54 | 577.71 | 3050.07
8 |  | PS | 14 | 403.7 | 6.05 | 47.49 | 577.71 | 3483.37
9 |  | FS | 1 | 507 | 7.69 | 58.61 | 577.71 | 4521.52
10 |  | WBC |  | 657.1 | 10.08 | 74.92 | 577.71 | 6156.28
11 |  | DFR | 1 | 177.7 | 3.7 | 30.11 | 577.71 | 2410.58
12 |  | WFR | 2 | 287.8 | 5.72 | 43.77 | 577.71 | 3676.92
13 | DB+3/6/9 | WET | 2 | 343.5 | 5.1 | 42.25 | 706.55 | 2995.92
14 |  | PS | 4 | 432 | 6.5 | 53.82 | 706.55 | 3584.33
15 |  | FS | 1 | 538.7 | 8.19 | 65.32 | 706.55 | 4489.87
16 |  | WBC | 2 | 657.1 | 10.08 | 78.2 | 706.55 | 5808.69
17 |  | DFR | 1 | 191.8 | 3.96 | 34.57 | 706.55 | 2413.89
18 |  | WFR | 1 | 299.7 | 5.94 | 47.93 | 706.55 | 3619.51
19 | DC+3/6/9 | WET | 2 | 417.7 | 6.27 | 54.69 | 862.05 | 3748.88
20 |  | PS | 8 | 519.6 | 7.89 | 65.66 | 862.05 | 4756.88
21 |  | FS |  | 648.3 | 9.94 | 81.87 | 862.05 | 5808.83
22 |  | WBC |  | 771.8 | 11.92 | 97.02 | 862.05 | 6965.45
23 |  | DFR |  | 242.8 | 4.9 | 43.44 | 862.05 | 3048.19
24 |  | WFR | 1 | 369.3 | 7.2 | 60.99 | 862.05 | 4317.16
25 | DD+3/6/9 | WET | 5 | 613.5 | 9.38 | 88.79 | 1257.68 | 6405.15
26 |  | PS | 6 | 748.9 | 11.55 | 112.64 | 1257.68 | 7328.41
27 |  | FS | 1 | 918.8 | 14.28 | 133.86 | 1257.68 | 9256.53
28 |  | WBC | 4 | 1060.3 | 16.56 | 151.64 | 1257.68 | 11144.3
29 |  | DFR | 3 | 364.6 | 7.32 | 72.85 | 1257.68 | 4877.77
30 |  | WFR | 2 | 532.6 | 10.37 | 96.4 | 1257.68 | 7391.3
31 | DD+18/25 | WET |  | 618.6 | 9.47 | 89.43 | 1324.64 | 6703
32 |  | PS | 9 | 752.7 | 11.61 | 113.12 | 1324.64 | 7557
33 |  | FS | 4 | 925.1 | 14.38 | 134.65 | 1324.64 | 9710
34 |  | WBC | 1 | 1073.9 | 16.78 | 153.35 | 1324.64 | 11657
35 |  | DFR | 6 | 366 | 7.34 | 73.04 | 1324.64 | 5077
36 |  | WFR |  | 540.6 | 10.51 | 97.52 | 1324.64 | 7738
Tentative Open Cast Volume |  |  | 120 | 57578 | 906.08 | 7979.18 | 103088.15 | 563.2798
|  |  | Soft/Loose Soil | 5757.8 | 10%
|  |  | Dense/Compact Soil | 8636.7 | 15%
|  |  | Soft rock/Disintegrated rock | 17273.4 | 30%
|  |  | Hard rock | 5757.8 | 10%
|  |  | Fully submerged soil | 5757.8 | 10%
|  |  | Partially submerged soil | 14394.5 | 25%
100%

## 400kV_Pile
NAME OF LINE: 400KV D/C NEW DUBURI TO LOC 182 TOWARDS ERSAMA T/L (WIND ZONE -6)
CLIENT: ODISHA POWER TRANSMISSION CORPORATION LIMITED
AGENCEY: TRANSRAIL LIGHTING LTD
Sub: VOLUME CHART
[7 empty] | 791 | 8786 | 154 | 5437 | 5960 | 61.513 | 9610 | 10551 | 61.513
SL NO | TOT | CLASSIFN. | Pile Dia (mm) | No. of Piles per Tower | Pile Length (mm) | No. of Locs | Boring Length per Tower (mtr) |  | Pile Cap & Chimney Volumes |  |  |  | Pile Volumes |  |  | Revenue (Rs lacs)
[7 empty] | 500mm | 1000mm | Excavation Volume (CuM) | M10 (1:3:6) | M20 (1:1.5:3) | Reinforcement Steel (Kg) | M20 | M25 | Reinforcement Steel (Kg)
1 | DA | Clay | 1000 | 8 | 22000 | 12 |  | 176 | 74.09 | 2.9 | 38.76 | 3079 | 128.81 |  | 7596 | 36.9904
2 | DA | Clay+Sand | 1000 | 8 | 16500 | 25 |  | 132 | 74.09 | 2.9 | 38.76 | 3079 | 94.25 |  | 5756 | 28.6715
3 | DB | Clay+Sand | 1000 | 8 | 19500 | 6 |  | 156 | 80.26 | 3.17 | 43.58 | 3444 | 113.1 |  | 8388 | 34.7466
4 | DB | Clay | 1000 | 8 | 26000 | 3 |  | 208 | 80.26 | 3.17 | 43.58 | 3444 | 153.94 |  | 11436
5 | DC | Fully Clay | 1000 | 16 | 17500 | 3 |  | 280 | 151.26 | 6.35 | 91.46 | 5665 | 201.06 |  | 15124
6 | DD | Clay | 1000 | 16 | 19500 | 5 |  | 312 | 160.87 | 6.35 | 99.73 | 6411 | 226.19 |  | 25360 | 75.2294
7 | DD | Clay+Sand | 1000 | 16 | 17500 |  |  | 280 | 160.87 | 6.35 | 99.73 | 6411 | 201.06 |  | 22928
8 | DA | Bramhani River Bed | 1000 | 20 | 24000 | 3 |  | 480 | 239.06 | 10.3 | 194.97 | 13092 |  | 353.43 | 57964
9 | DD | Bramhani River Bank | 1000 | 16 | 18500 | 2 |  | 296 | 160.87 | 6.35 | 118.45 | 8731 |  | 213.63 | 31252
10 | DD | Birupa River_AP-80 & 81 | 1000 | 16 | 27000 | 2 |  | 432 | 160.87 | 6.35 | 128.12 | 9259 |  | 320.44 | 39800
11 | DD | Birupa River_AP82 | 1000 | 16 | 18500 | 1 |  | 296 | 160.87 | 6.35 | 118.43 | 8275 |  | 213.63 | 25048
Tentative Pile Volumes | [5 empty] | 62 | 0 | 12564 | 6243.33 | 249.28 | 3795.85 | 277.5 | 6776.52 | 2342.06 | 832.904
Soft/Loose Soil |  | 1872.999 | 30%
Dense/Compact Soil |  | 3745.998 | 60% |  |  | Work |  | Open cast | Pile Cap | Total | % Increase | Grand Total
Soft rock/Disintegrated rock |  | 0 |  |  |  | Soft/Loose soil |  | 5757.8 | 1872.999 | 7630.799 | 5% | 8012.339
Hard rock |  | 0 |  |  |  | Dense/Compact soil |  | 8636.7 | 3745.998 | 12382.698 | 5% | 13001.8329
Fully submerged soil |  | 312.1665 | 5% |  |  | Soft/Disintegrated rock |  | 17273.4 | 0 | 17273.4 | 5% | 18137.07
Partially submerged soil |  | 312.1665 | 5% |  |  | Hard rock |  | 5757.8 | 0 | 5757.8 | 5% | 6045.69
[6 empty] | Fully submerged soil |  | 5757.8 | 312.1665 | 6069.9665 | 5% | 6373.4648
[6 empty] | Partial Submerged soil |  | 14394.5 | 312.1665 | 14706.6665 | 5% | 15441.9998
[6 empty] | M10 PCC(Open+ Cap) |  | 906.08 | 249.28 | 1155.36 | 38% | 1594.3968
[6 empty] | M20 RCC (Open+Cap) |  | 7979.18 | 3795.85 | 11775.03 | 25% | 14718.7875
[6 empty] | REINFORCEMENT(Open+Pile+Cap) |  | 563.2798 | 1110.404 | 1673.6838 | 5% | 1757.368
[6 empty] | M20 RCC (Pile) |  |  | 6776.52 | 6776.52 | 5% | 7115.346

## 220kV_Open
NAME OF LINE: 220KV D/C PRATAPSASAN TO ERSAMA T/L (WIND ZONE -6)
CLIENT: ODISHA POWER TRANSMISSION CORPORATION LIMITED
AGENCEY: TRANSRAIL LIGHTING LTD
Sub: | VOLUME CHART
SL NO | TOT | CLASSIFN. | No. of Locs | EXCAVATION VOLUME (CuM) | FOUNDATION VOLUME (CuM ) |  | Stub weight incl N&B in kG | REINFORCEMENT (kg)
[5 empty] | M10 (1:3:6) | M20 (1:1.5:3)
1 | OA+0/3/6 | WET | 3 | 164.3 | 2.31 | 17.42 | 341.76 | 1088.42
2 |  | PS | 20 | 216.8 | 3.12 | 22.48 | 341.76 | 1340
3 |  | FS | 25 | 282.3 | 4.14 | 28.41 | 341.76 | 1762.5
4 |  | WBC | 10 | 363 | 5.41 | 36.58 | 341.76 | 2417.21
5 |  | DFR |  | 86.5 | 1.86 | 14.76 | 341.76 | 948.86
6 |  | WFR |  | 141.6 | 2.89 | 20.68 | 341.76 | 1331.14
7 | 0B+0/3/6 | WET |  | 227.1 | 3.28 | 24.08 | 440.21 | 1798.46
8 |  | PS | 1 | 294 | 4.32 | 30.6 | 440.21 | 2203.24
9 |  | FS | 3 | 373.6 | 5.58 | 37.9 | 440.21 | 2883.78
10 |  | WBC | 1 | 473.3 | 7.15 | 51.59 | 440.21 | 3076.21
11 |  | DFR |  | 125.6 | 2.59 | 20.03 | 440.21 | 1453.46
12 |  | WFR |  | 200.2 | 3.96 | 27.96 | 440.21 | 1826.79
13 | OC+0/3/6 | WET |  | 265.1 | 3.87 | 28.54 | 518.29 | 2181.95
14 |  | PS |  | 339.6 | 5.04 | 36 | 518.29 | 2660.23
15 |  | FS |  | 429.1 | 6.45 | 45.06 | 518.29 | 3312.2
16 |  | WBC |  | 535.5 | 8.14 | 58.6 | 518.29 | 3753.76
17 |  | DFR |  | 154.2 | 3.12 | 24.1 | 518.29 | 1733.67
18 |  | WFR |  | 236 | 4.61 | 33.48 | 518.29 | 2431.93
|  |  | 63 | 17404.5 | 255.14 | 1773.8 | 22023.13 | 112.2307
|  |  | Soft/Loose soil | 4177.08 | 24%
|  |  | Dense/Compact soil | 4177.08 | 24%
|  |  | Soft/Disintegrated rock | 0 | 0%
|  |  | Hard rock | 0 | 0%
|  |  | Fully submerged soil | 4351.125 | 25%
|  |  | Partial Submerged soil | 4699.215 | 27%

## 220kV_Pile
CLIENT: ODISHA POWER TRANSMISSION CORPORATION LIMITED
AGENCY: TRANSRAIL LIGHTING LTD
Sub: VOLUME CHART (PILE)
220 kV
[7 empty] | 791 | 8786 | 189 | 6031 | 7061 | 67.97 | 9610 | 10551 | 67.97
SL NO | TOT | CLASSIFN. | Pile Dia (mm) | No. of Piles per Tower | Pile Length (mm) | No. of Locs | Boring Length per Tower (mtr) |  | Pile Cap & Chimney Volumes |  |  |  | Pile Volumes |  |  | Revenue (Rs. Lacs)
[7 empty] | 500mm | 1000mm | Excavation Volume (CuM) | M10 (1:3:6) | M20 (1:1.5:3) | Reinforcement Steel (Kg) | M20 | M25 | Reinforcement Steel (Kg)
1 | OA | Fully Clay Soil & Clay + Sandy Soil | 1000 | 4 | 25500 | 82 |  | 102 | 25.2 | 0.87 | 11.01 | 1322 | 75.4 |  | 7248 | 22.9102
2 | OB | Fully Clay Soil, Clay + Sandy Soil & Fully Sandy Soil | 1000 | 8 | 18000 | 43 |  | 144 | 74.09 | 2.9 | 38.77 | 3031 | 103.67 |  | 7008 | 32.4905
3 | OC | Fully Clay Soil & Clay + Sandy Soil | 1000 | 16 | 12500 | 29 |  | 200 | 151.26 | 6.35 | 91.1 | 5657 | 138.23 |  | 7792 | 47.0986
4 | OA | River Crossing | 1000 | 16 | 16250 | 2 |  | 260 | 196.638 | 8.255 | 118.43 | 7354.1 | 0 | 179.699 | 10129.6 | 62.9192
5 | OC | For Pratapsasan-Nuapada line | 500 | 12 | 12500 | 3 | 150 |  | 36.892 | 4.891 | 33.168 |  | 48.552 |  | 4951
Tentative Pile Volume | [5 empty] | 159 | 450 | 20876 | 10142.762 | 411.373 | 5548.194 | 417.4982 | 14794.936 | 359.398 | 1156.7602
|  | Soft/Loose soil | 6085.6572 | 60% |  |  | Work |  | Open cast | Pile Cap | Total | % Increase | Grand Total
|  | Dense/Compact soil | 4057.1048 | 40% |  |  | Soft/Loose soil |  | 4177.08 | 6085.6572 | 10262.7372 | 5% | 10775.8741
|  | Soft/Disintegrated rock | 0 |  |  |  | Dense/Compact soil |  | 4177.08 | 4057.1048 | 8234.1848 | 5% | 8645.894
|  | Hard rock | 0 |  |  |  | Soft/Disintegrated rock |  | 0 | 0 | 0 | 5% | 0
|  | Fully submerged soil | 0 | 0% |  |  | Hard rock |  | 0 | 0 | 0 | 5% | 0
|  | Partial Submerged soil | 0 | 0% |  |  | Fully submerged soil |  | 4351.125 | 0 | 4351.125 | 5% | 4568.6812
[7 empty] | Partial Submerged soil |  | 4699.215 | 0 | 4699.215 | 5% | 4934.1758
[7 empty] | M10 PCC(Open+ Cap) |  | 255.14 | 411.373 | 666.513 | 10% | 733.1643
[7 empty] | M20 RCC (Open+Cap) |  | 1773.8 | 5548.194 | 7321.994 | 10% | 8054.1934
[7 empty] | REINFORCEMENT(Open+Pile+Cap) |  | 112.2307 | 1574.2584 | 1686.489 | 0% | 1686.489

## HW 400 kV
Transrail Lighting Limited
Calculation of Hardware fittings, Accessories & Insulators (400kV)
|  |  | 101 |  | 20 |  | 15 |  | 52 | 188
Item Description | Unit | DA |  | DB |  | DC |  | DD |  | Grand Total | Permitted Wastage | Total including Wastage
|  | Per Tower | Total | Per Tower | Total | Per Tower | Total | Per Tower | Total
Single suspension Hardwares (AGS type) fittings for pilot insulator. | set |  | 0 |  | 0 | 6 | 90 | 6 | 312 | 402 | 20 | 422
Double suspension Hardwares fittings.(AGS type) for ACSR Moose. | set | 6 | 606 |  | 0 |  | 0 |  | 0 | 606 | 20 | 626
Double tension Hardwares fittings suitable for ACSR Moose. | set |  | 0 | 12 | 240 | 12 | 180 | 12 | 624 | 1044 | 20 | 1064
D SACKLE(SUITABLE FOR 20MM DIA, 75MM LONG) | Nos. |  | 0 | 12 | 240 | 12 | 180 | 12 | 624 | 1044 | 20 | 1064
U' Bolt | Nos. | 1 | 101 |  | 0 |  | 0 |  | 0 | 101 | 10 | 111
4R VIBRATION DAMPER FOR SUSPENSION | Nos. | 24 | 2424 |  | 0 |  | 0 |  | 0 | 2424 | 16 | 2440
4R VIBRATION DAMPER FOR TENSION | Nos. |  | 0 | 48 | 960 | 48 | 720 | 48 | 2496 | 4176 | 20 | 4196
Rigid Spacer | Nos. |  | 0 | 18 | 360 | 18 | 270 | 26 | 1352 | 1982 | 24 | 2006
160 KN Long Rod PORCELAIN INSULATOR (taking 5% extra towards wastage) | Nos. | 0 | 0 | 72 | 1440 | 72 | 1080 | 72 | 3744 | 6264 | 188 | 6452
120 KN Long Rod PORCELAIN INSULATOR (taking 5% extra towards wastage) | Nos. | 36 | 3636 | 0 | 0 | 18 | 270 | 18 | 936 | 4842 | 145 | 4987
EARTH CONDUCTOR ACESSORIES
VIBRATION DAMPER | Nos. | 2 | 202 | 4 | 80 | 4 | 60 | 4 | 208 | 550 |  | 550
FLEXIBLE EARTH BOND for 7/3.66mm earth wire | Nos. | 1 | 101 | 2 | 40 | 2 | 30 | 2 | 104 | 275 |  | 275
SUSPENSION CLAMP for 7/3.66mm earth wire | Nos. | 1 | 101 |  | 0 |  | 0 |  | 0 | 101 |  | 101
TENSION CLAMP with terminal jumper for 7/3.66mm earth wire | Nos. |  | 0 | 2 | 40 | 2 | 30 | 2 | 104 | 174 |  | 174
|  |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0

## HW 220 kV
Transrail Lighting Limited
Calculation of Hardware fittings, Accessories & Insulators (220kV)
|  |  | 144 |  | 7 |  | 48 |  |  |  | 22 |  | 8 | 229
Item Description | Unit | OA |  | OA (crossing) |  | OB |  | OB (crossing) |  | OC |  | OC (crossing) |  | Grand Total | Permitted Wastage | Total including Wastage
|  | Per Tower | Total | Per Tower | Total | Per Tower | Total | Per Tower | Total | Per Tower | Total | Per Tower | Total
Single suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set | 6 | 864 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 864 |  | 864
Double suspension Hard wares AGS Type fittings suitable for 90 KN Long Rod insulator. | Set |  | 0 | 6 | 42 |  | 0 |  | 0 |  | 0 |  | 0 | 42 |  | 42
Single tension Hard wares fittings, suitable for 160 KN Long Rod insulator. | Set |  | 0 |  | 0 | 12 | 576 |  | 0 | 12 | 264 |  | 0 | 840 |  | 840
Double tension Hard wares fittings, suitable for 160 KN Log Rod insulator. | Set |  | 0 |  | 0 |  | 0 | 12 | 0 |  | 0 | 12 | 96 | 96 |  | 96
“D” Shackle | Nos. |  | 0 |  | 0 | 12 | 576 | 12 | 0 | 12 | 264 | 12 | 96 | 936 |  | 936
Hanger | Nos. | 6 | 864 | 6 | 42 |  | 0 |  | 0 |  | 0 |  | 0 | 906 |  | 906
U'-Bolt. | Nos |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
160 KN Long Rod Antifog PORCELAIN INSULATOR | Nos | 0 | 0 | 0 | 0 | 24 | 1152 | 48 | 0 | 24 | 528 | 48 | 384 | 2064 | 62 | 2126
90 KN Long Rod Antifog PORCELAIN INSULATOR | Nos | 12 | 1728 | 24 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1896 | 57 | 1953
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
VIBRATION DAMPER | Nos. | 12 | 1728 | 12 | 84 | 24 | 1152 | 24 | 0 | 24 | 528 | 24 | 192 | 3684 |  | 3684
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0
|  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 | 0 |  | 0

## Volume
CLIENT : ODISHA POWER TRANSMISSION & CORPORATION LTD.
AGENCY : TRANSRAIL LIGHTING LTD
SITE : 220/132/33 KV EXTENTION BAY.PRATAPSASAN
ACTIVITY : SWITCH YARD FOUNDATION
SUMMARY
SNO | PARTICULARS | SI No | Unit | NOS OF FOUNDATION | NOS | Qty. as per BOQ | CT | CVT | SA | PI | CB | ISO | RP-1S (Tower) | QTY
1 | Pile Boring | 5.1 | Mtr
| 375 mm Dia | 5.1.3 | Mtr |  | 1 |  | 33.6 | 27.6 | 36.6 | 81.6 | 36.6 | 292.8 | 188 | 696.8
2 | Earth work in excavation in loose/soft soil | 2.1 | Cum |  | 1 |  | 19.074 | 14.175 | 10.647 | 34.496 | 10.647 | 105.44 | 70.56 | 265.039
3 | Providing & Laying in position of specified grade Cement Concrete Nominal Mix -1 Cement : 3 sand : 6 graded stone aggregate (M -10) |  | Cum |  | 1 |  | 1.35 | 0.864 | 0.6 | 1.936 | 0.726 | 14 | 3.44 | 22.916
4 | Reinforcement for RCC work…copmplete.
| TMT Bars |  | Kg |  |  |  | 792.96 | 521.5378 | 530.9422 | 1434.2163 | 551.6237 | 6102.8662 | 3136.637 | 13070.7832
| Mild steel & medium tensile bars |  | Kg
5 | Centering & shuttering …. For foundations, footings & Pedestal |  | Sqm |  |  |  | 42.6 | 31.68 | 25.44 | 79.04 | 28.56 | 309.76 | 139 | 656.08
6 | Providing & laying in position reinforced cement concrete M-20 Grade(1:1.5:3) |  | Cum |  |  |  | 18.1709 | 12.0335 | 10.435 | 47.5725 | 11.659 | 97.3762 | 53.6359 | 250.883
7 | Foundation bolt for grouting |  | Kg |  | 8 |  | 48 | 48 |  | 128 | 24 |  |  | 248
8 | Back Filling available excavated earth in Excavation |  | Cum |  | 1 |  | 6.57 | 7.011 | 6.015 | 18.304 | 4.818 | 55.8 | 43.2 | 141.718

## BBS
SUMMARY SHEET
TRANSRAIL LIGHTING LTD.
Name of Project :-220/132/33 KV Bay Ext.Pratap Sasan
BAR BENDING SCHEDULE FOR FOUNDATION :-
Sr. No | Description
|  | 8mm | 10mm | 12mm | 16mm | 20mm | 25mm | 32mm | Total
1 | 220 KV PI | 153.9793 | 574.8148 | 705.4222 | 0 | 0 | 0 | 0 | 1434.2163
2 | 220 KV CVT | 52.9304 | 204.0741 | 264.5333 | 0 | 0 | 0 | 0 | 521.5378
3 | 220 KV CT | 64.96 | 280 | 448 | 0 | 0 | 0 | 0 | 792.96
4 | 220 KV SA | 69.7719 | 213.7037 | 247.4667 | 0 | 0 | 0 | 0 | 530.9422
5 | 220 KV CB | 69.7719 | 225.8519 | 256 | 0 | 0 | 0 | 0 | 551.6237
6 | 220 KV ISO | 1158.5106 | 1688.8889 | 3255.4667 | 0 | 0 | 0 | 0 | 6102.8662
7 | 220 KV RP-1S | 538.7852 | 1115.1852 | 1482.6667 | 0 | 0 | 0 | 0 | 3136.637
| TOTAL | 2108.7091 | 4302.5185 | 6659.5556 | 0 | 0 | 0 | 0 | 13070.7832 | 13070.7832 | Kg
[9 empty] | 13.0708 | 12549.2454
12.5492

## Crossing
TRANSRAIL LIGHTING LIMITED
400kV Crossing Details
Sl. No. | Section | Section Length (Mtr) | Type of Crossing
1 | AP 57 - AP 58 | 237 | NH Crossing
2 | AP 27 - AP 28 | 236 | NH Crossing
3 | AP 11 - AP 12 | 219 | NH Crossing
4 | AP 39 - AP 40 | 291 | Rly Crossing
5 | AP 1 - AP 2 | 130 | 400 kV New Duburi - Tata T/L Crossing
6 | AP 8 - AP 9 | 154 | 220 kV Dc Old Duburi-New Duburi Line
7 | AP 12 - AP 13 | 230 | 132 kV Traction Line To Jakhapura Line & 220Kv Old Duburi-New Duburi Dc Line
8 | AP 14 - AP 15 | 181 | 132 kV S/C Old Duburi - Mishralal Plant
9 | AP 18 - AP 19 | 180 | 132 kV S/C Old Duburi-Mishralal Line
10 | AP 22 - AP 22A | 164 | 132 kV S/C Old Duburi-Mishralal Line
11 | AP 22A - AP 23 | 185 | 400 kV D/C Meramundali -Duburi Line
12 | AP 25 - AP 26 | 199 | 220 kV D/C Duburi- Paradeep Line
13 | AP 48 - AP 49 | 189 | 400 kV D/C Baripada-Mendhashal T/L, Pond, Nala
14 | AP 54 - AP 55 | 161 | 132 kV Jajpur Road-Kendrapara Line
2756

## 400_FDN Type
TRANSRAIL LIGHTING LIMITED.
400KV D/C NEW DUBURI TO LOC 182 TOWARDS ERSAMA T/L (WIND ZONE -6)
CHECK SURVEY REPORT FROM GANTRY to AP82/0 = 68.001 Km.
Sl.No. | Loc. No. | Type of Tower | RC | Angle of Deviation | Span Length (m) | Section Length (m) | Crossing Details | Remarks / Village | GPS Co-ordinate (UTM) |  | Foundation Type | Tentative Soil Classification
[9 empty] | Easting | Northing
1 | AP-1 | DD+12 |  | 35°53'40"RT |  | 75 |  | MIRIGACHARA | 396805 | 2315373 | Open Cast | HR
[5 empty] | 130 |  | PADDY FIELD
2 | AP-2 | DD+25 |  | 42°07'45"RT |  | 130 |  | MIRIGACHARA | 396826 | 2315245 | Open Cast | DFR
[5 empty] | 114 |  | PADDY FIELD
3 | AP-3 | DD+12 |  | 48°02'54"RT |  | 114 |  | MIRIGACHARA | 396750 | 2315160 | Open Cast | WFR
[5 empty] | 82 |  | PADDY FIELD, 11KV LINE
4 | AP-4 | DD+6 |  | 36°15'46"RT |  | 82 |  | MIRIGACHARA | 396668 | 2315154 | Open Cast | WFR
[5 empty] | 186 |  | PADDY FIELD
5 | AP-6 | DB+3 |  | 12°31'58"RT |  | 186 |  | MIRIGACHARA | 396511.895 | 2315251.938 | Open Cast | WFR
[5 empty] | 371 |  | 11KV LINE,LIGHT POST,TAR ROAD
6 | AP-7 | DB+9 |  | 12°22'28"LT |  | 371 |  | MIRIGACHARA | 396237.309 | 2315500.855 | Open Cast | DFR
[5 empty] | 439 |  | 11KV LINE ,PADDY FIELD
7 | AP-8 | DD+25 |  | 54°57'33"RT |  | 439 |  | MIRIGACHARA | 395857.104 | 2315718.762 | Open Cast | HR
[5 empty] | 154 |  | 220KV DC OLD DUBURI-NEW DUBURI LINE
8 | AP-9 | DD+25 |  | 15°09'01"LT |  | 154 |  | MIRIGCHARA | 395843.093 | 2315872.057 | Open Cast | DFR
[5 empty] | 392 |  | PADDY FIELD
9 | AP-10 | DD+0 |  | 48°53'5"LT |  | 392 |  | MIRIGCHARA | 395706.936 | 2316238.71 | Open Cast | HR
[5 empty] | 405 |  | PADDY FIELD , POND
10 | AP-11 | DD+6 |  | 52°50'25"LT |  | 405 |  | MIRIGCHARA | 395329.137 | 2316381.789 | Open Cast | HR
[5 empty] | 219 |  | NH-53, 2NOS 11KV LINE, 33KV LINE
11 | AP-12 | DD+25 |  | 8°06'50"LT |  | 219 |  | MIRIGCHARA | 395143.938 | 2316265.624 | Open Cast | DFR
[5 empty] | 230 |  | 132KV TRACTION LINE TO JAKHAPURA LINE & 220KV OLD DUBURI-NEW DUBURI DC LINE
12 | AP-13 | DD+25 |  | 16°05'17"RT |  | 230 |  | MIRIGCHARA | 394968.878 | 2316117.625 | Open Cast | DFR
[5 empty] | 509 |  | PADDY FIELD, NALA
13 | AP-14 | DD+18 |  | 23°06'38"RT |  | 509 |  | MIRIGCHARA | 394505.516 | 2315910.124 | Open Cast | DFR
[5 empty] | 181 |  | 132KV SC OLD DUBURI - MISHRALAL PLANT
14 | AP-15 | DD+18 |  | 53°43'22"LT |  | 181 |  | ANKURAPALA | 394325.069 | 2315906.933 | Open Cast | DFR
[5 empty] | 349 |  | PADDY FIELD
15 | AP-16 | DD+0 |  | 48°32'26"LT |  | 349 |  | ANKURAPALA | 394124.525 | 2315623.319 | Open Cast | DFR
[5 empty] | 357 |  | PADDY FIELD
16 | 16/1 | DA+0 | [5 empty] | ANKURAPALA | 394206.396 | 2315276.336 | Open Cast | DFR
[5 empty] | 324 |  | PADDY FIELD
17 | 16/2 | DA+0 | [5 empty] | ANKURAPALA | 394280.718 | 2314961.346 | Open Cast | DFR
[5 empty] | 339 |  | PADDY FIELD , LOW LAND
18 | 16/3 | DA+0 | [5 empty] | ANKURAPALA | 394358.506 | 2314631.667 | Open Cast | DFR
[5 empty] | 352 |  | PADDY FIELD
19 | AP-17 | DD+0 |  | 56°17'27"LT |  | 1372 |  | ANKURAPALA | 394439.313 | 2314289.192 | Open Cast | WET
[5 empty] | 407 |  | PADDY FIELD, NALA
20 | AP-18 | DD+18 |  | 53°02'11"LT |  | 407 |  | ANKURAPALA | 394819.459 | 2314147.569 | Open Cast | PS
[5 empty] | 180 |  | 132KV SC OLD DUBURI-MISHRALAL LINE
21 | AP-19 | DD+18 |  | 54°39'15"RT |  | 180 |  | ANKURAPALA | 394970.809 | 2314244.375 | Open Cast | PS
[5 empty] | 419 |  | PADDY FIELD, 11KV LINE,33KV LINE,TAR ROAD
22 | AP-20 | DD+0 |  | 30°49'00"RT |  | 419 |  | GOLA GAON | 395358.273 | 2314087.432 | Open Cast | WET
[5 empty] | 433 |  | FENCING ,PADDY FIELD
23 | AP-21 | DC+6 |  | 20°31'24"RT |  | 433 |  | GOLA GAON | 395618.975 | 2313743.133 | Open Cast | WET
[5 empty] | 485 |  | PADDY FIELD, NALA
24 | AP-22 | DD+18 |  | 15°18'15"RT |  | 485 |  | NIMAPALI | 395757.182 | 2313279.805 | Open Cast | PS
[5 empty] | 164 |  | 132KV SC OLD DUBURI-MISHRALAL LINE , NALA
25 | AP-22A | DD+18 |  | 3°05'04"LT |  | 164 |  | NIMAPALI | 395760.9 | 2313116.6 | Open Cast | PS
[5 empty] | 185 |  | NALA, 400KV DC MERAMUNDALI -DUBURI LINE
26 | AP-23 | DD+25 |  | 44°55'58"LT |  | 185 |  | NIMAPALI | 395775.045 | 2312932.334 | Open Cast | PS
[5 empty] | 519 |  | PADDY FIELD
27 | AP-24 | DD+3 |  | 37°56'05"RT |  | 519 |  | NIMAPALI | 396151 | 2312577 | Open Cast | DFR
[5 empty] | 398 |  | GAIL GAS PIPE LINE
28 | AP-24A | DD+0 |  | 52°57'40"LT |  | 398 |  | NIMAPALI | 396211 | 2312184 | Open Cast | DFR
[5 empty] | 418 |  | PADDY FIELD,NALA, TAR ROAD
29 | AP-25 | DD+18 |  | 2°41'46"RT |  | 418 |  | NIMAPALI | 396578.43 | 2311985.67 | Open Cast | PS
[5 empty] | 199 |  | 220KV DC DUBURI- PARADEEP LINE
30 | AP-26 | DD+18 |  | 8°57'14"LT |  | 199 |  | NIMAPALI | 396748.139 | 2311883.478 | Open Cast | PS
[5 empty] | 445 |  | PADDY FIELD
31 | AP-27 | DD+9 |  | 19°19'18"LT |  | 445 |  | NIMAPALI | 397159.43 | 2311716.465 | Open Cast | PS
[5 empty] | 236 |  | NH-53 , 2NOS 33KV LINE
32 | AP-28 | DD+9 |  | 49°15'11"RT |  | 236 |  | NIMAPALI | 397394.634 | 2311705.049 | Open Cast | PS
[5 empty] | 430 |  | -
33 | 28/1 | DA+0 | [6 empty] | 397659.11 | 2311366.06 | Open Cast | PS
[5 empty] | 401 |  | NALA,FENCING
34 | 28/2 | DA+3 | [6 empty] | 397905.826 | 2311049.917 | Open Cast | PS
[5 empty] | 387 |  | FENCING,NALA,
35 | AP-29 | DC+0 |  | 16°33'27"LT |  | 1218 |  | PANKAPALA | 398142.99 | 2310746.072 | Open Cast | PS
[5 empty] | 399 |  | TAR ROAD , NALA
36 | AP-30 | DD+3 |  | 52°27'03"LT |  | 399 |  | NILAMANIDEI | 398467.008 | 2310515.17 | Open Cast | PS
[5 empty] | 399 |  | 2 NOS NALA
37 | AP-31 | DC+3 |  | 24°16'57"RT |  | 399 |  | MANOHARAPUR | 398847 | 2310631.175 | Open Cast | PS
[5 empty] | 394 |  | TAR ROAD , NALA
38 | AP-32 | DD+0 |  | 55°26'38"RT |  | 394 |  |  | 399237 | 2310581.174 | Open Cast | PS
[5 empty] | 300 |  | NALA
39 | AP-33 | DD+18 | 2 | 29°36'59"RT |  | 300 |  |  | 399374 | 2310315.174 | Pile | Brahmani River Bank
[5 empty] | 405 |  | BRAHMANI RIVER HFL-24.78
40 | 33/1 | DA+15 | 6 | [5 empty] | 399357.298 | 2309910.989 | Pile | Brahmani River Bed
[5 empty] | 397 |  | BRAHMANI RIVER
41 | 33/2 | DA+15 | 6 | [5 empty] | 399340.894 | 2309514.014 | Pile | Brahmani River Bed
[5 empty] | 423 |  | BRAHMANI RIVER
42 | 33/3 | DA+15 | 6 | [5 empty] | 399323.408 | 2309090.839 | Pile | Brahmani River Bed
[5 empty] | 470 |  | BRAHMANI RIVER , TAR ROAD, 11 KV LINE
43 | AP-34 | DD+18 | 4 | 14°22'54"LT |  | 1695 |  |  | 399304 | 2308621.174 | Pile | Brahmani River Bank
303
44 | AP-35 | DC+0 |  | 24°16'57"LT |  | 303 |  |  | 399367 | 2308325.174 | Open Cast | PS
[5 empty] | 403 |  | 11 KV LINE, FOOTPATH
45 | 35/1 | DA+6 | [6 empty] | 399609.573 | 2308003.928 | Open Cast | PS
[5 empty] | 397 |  | 11 KV LINE, TAR ROAD
46 | AP-36 | DB+0 |  | 9°25'21"LT |  | 800 |  | MARJITAPUR | 399848 | 2307688.173 | Open Cast | PS
[5 empty] | 399 |  | 11 KV LINE
47 | 36/1 | DA+9 | [6 empty] | 400136.822 | 2307413.891 | Open Cast | WET
405
48 | 36/2 | DA+0 | [6 empty] | 400430.25 | 2307135.234 | Open Cast | PS
400
49 | 36/3 | DA+3 | [6 empty] | 400720.04 | 2306860.032 | Open Cast | PS
400
50 | 36/4 | DA+3 | [6 empty] | 401009.854 | 2306584.807 | Open Cast | PS
399
51 | AP-37 | DB+0 |  | 0°00'00" |  | 2003 |  | MADHUSUDHANPUR | 401298.245 | 2306310.933 | Open Cast | WBC
383
52 | 37/1 | DA+0 | [6 empty] | 401575.487 | 2306047.647 | Open Cast | FS
[5 empty] | 408 |  | TAR ROAD
53 | 37/2 | DA+3 | [6 empty] | 401870.89 | 2305767.115 | Open Cast | WET
435
54 | 37/3 | DA+3 | [6 empty] | 402186.038 | 2305467.831 | Open Cast | WET
[5 empty] | 406 |  | TAR ROAD
55 | 37/4 | DA+3 | [6 empty] | 402479.983 | 2305188.683 | Open Cast | WET
[5 empty] | 398 |  | TAR ROAD
56 | AP-38 | DC+0 |  | 23°32'05"LT |  | 2030 |  | NACHHINDRAPUR | 402768.094 | 2304915.131 | Open Cast | PS
357
57 | AP-39 | DD+18 |  | 22°28'51"LT |  | 357 |  | NACHHINDRAPUR | 403102.639 | 2304793.512 | Open Cast | FS
[5 empty] | 291 |  | TRIPLE LANE RAILWAY LINE
58 | AP-40 | DD+18 |  | 39°31'49"RT |  | 291 |  | ARIMULA | 403393.291 | 2304806.175 | Open Cast | FS
341
59 | AP-41 | DD+0 |  | 47°18'49"RT |  | 341 |  | ARIMULA | 403665 | 2304601.163 | Open Cast | FS
[5 empty] | 409 |  | NALA
60 | 41/1 | DA+6 | [6 empty] | 403705.197 | 2304194.913 | Open Cast | PS
411
61 | 41/2 | DA+0 | [6 empty] | 403745.586 | 2303786.717 | Open Cast | WET
392
62 | 41/3 | DA+0 | [6 empty] | 403784.122 | 2303397.247 | Open Cast | WET
[5 empty] | 409 |  | CART TRACK
63 | 41/4 | DA+9 | [6 empty] | 403824.277 | 2302991.417 | Open Cast | WFR
[5 empty] | 383 |  | POND, 11 KV LINE, CART TRACK
64 | AP-42 | DB+0 |  | 0°00'00" |  | 2004 |  | KAMAGADA | 403861.929 | 2302610.882 | Open Cast | WET
[5 empty] | 402 |  | TAR ROAD
65 | 42/1 | DA+3 | [6 empty] | 403901.398 | 2302211.984 | Open Cast | WET
395
66 | 42/2 | DA+0 | [6 empty] | 403940.27 | 2301819.123 | Open Cast | WET
[5 empty] | 416 |  | CART TRACK, TAR ROAD, 11 KV LINE
67 | 42/3 | DA+6 | [6 empty] | 403981.205 | 2301405.405 | Open Cast | DFR
[5 empty] | 366 |  | POND
68 | 42/4 | DA+0 | [6 empty] | 404017.196 | 2301041.662 | Open Cast | WET
[5 empty] | 425 |  | TAR ROAD
69 | AP-43 | DD+3 |  | 31°02'36"RT |  | 2004 |  | THAKURA | 404059 | 2300619.162 | Open Cast | WET
[5 empty] | 387 |  | CART TRACK, 11 KV LINE
70 | 43/1 | DA+6 | [6 empty] | 403893.125 | 2300269.712 | Open Cast | PS
423
71 | AP-44 | DC+6 |  | 21°25'09"LT |  | 810 |  | RAGADIPASI | 403712.01 | 2299888.158 | Open Cast | PS
[5 empty] | 406 |  | 33 KV LINE, TAR ROAD
72 | 44/1 | DA+3 | [6 empty] | 403683.864 | 2299482.938 | Open Cast | WET
409
73 | AP-45 | DD+3 |  | 32°31'44"LT |  | 815 |  | JAMUJHARI | 403655.607 | 2299076.117 | Open Cast | WET
[5 empty] | 400 |  | TAR ROAD
74 | AP-46 | DC+0 |  | 17°00'23"LT |  | 400 |  | KULABENGIPATA | 403846.056 | 2298726.162 | Open Cast | PS
414
75 | 46/1 | DA+3 | [6 empty] | 404140.891 | 2298437.054 | Open Cast | PS
403
76 | 46/2 | DA+0 | [6 empty] | 404428.208 | 2298155.318 | Open Cast | PS
[5 empty] | 395 |  | NALA, CART TRACK
77 | AP-47 | DB+3 |  | 7°41'02"LT |  | 1212 |  | BHUBANA PUR | 404709.913 | 2297879.084 | Open Cast | WBC
[5 empty] | 353 |  | NALA
78 | 47/1 | DA+0 | [6 empty] | 404992.376 | 2297668.125 | Open Cast | FS
[5 empty] | 453 |  | NALA
79 | AP-48 | DD+25 | 2 | 37°11'13"RT |  | 806 |  | OSARA | 405354.79 | 2297397.456 | Open Cast | FS
[5 empty] | 189 |  | 400kV DC BARIPADA-MENDHASHAL T/L, POND, NALA
80 | AP-49 | DD+25 | 2 | 36°06'42"LT |  | 189 |  | NAKUA | 405407.071 | 2297215.832 | Open Cast | FS
[5 empty] | 436 |  | NALA
81 | 49/1 | DA+3 | [6 empty] | 405750.999 | 2296948.77 | Open Cast | PS
[5 empty] | 388 |  | POND ,CART TRACK
82 | AP-50 | DC+0 |  | 23°42'28"RT |  | 824 |  | TULAR | 406057.007 | 2296711.152 | Open Cast | WET
[5 empty] | 413 |  | -
83 | 50/1 | DA+6 | [6 empty] | 406253.632 | 2296348.452 | Open Cast | WET
[5 empty] | 425 |  | CART TRACK, TAR ROAD, 11 KV LINE
84 | AP-51 | DD+6 |  | 31°30'07"LT |  | 838 |  | PAKHARA | 406456 | 2295975.156 | Open Cast | WBC
[5 empty] | 432 |  | -
85 | 51/1 | DA+0 | [6 empty] | 406829.022 | 2295759.485 | Open Cast | PS
[5 empty] | 371 |  | -
86 | AP-52 | DC+0 |  | 24°24'55"LT |  | 803 |  | BAJABATI | 407149.955 | 2295573.93 | Open Cast | WFR
[5 empty] | 407 |  | TAR ROAD, POND
87 | 52/1 | DA+3 | [6 empty] | 407533.195 | 2295536.218 | Open Cast | WFR
[5 empty] | 372 |  | PUMP HOUSE,11 KV LINE, TAR ROAD
88 | 52/2 | DA+3 | [6 empty] | 407924.805 | 2295497.682 | Open Cast | WET
[5 empty] | 395 |  | CART TRACK
89 | 52/3 | DA+0 | [6 empty] | 408317.424 | 2295459.046 | Open Cast | WET
412
90 | 52/4 | DA+3 | [6 empty] | 408726.867 | 2295418.756 | Open Cast | WET
[5 empty] | 418 |  | MURRUM ROAD, CANAL,11 KV LINE, TAR ROAD
91 | AP-53 | DD+3 |  | 30°17'34"RT |  | 2004 |  | ARJUN PUR | 409142.66 | 2295377.84 | Open Cast | WET
[5 empty] | 385 |  | DRAIN (2)
92 | 53/1 | DA+0 | [6 empty] | 409453.939 | 2295152.405 | Open Cast | WET
[5 empty] | 367 |  | TAR ROAD , CANAL
93 | 53/2 | DA+0 | [6 empty] | 409750.935 | 2294937.315 | Open Cast | WET
[5 empty] | 326 |  | 11 KV LINE
94 | 53/3 | DA+6 | [6 empty] | 410014.942 | 2294746.116 | Open Cast | WET
[5 empty] | 347 |  | DRAIN,TAR ROAD, NALA
95 | AP-54 | DD+18 |  | 19°22'40"LT |  | 1425 |  | BRAHMANANDA | 410295.39 | 2294543.01 | Open Cast | PS
[5 empty] | 161 |  | 132kV JAJPUR ROAD-KENDRAPARA LINE
96 | AP-55 | DD+18 |  | 13°39'13"RT |  | 161 |  | BRAHMANANDA | 410448.92 | 2294497.43 | Open Cast | PS
[5 empty] | 445 |  | NALA, POND,CC ROAD
97 | AP-56 | DB+0 |  | 10°09'27"LT |  | 445 |  | RATHIA | 410832.99 | 2294273.996 | Open Cast | PS
[5 empty] | 439 |  | DRAIN
98 | AP-57 | DD+9 |  | 4°15'35"RT |  | 439 |  | RATHIA | 411244.007 | 2294124.143 | Open Cast | PS
[5 empty] | 237 |  | NATIONAL HIGHWAY 16,33 KV LINE,
99 | AP-58 | DD+9 |  | 21°19'41"RT |  | 237 |  | RATHIA | 411460.192 | 2294026.572 | Open Cast | PS
[5 empty] | 432 |  | DRAIN
100 | 58/1 | DA+0 | [6 empty] | 411762.097 | 2293718.071 | Open Cast | WET
[5 empty] | 383 |  | DRAIN
101 | 58/2 | DA+0 | [6 empty] | 412030.023 | 2293444.29 | Open Cast | WET
[5 empty] | 393 |  | -
102 | 58/3 | DA+3 | [6 empty] | 412304.048 | 2293164.277 | Open Cast | WET
[5 empty] | 410 |  | DRAIN
103 | AP-59 | DB+0 |  | 00°00'00" |  | 1618 |  | SENDHAPUR | 412590.683 | 2292871.38 | Open Cast | WET
[5 empty] | 415 |  | PADDY FIELD, 2 NOS NALA
104 | 59/1 | DA+3 | [6 empty] | 412876.904 | 2292578.187 | Open Cast | WET
[5 empty] | 389 |  | 2 NOS NALA , MORRUM ROAD
105 | 59/2 | DA+0 | [6 empty] | 413148.634 | 2292299.847 | Open Cast | PS
[5 empty] | 364 |  | LT LINE
106 | 59/3 | DA+6 | [6 empty] | 413402.933 | 2292039.363 | Open Cast | WET
[5 empty] | 432 |  | LT LINE , TRANSFORMER, NALA, DEAD 11KV LINE
107 | AP-60 | DB+3 |  | 0°00'00" |  | 1600 |  |  | 413704.895 | 2291730.056 | Open Cast | PS
[5 empty] | 402 |  | 2 NOS CART TRACK, TAR ROAD
108 | 60/1 | DA+3 | [6 empty] | 413985.797 | 2291442.279 | Open Cast | PS
[5 empty] | 373 |  | LT LINE ,PADDY FIELD
109 | 60/2 | DA+3 | [6 empty] | 414246.288 | 2291175.413 | Open Cast | PS
[5 empty] | 417 |  | PADDY FIELD
110 | 60/3 | DA+3 | [6 empty] | 414537.573 | 2290877 | Open Cast | WET
[5 empty] | 410 |  | PADDY FIELD
111 | 60/4 | DA+3 | [6 empty] | 414823.393 | 2290584.184 | Open Cast | WET
[5 empty] | 390 |  | PADDY FIELD, NALA
112 | AP-61 | DC+0 |  | 21°23'10"LT |  | 1992 |  |  | 415094.87 | 2290306.064 | Open Cast | PS
[5 empty] | 400 |  | PADDY FIELD, NALA, CC ROAD
113 | AP-62 | DB+3 |  | 13°24'13"RT |  | 400 |  |  | 415457.913 | 2290142.095 | Open Cast | PS
[5 empty] | 409 |  | PADDY FIELD
114 | 62/1 | DA+3 | [6 empty] | 415781.624 | 2289891.812 | Open Cast | PS
[5 empty] | 397 |  | CART TRACK
115 | 62/2 | DA+3 | [6 empty] | 416095.903 | 2289648.822 | Open Cast | PS
[5 empty] | 384 |  | PADDY FIELD
116 | 62/3 | DA+0 | [6 empty] | 416399.61 | 2289414.005 | Open Cast | PS
[5 empty] | 396 |  | PADDY FIELD
117 | 62/4 | DA+3 | [6 empty] | 416712.904 | 2289171.776 | Open Cast | PS
[5 empty] | 410 |  | PADDY FIELD, NALA , CC ROAD
118 | 62/5 | DA+3 | [6 empty] | 417037.376 | 2288920.905 | Open Cast | WET
[5 empty] | 404 |  | PADDY FIELD
119 | AP-63 | DB+0 |  | -0°00'00" |  | 2400 |  |  | 417356.592 | 2288674.097 | Open Cast | FS
[5 empty] | 386 |  | PADDY FIELD, NALA
120 | 63/1 | DA+0 | [6 empty] | 417661.938 | 2288438.013 | Open Cast | FS
[5 empty] | 395 |  | PADDY FIELD
121 | 63/2 | DA+3 | [6 empty] | 417974.386 | 2288196.439 | Open Cast | FS
[5 empty] | 392 |  | PADDY FIELD
122 | 63/3 | DA+0 | [6 empty] | 418284.639 | 2287956.562 | Open Cast | PS
[5 empty] | 385 |  | PADDY FIELD
123 | 63/4 | DA+3 | [6 empty] | 418589.247 | 2287721.048 | Open Cast | WET
[5 empty] | 421 |  | PADDY FIELD
124 | 63/5 | DA+3 | [6 empty] | 418921.416 | 2287464.227 | Open Cast | PS
[5 empty] | 421 |  | PADDY FIELD
125 | AP-64 | DC+0 |  | 20°31'20"LT |  | 2400 |  |  | 419253.959 | 2287207.115 | Open Cast | PS
[5 empty] | 396 |  | 11KV LINE,TAR ROAD,PADDY FIELD
126 | 64/1 | DA+3 | [6 empty] | 419631.915 | 2287090.207 | Pile | Clay
[5 empty] | 379 |  | PADDY FIELD
127 | 64/2 | DA+0 | [6 empty] | 419994.352 | 2286978.099 | Pile | Clay
[5 empty] | 297 |  | PADDY FIELD
128 | 64/3 | DA+3 | [6 empty] | 420277.792 | 2286890.427 | Pile | Clay
[5 empty] | 296 |  | CART TRACK, 3NOS 11KV LINE
129 | 64/4 | DA+0 | [6 empty] | 420560.398 | 2286803.012 | Pile | Clay
[5 empty] | 381 |  | PADDY FIELD
130 | 64/5 | DA+3 | [6 empty] | 420923.883 | 2286690.58 | Pile | Clay
[5 empty] | 380 |  | PADDY FIELD
131 | 64/6 | DA+3 | [6 empty] | 421285.986 | 2286578.576 | Pile | Clay
[5 empty] | 388 |  | 11KV LINE,CART TRACK, NALA
132 | AP-65 | DC+0 |  | 18°39'23"RT |  | 2517 |  |  | 421655.989 | 2286464.128 | Pile | Clay
[5 empty] | 417 |  | PADDY FIELD
133 | 65/1 | DA+3 | [6 empty] | 421992.878 | 2286220.761 | Pile | Clay + Sand
[5 empty] | 367 |  | PADDY FIELD, TAR ROAD
134 | AP-66 | DB+3 |  | 7°36'17"LT |  | 784 |  |  | 422289.996 | 2286006.124 | Pile | Clay + Sand
[5 empty] | 421 |  | PADDY FIELD
135 | 66/1 | DA+6 | [6 empty] | 422660.583 | 2285807.088 | Pile | Clay + Sand
[5 empty] | 422 |  | PADDY FIELD
136 | 66/2 | DA+3 | [6 empty] | 423032.355 | 2285607.415 | Pile | Clay + Sand
[5 empty] | 418 |  | PADDY FIELD , FOOT PATH, 11KV LINE, POND
137 | 66/3 | DA+3 | [6 empty] | 423399.622 | 2285410.162 | Pile | Clay + Sand
[5 empty] | 416 |  | PADDY FIELD , CART TRACK,NALA
138 | AP-67 | DC+3 |  | 15°26'47"LT |  | 1677 |  |  | 423764.95 | 2285213.95 | Pile | Clay
[5 empty] | 415 |  | PADDY FIELD
139 | AP-68 | DD+3 |  | 51°48'11"LT |  | 415 |  |  | 424169.08 | 2285122.185 | Pile | Clay
[5 empty] | 420 |  | PADDY FIELD , NALA
140 | AP-69 | DD+6 |  | 35°07'41"LT |  | 420 |  |  | 424494.94 | 2285386.155 | Pile | Clay
[5 empty] | 430 |  | CART TRACK , KIMIRIA NADI , TAR ROAD
141 | AP-70 | DD+9 |  | 0°00'51"RT |  | 430 |  |  | 424612.475 | 2285799.809 | Pile | Clay
[5 empty] | 397 |  | CULTIVATED LAND, 11KV LINE
142 | AP-71 | DD+3 |  | 44°51'09"RT |  | 397 |  |  | 424738.018 | 2286168.174 | Pile | Clay
[5 empty] | 415 |  | PADDY FIELD
143 | 71/1 | DA+3 | [6 empty] | 425082.798 | 2286383.959 | Pile | Clay
[5 empty] | 396 |  | PADDY FIELD
144 | 71/2 | DA+0 | [6 empty] | 425427.585 | 2286577.22 | Pile | Clay
[5 empty] | 393 |  | PADDY FIELD,FOOT PATH
145 | AP-72 | DB+3 |  | 8°28'45"RT |  | 1204 |  |  | 425769.972 | 2286769.135 | Pile | Clay
[5 empty] | 392 |  | MORRUM ROAD,TAR ROAD ,PADDY FIELD
146 | AP-73 | DD+3 |  | 40°39'38"RT |  | 392 |  |  | 426135.985 | 2286908.115 | Pile | Clay
[5 empty] | 380 |  | PADDY FIELD
147 | 73/1 | DA+0 | [6 empty] | 426492.902 | 2286779.137 | Pile | Clay + Sand
[5 empty] | 398 |  | PADDY FIELD
148 | 73/2 | DA+3 | [6 empty] | 426867.245 | 2286643.862 | Pile | Clay + Sand
[5 empty] | 444 |  | PADDY FIELD ,NALA,11KV LINE
149 | 73/3 | DA+3 | [6 empty] | 427284.961 | 2286492.914 | Pile | Clay + Sand
[5 empty] | 389 |  | PADDY FIELD
150 | 73/4 | DA+0 | [6 empty] | 427651.418 | 2286360.489 | Pile | Clay + Sand
[5 empty] | 289 |  | PADDY FIELD,FOOT PATH
151 | AP-74 | DB+0 |  | -0°00'00" |  | 1900 |  |  | 427922.892 | 2286262.387 | Pile | Clay + Sand
[5 empty] | 387 |  | PADDY FIELD
152 | 74/1 | DA+0 | [6 empty] | 428286.547 | 2286130.975 | Pile | Clay + Sand
[5 empty] | 344 |  | PADDY FIELD,11KV LINE
153 | 74/2 | DA+0 | [6 empty] | 428609.519 | 2286014.264 | Pile | Clay + Sand
[5 empty] | 389 |  | PADDY FIELD
154 | 74/3 | DA+0 | [6 empty] | 428974.359 | 2285882.423 | Pile | Clay + Sand
[5 empty] | 391 |  | PADDY FIELD , NALA
155 | 74/4 | DA+3 | [6 empty] | 429341.869 | 2285749.617 | Pile | Clay + Sand
[5 empty] | 376 |  | POND, TAR ROAD , 11 KV LINE
156 | AP-75 | DC+0 |  | 22°09'53"RT |  | 1887 |  |  | 429695.135 | 2285621.914 | Pile | Clay + Sand
[5 empty] | 386 |  | PADDY FIELD
157 | 75/1 | DA+3 | [6 empty] | 429981.946 | 2285363.371 | Pile | Clay + Sand
[5 empty] | 401 |  | PADDY FIELD
158 | 75/2 | DA+0 | [6 empty] | 430279.134 | 2285095.473 | Pile | Clay + Sand
[5 empty] | 371 |  | PADDY FIELD
159 | 75/3 | DA+0 | [6 empty] | 430554.112 | 2284847.597 | Pile | Clay + Sand
[5 empty] | 394 |  | PADDY FIELD , CART TRACK
160 | 75/4 | DA+3 | [6 empty] | 430846.114 | 2284584.375 | Pile | Clay + Sand
[5 empty] | 419 |  | PADDY FIELD
161 | 75/5 | DA+3 | [6 empty] | 431157.32 | 2284303.841 | Pile | Clay + Sand
[5 empty] | 409 |  | NALA,PADDY FIELD
162 | AP-76 | DB+0 |  | 8°48'23"LT |  | 2380 |  |  | 431460.988 | 2284030.102 | Pile | Clay + Sand
[5 empty] | 380 |  | PADDY FIELD
163 | 76/1 | DA+3 | [6 empty] | 431709.046 | 2283742.236 | Pile | Clay + Sand
[5 empty] | 380 |  | TAR ROAD,NALA,11KV LINE
164 | 76/2 | DA+3 |  |  |  |  | . |  | 431957.105 | 2283454.371 | Pile | Clay + Sand
[5 empty] | 380 |  | 11KV LINE, FOOTPATH
165 | 76/3 | DA+0 | [6 empty] | 432205.165 | 2283166.505 | Pile | Clay + Sand
[5 empty] | 380 |  | PADDY FIELD
166 | 76/4 | DA+3 | [6 empty] | 432453.224 | 2282878.639 | Pile | Clay + Sand
[5 empty] | 380 |  | FOOTPATH
167 | 76/5 | DA+0 | [6 empty] | 432701.283 | 2282590.774 | Pile | Clay + Sand
380
168 | AP-77 | DB+0 |  | 0°00'00" |  | 2280 |  |  | 432949.517 | 2282302.705 | Pile | Clay + Sand
[5 empty] | 380 |  | PADDY FIELD
169 | 77/1 | DA+0 | [6 empty] | 433197.577 | 2282014.838 | Pile | Clay + Sand
380
170 | 77/2 | DA+0 | [6 empty] | 433445.636 | 2281726.972 | Pile | Clay + Sand
[5 empty] | 380 |  | PADDY FIELD
171 | 77/3 | DA+0 | [6 empty] | 433693.695 | 2281439.106 | Pile | Clay + Sand
380
172 | 77/4 | DA+0 | [6 empty] | 433941.754 | 2281151.24 | Pile | Clay + Sand
[5 empty] | 380 |  | PADDY FIELD
173 | 77/5 | DA+0 | [6 empty] | 434189.813 | 2280863.374 | Pile | Clay + Sand
381
174 | AP-78 | DB+0 |  | 3°21'55"RT |  | 2281 |  |  | 434438.311 | 2280574.983 | Pile | Clay
[5 empty] | 386 |  | PADDY FIELD
175 | 78/1 | DA+3 | [6 empty] | 434672.748 | 2280268.207 | Pile | Clay
388
176 | 78/2 | DA+3 | [6 empty] | 434908.551 | 2279959.643 | Pile | Clay
[5 empty] | 390 |  | PADDY FIELD
177 | 78/3 | DA+0 | [6 empty] | 435145.063 | 2279650.151 | Pile | Clay
[5 empty] | 400 |  | NALA
178 | 78/4 | DA+3 | [6 empty] | 435387.99 | 2279332.265 | Pile | Clay
[5 empty] | 330 |  | MURRAM ROAD
179 | AP-79 | DB+0 |  | 2°23'03"LT |  | 1894 |  |  | 435588.195 | 2279070.284 | Pile | Clay
[5 empty] | 402 |  | 11KV LINE
180 | AP-80 | DD+18 | 3 | 0°00'00" |  | 402 |  |  | 435845.235 | 2278761.458 | Pile | BIRUPA RIVER
[5 empty] | 465 |  | BIRUPA RIVER
181 | AP-81 | DD+18 | 3 | 0°00'00" |  | 465 |  |  | 436142.624 | 2278404.157 | Pile | BIRUPA RIVER
[5 empty] | 224 |  | NALA
182 | AP-82 | DD+6 | 2 |  |  | 224 |  |  | 436285.851 | 2278232.074 | Pile | BIRUPA RIVER
67926
[11 empty] | Open Cast | 120
[11 empty] | Pile | 62

## 400_Welding
Transrail Lighting Limited
Bolt Nut Calculation for Tack Welding (400 kV)
|  |  | Qty in Sets | 97 | 51 | 46 | 8 | 5 | 20 | 14 | 6 | 0 | 1 | 14 | 12 | 2 | 2 | 51 | 43 | 8 | 5 | 7 | 16 | 8 | Total Requirement
Sl. No. | Item Description | Size | Unit Weight (Kgs) | TOWERS
|  |  |  | DA |  |  |  |  | DB |  |  |  |  | DC |  |  |  | DD
|  |  |  | Basic Body | +0MBE | +3MBE | +6MBE | +9MBE | Basic Body | +0MBE | +3MBE | +6MBE | +9MBE | Basic Body | +0MBE | +3MBE | +6MBE | Basic Body | +0MBE | +3MBE | +6MBE | +9MBE | +18MBE | +25MBE
1 | 16 dia Bolts | 16X35 | 0.119 | 686 | 232 | 288 | 288 | 336 | 455 | 256 | 184 | 300 | 372 | 420 | 272 | 344 | 352 | 1479 | 344 | 436 | 420 | 512 | 828 | 892 | 240079
2 |  | 16X40 | 0.126 | 869 | 148 | 220 | 186 | 282 | 1104 | 204 | 352 | 360 | 404 | 1098 | 180 | 220 | 264 | 1156 | 152 | 260 | 324 | 256 | 656 | 580 | 236931
3 |  | 16X45 | 0.134 | 1018 | 144 | 192 | 282 | 334 | 990 | 160 | 328 | 138 | 202 | 909 | 72 | 216 | 160 | 1516 | 205 | 256 | 231 | 492 | 1064 | 896 | 274370
4 |  | 16X50 | 0.142 | 460 | 24 | 32 | 38 | 72 | 527 | 48 | 72 | 116 | 108 | 646 | 88 | 188 | 164 | 510 | 128 | 152 | 106 | 108 | 600 | 836 | 120840
5 |  | 16X55 | 0.15 | 416 | 182 | 186 | 102 | 148 | 214 |  |  | 4 | 4 | 430 | 56 | 36 | 16 | 398 | 104 | 176 | 88 | 184 | 324 | 340 | 106636
6 |  | 16X60 | 0.158 | 28 | 2 | 2 | 10 | 16 | 526 |  |  | 32 | 32 | 374 |  |  |  | 100 |  | 8 |  | 8 | 160 | 396 | 29806
7 |  | 16X65 | 0.164 | [5 empty] | 114 | 180 | 182 | 88 | 182 | 56 |  |  | 32 | 162 | 8 |  | 8 |  | 8 | 8 | 15760
8 |  | 16X70 | 0.173 |  |  |  |  | 28 | 2 | 44 | 42 | 32 | 34 | 362 |  |  |  | 26 |  | 24 |  | 16 | 16 |  | 8036
9 |  | 16X75 | 0.18 | [10 empty] | 6 | 242 | 220 | 128 | 40 | 24 |  | 24 |  | 24 | 48 | 7644
10 |  | 16X80 | 0.185 | [11 empty] | 14 | 12 | 8 | [7 empty] | 208
11 |  | 16X85 | 0.193 | [21 empty] | 0
12 | 24 dia Bolts | 24X60 | 0.416 | [14 empty] | 45 | [6 empty] | 2295
13 |  | 24X65 | 0.434 | [14 empty] | 63 | [6 empty] | 3213
14 |  | 24X70 | 0.452 | [14 empty] | 66 | [6 empty] | 3366
15 |  | 24X80 | 0.488 | [14 empty] | 233 | [6 empty] | 11883
16 |  | 24X85 | 0.506 | [14 empty] | 86 | 149 | 148 | 72 | 147 | 75 |  | 14566
17 |  | 24X90 | 0.524 | [14 empty] | 3 | 11 | 12 | 14 | 19 | 225 | 349 | 7317
18 |  | 24X95 | 0.541 | [19 empty] | 18 | 24 | 480
19 |  | 24X100 | 0.56 | [19 empty] | 8 | 27 | 344
20 |  | 24X105 | 0.575 | [21 empty] | 0
1083774

## 220_FDN Type
TRANSRAIL LIGHTING LIMITED
220KV D/C PRATAPSASAN TO ERSAMA TRANSMISSION LINE (Wine Zone - 6)
Check Survey Tower Schedule of Section - ( AP03 TO ERSAMA GANTRY ) TOTAL 61.177 KM
Sl. No | Loc. No. | Tower of Type | Deviation Angle (DMS) | Span (m) | Section Length (m) | GPS Co-ordinate |  | Elevation (m) | Major Crossings / Remarks (With in ROW) | VILLAGE NAME | Foundation Type | Tentative Soil Classification
[6 empty] | Latitude | Longitude
1 | AP-3 | OC+0 | 4°01'23 LT" |  |  | 20°11'40.417" | 85°52'33.74" | 24.634 | EXISTING LOC, OF NUAPADA-PRATAPSASAN LINE | PRATAPSASAN
|  |  |  | 221 |  |  |  |  | TAR ROAD,CART TRACK,FENCING,HOUSE,LT LINE
2 | AP-4 | OB+3 | 3°19'50"LT |  | 221 | 20°11'36.54" | 85°52'40.17" | 24.977 | 2 MTR RC | PRATAPSASAN | Pile | Sandy
|  |  |  | 283 |  |  |  |  | TAR ROAD,CART TRACK,HUT,LT LINE
3 | AP-5 | OB+6 | 16°40'15"LT |  | 283 | 20°11'32.04" | 85°52'48.68" | 24.148 | 2 MTR RC | CHADHEIBAR | Pile | Sandy
|  |  |  | 322 |  |  |  |  | CART TRACK,CANAL,11KV LINE
4 | AP-5A | OC+3 | 32°53'48"LT |  | 322 | 20°11'29.76" | 85°52'59.51" | 22.518 |  | CHADHEIBAR | Pile
|  |  |  | 300 |  |  |  |  | CART TRACK,LT LINE
5 | AP-6 | OC+3 | 31°27'37"RT |  | 300 | 20°11'33.15" | 85°53'9.2" | 22.307 |  | BAYAN PADA | Pile | Sandy
|  |  |  | 362 |  |  |  |  | POND
6 | 6/1 | OA+3 |  |  |  | 20°11'31.08" | 85°53'21.47" | 21.471 |  | BAYAN PADA | Open Cast | FS
|  |  |  | 307 |  |  |  |  | CANAL
7 | 6/2 | OA+0 |  |  |  | 20°11'29.32" | 85°53'31.87" | 21.303 |  | BAYAN PADA | Open Cast | FS
278
8 | AP-7 | OC+0 | 31°56'43"LT |  | 947 | 20°11'27.73" | 85°53'41.29" | 21.119 |  | SINGIRI SASAN | Pile
|  |  |  | 287 |  |  |  |  | 11KV LINE,CANAL,BOUNDARY
9 | 7/1 | OA+6 |  |  |  | 20°11'31.2" | 85°53'50.47" | 20.667 |  | BAYAN PADA | Open Cast | FS
|  |  |  | 293 |  |  |  |  | TAR ROAD,LT LINE,MINI STADIUM,CANAL,WATER LOGGING AREA
10 | AP-8 | OC+3 | 41°27'12"RT |  | 580 | 20°11'34.74" | 85°53'59.84" | 21.355 |  | BISUNIA PADA | Pile
275
11 | 8/1 | OA+0 |  |  |  | 20°11'31.73" | 85°54'8.76" | 21.132 |  | BISUNIA PADA | Open Cast | FS
275
12 | 8/2 | OA+0 |  |  |  | 20°11'28.72" | 85°54'17.68" | 20.985 |  | BISUNIA PADA | Open Cast | FS
275
13 | 8/3 | OA+0 |  |  |  | 20°11'25.71" | 85°54'26.61" | 20.86 |  | BISUNIA PADA | Open Cast | FS
275
14 | 8/4 | OA+0 |  |  |  | 20°11'22.71" | 85°54'35.53" | 20.738 |  | BISUNIA PADA | Open Cast | FS
275
15 | 8/5 | OA+0 |  |  |  | 20°11'19.7" | 85°54'44.45" | 20.235 |  | BODHA KHANDI | Open Cast | FS
275
16 | 8/6 | OA+0 |  |  |  | 20°11'16.69" | 85°54'53.37" | 19.548 |  | BODHA KHANDI | Open Cast | FS
|  |  |  | 275 |  |  |  |  | LOW LAND
17 | 8/7 | OA+3 |  |  |  | 20°11'13.68" | 85°55'2.29" | 19.226 |  | BODHA KHANDI | Open Cast | FS
|  |  |  | 262 |  |  |  |  | 11KV LINE,TAR ROAD,CANAL
18 | AP-9 | OB+3 | 3°45'12"RT |  | 2187 | 20°11'10.82" | 85°55'10.79" | 19.705 |  | BODHA KHANDI | Pile
|  |  |  | 264 |  |  |  |  | 11KV LINE,LT LINE,PUMP HOUSE
19 | 9/1 | OA+6 |  |  |  | 20°11'7.4" | 85°55'19.15" | 19.681 |  | BODHA KHANDI | Open Cast | FS
|  |  |  | 316 |  |  |  |  | CC ROAD,11KV LINE
20 | 9/2 | OA+3 |  |  |  | 20°11'3.32" | 85°55'29.14" | 19.247 |  | BODHA KHANDI | Open Cast | FS
|  |  |  | 328 |  |  |  |  | DHANUA RIVER,LT LINE
21 | 9/3 | OA+3 |  |  |  | 20°10'59.07" | 85°55'39.52" | 19.619 |  | BODHA KHANDI | Open Cast | FS
337
22 | AP-10 | OB+0 | 6°25'03"LT |  | 1245 | 20°10'54.71" | 85°55'50.19" | 18.912 |  | NUAPADA | Pile
|  |  |  | 238 |  |  |  |  | WATER PIPE LINE
23 | 10/1 | OA+0 |  |  |  | 20°10'52.45" | 85°55'58.03" | 19.102 |  | NUAPADA | Open Cast | FS
|  |  |  | 251 |  |  |  |  | CART TRACK,LT LINE
24 | 10/2 | OA+0 |  |  |  | 20°10'50.07" | 85°56'6.28" | 19.186 |  | NUAPADA | Open Cast | FS
266
25 | 10/3 | OA+0 |  |  |  | 20°10'47.54" | 85°56'15.04" | 18.932 |  | NUAPADA | Open Cast | FS
|  |  |  | 283 |  |  |  |  | 11KV LINE
26 | AP-11 | OB+6 | 16°18'41"RT |  | 1038 | 20°10'44.85" | 85°56'24.35" | 19.122 |  | PAMPALO | Pile
|  |  |  | 299 |  |  |  |  | NALA,POND,11KV LINE,CANAL,TAR ROAD,LT LINE
27 | AP-12 | OC+0 | 40°48'43"LT |  | 299 | 20°10'39.5" | 85°56'32.97" | 18.929 |  | PAMPALO | Pile
|  |  |  | 330 |  |  |  |  | CC ROAD,LT LINE
28 | 12/1 | OA+6 |  |  |  | 20°10'40.91" | 85°56'44.24" | 18.734 |  | PAMPALO | Open Cast | FS
|  |  |  | 324 |  |  |  |  | CC ROAD,11KV LINE,TAR ROAD,CANAL
29 | 12/2 | OA+3 |  |  |  | 20°10'42.28" | 85°56'55.31" | 18.814 |  | SARAT | Open Cast | FS
256
30 | AP-13 | OB+0 | 7°28'35"LT |  | 910 | 20°10'43.36" | 85°57'4.02" | 18.863 |  | SARAT | Pile
272
31 | 13/1 | OA+3 |  |  |  | 20°10'45.65" | 85°57'13.07" | 18.684 |  | SARAT | Open Cast | FS
|  |  |  | 295 |  |  |  |  | CANAL,DRAIN
32 | 13/2 | OA+3 |  |  |  | 20°10'48.13" | 85°57'22.89" | 18.782 |  | SARAT | Open Cast | FS
|  |  |  | 289 |  |  |  |  | DRAIN
33 | 13/3 | OA+3 |  |  |  | 20°10'50.56" | 85°57'32.51" | 18.883 |  | SARAT | Open Cast | FS
|  |  |  | 280 |  |  |  |  | 11KV LINE,TAR ROAD,BOUNDRY
34 | 13/4 | OA+3 |  |  |  | 20°10'52.91" | 85°57'41.8" | 19.341 |  | SARAT | Open Cast | FS
303
35 | 13/5 | OA+0 |  |  |  | 20°10'55.45" | 85°57'51.87" | 19.32 |  | SARAT | Open Cast | FS
288
36 | AP-14 | OB+0 | 26°05'59"RT |  | 1727 | 20°10'57.87" | 85°58'1.46" | 19.322 |  | SARAT | Pile
|  |  |  | 233 |  |  |  |  | TAR ROAD,CANAL,POND
37 | AP-15 | OB+0 | 19°05'21"LT |  | 233 | 20°10'56.41" | 85°58'9.33" | 19.771 |  | ATHANTARA | Pile
|  |  |  | 290 |  |  |  |  | POND
38 | AP-16 | OC+0 | 46°42'05"LT |  | 290 | 20°10'57.71" | 85°58'19.21" | 19.598 |  | ATHANTARA | Pile
|  |  |  | 216 |  |  |  |  | 11KV LINE,CANAL,TAR ROAD,LT LINE,WATER LOGGING AREA
39 | AP-17 | OC+0 | 3°33'21"LT |  | 216 | 20°11'3.43" | 85°58'23.51" | 19.528 |  | ATHANTARA | Pile
|  |  |  | 187 |  |  |  |  | WATER LOGGING AREA
40 | 17/1 | OA+3 |  |  |  | 20°11'8.59" | 85°58'26.9" | 19.742 |  | ATHANTARA | Open Cast | FS
|  |  |  | 191 |  |  |  |  | WATER LOGGING AREA
41 | AP-18 | OB+0 | 20°03'25"RT |  | 378 | 20°11'13.88" | 85°58'30.37" | 19.901 |  | ATHANTARA | Pile
|  |  |  | 292 |  |  |  |  | TEMPLE,CART TRACK,11KV LINE,NALA,RIVER BUND,LOW LAND AREA
42 | AP-19 | OC+6 | 0°34'15"LT |  | 292 | 20°11'19.75" | 85°58'38.28" | 22.541 |  | ATHANTARA | Pile
|  |  |  | 399 |  |  |  |  | KUSABHADRA RIVER,RIVER BUND,CANAL,11KV LINE,TAR ROAD
43 | AP-20 | OC+6 | 7°42'36"RT |  | 399 | 20°11'27.87" | 85°58'49" | 18.034 |  | MAHUKHANDA | Pile
|  |  |  | 289 |  |  |  |  | POND,FOOTPATH
44 | 20/1 | OA+0 |  |  |  | 20°11'32.71" | 85°58'57.53" | 18.403 |  | MAHUKHANDA | Open Cast | FS
228
45 | 20/2 | OA+0 |  |  |  | 20°11'36.53" | 85°59'4.26" | 18.415 |  | MAHUKHANDA | Open Cast | FS
216
46 | AP-21 | OB+0 | 19°54'47"RT |  | 733 | 20°11'40.15" | 85°59'10.64" | 18.498 |  | MAHUKHANDA | Pile
|  |  |  | 297 |  |  |  |  | NALA
47 | 21/1 | OA+0 |  |  |  | 20°11'42.01" | 85°59'20.69" | 18.453 |  | UPAR SAHI | Open Cast | FS
|  |  |  | 290 |  |  |  |  | CART TRACK
48 | 21/2 | OA+0 |  |  |  | 20°11'43.83" | 85°59'30.48" | 18.781 |  | PRATAP RUDRA PUR | Open Cast | FS
|  |  |  | 305 |  |  |  |  | NALA
49 | 21/3 | OA+0 |  |  |  | 20°11'45.74" | 85°59'40.8" | 18.544 |  | PRATAP RUDRA PUR | Open Cast | FS
288
50 | 21/4 | OA+0 |  |  |  | 20°11'47.54" | 85°59'50.52" | 18.517 |  | PRATAP RUDRA PUR | Open Cast | FS
|  |  |  | 250 |  |  |  |  | LT LINE,CART TRACK,CANAL
51 | AP-22 | OB+0 | 18°59'22"RT |  | 1430 | 20°11'49.11" | 85°59'58.99" | 18.921 |  | PRATAP RUDRA PUR | Pile
|  |  |  | 236 |  |  |  |  | LT LINE,CART TRACK,CANAL
52 | 22/1 | OA+3 |  |  |  | 20°11'48.05" | 86°0'7.05" | 19.397 |  | PRATAP RUDRA PUR | Open Cast | PS
|  |  |  | 244 |  |  |  |  | 11KV LINE,TAR ROAD
53 | AP-23 | OB+0 | 11°56'11"RT |  | 480 | 20°11'46.96" | 86°0'15.37" | 19.931 |  | PRATAP RUDRA PUR | Open Cast | FS
|  |  |  | 310 |  |  |  |  | 11KV LINE,NALA,TAR ROAD,LT LINE
54 | AP-24 | OB+0 | 21°17'56"RT |  | 310 | 20°11'43.54" | 86°0'25.42" | 19.939 |  | PRATAP RUDRA PUR | Open Cast | FS
280
55 | 24/1 | OA+0 |  |  |  | 20°11'37.54" | 86°0'32.7" | 19.816 |  | PRATAP RUDRA PUR | Open Cast | PS
301
56 | 24/2 | OA+3 |  |  |  | 20°11'31.1" | 86°0'40.51" | 19.402 |  | PRATAP RUDRA PUR | Open Cast | FS
|  |  |  | 254 |  |  |  |  | CART TRACK,11KV LINE
57 | 24/3 | OA+3 |  |  |  | 20°11'25.66" | 86°0'47.1" | 19.104 |  | BHAKAR SAHI | Open Cast | FS
278
58 | 24/4 | OA+0 |  |  |  | 20°11'19.72" | 86°0'54.3" | 18.701 |  | BHAKAR SAHI | Open Cast | FS
257
59 | AP-25 | OC+0 | 40°39'30"RT |  | 1370 | 20°11'14.23" | 86°1'0.96" | 18.439 |  | BHAKAR SAHI | Pile
|  |  |  | 296 |  |  |  |  | LT LINE
60 | 25/1 | OA+0 |  |  |  | 20°11'4.7" | 86°1'2.42" | 18.115 |  | BHAKAR SAHI | Open Cast | FS
|  |  |  | 265 |  |  |  |  | LT LINE
61 | AP-26 | OB+0 | 20°02'21"RT |  | 561 | 20°10'56.17" | 86°1'3.72" | 18.156 |  | BHAKAR SAHI | Pile
|  |  |  | 271 |  |  |  |  | CART TRACK,LT LINE
62 | 26/1 | OA+0 |  |  |  | 20°10'47.55" | 86°1'1.81" | 18.765 |  | BHAKAR SAHI | Open Cast | FS
252
63 | 26/2 | OA+0 |  |  |  | 20°10'39.52" | 86°1'0.03" | 19.055 |  | BHAPUR | Open Cast | FS
|  |  |  | 245 |  |  |  |  | CANAL,NALA
64 | 26/3 | OA+0 |  |  |  | 20°10'31.72" | 86°0'58.3" | 19.003 |  | BHAPUR | Open Cast | FS
|  |  |  | 248 |  |  |  |  | 11KV LINE
65 | AP-27 | OB+3 | 18°02'03"LT |  | 1016 | 20°10'23.82" | 86°0'56.55" | 19.516 |  | BHAPUR | Pile
|  |  |  | 299 |  |  |  |  | 11KV LINE,TAR ROAD,NALA
66 | 27/1 | OA+6 |  |  |  | 20°10'14.14" | 86°0'57.66" | 19.266 |  | BHAPUR | Open Cast | FS
|  |  |  | 208 |  |  |  |  | 11KV LINE
67 | AP-28 | OC+3 | 44°14'14"LT |  | 507 | 20°10'7.41" | 86°0'58.43" | 18.956 |  | BHAPUR | Pile
|  |  |  | 279 |  |  |  |  | CC ROAD,11KV LINE,POND
68 | 28/1 | OA+0 |  |  |  | 20°10'1.62" | 86°1'5.85" | 19.137 |  | BHAPUR | Open Cast | FS
|  |  |  | 247 |  |  |  |  | DRAIN
69 | 28/2 | OA+0 |  |  |  | 20°9'56.51" | 86°1'12.41" | 18.888 |  | BHAPUR | Open Cast | FS
|  |  |  | 263 |  |  |  |  | DRAIN
70 | 28/3 | OA+0 |  |  |  | 20°9'51.05" | 86°1'19.41" | 18.659 |  | BHAPUR | Open Cast | FS
|  |  |  | 275 |  |  |  |  | BORE WELL
71 | AP-29 | OB+0 | 7°22'36"LT |  | 1064 | 20°9'45.36" | 86°1'26.7" | 18.45 |  | BHANRA NIGADA | Open Cast | PS
|  |  |  | 252 |  |  |  |  | TAR ROAD,CANAL,11KV LINE,LT LINE
72 | 29/1 | OA+3 |  |  |  | 20°9'40.99" | 86°1'34.06" | 18.243 |  | AMANA KUDA | Open Cast | PS
256
73 | AP-30 | OB+0 | 13°14'59"LT |  | 508 | 20°9'36.56" | 86°1'41.51" | 18.15 |  | AMANA KUDA | Open Cast | FS
|  |  |  | 359 |  |  |  |  | NALA
74 | 30/1 | OA+3 |  |  |  | 20°9'32.77" | 86°1'53.2" | 18.334 |  | AMANA KUDA | Open Cast | FS
|  |  |  | 245 |  |  |  |  | 11KV LINE
75 | 30/2 | OA+0 |  |  |  | 20°9'30.18" | 86°2'1.17" | 18.513 |  | AMANA KUDA | Open Cast | FS
|  |  |  | 330 |  |  |  |  | NALA
76 | AP-31 | OB+0 | 21°52'40"LT |  | 934 | 20°9'26.7" | 86°2'11.92" | 18.65 |  | AMANA KUDA | Open Cast | WBC
|  |  |  | 256 |  |  |  |  | TAR ROAD,CANAL
77 | 31/1 | OA+0 |  |  |  | 20°9'27.13" | 86°2'20.74" | 18.339 |  | AMANA KUDA | Open Cast | PS
242
78 | 31/2 | OA+0 |  |  |  | 20°9'27.53" | 86°2'29.06" | 18.261 |  | KHULISO | Open Cast | FS
|  |  |  | 230 |  |  |  |  | DRAIN,11KV LINE
79 | AP-32 | OB+3 | 28°07'06"LT |  | 728 | 20°9'27.91" | 86°2'36.96" | 17.52 |  | KHULISO | Pile | Sandy Clay
|  |  |  | 204 |  |  |  |  | TAR ROAD,LT LINE
80 | AP-33 | OC+3 | 45°26'43"RT |  | 204 | 20°9'31.33" | 86°2'42.96" | 17.09 |  | KHULISO | Pile
|  |  |  | 283 |  |  |  |  | 33KV LINE
81 | AP-34 | OB+0 | 21°51'03"RT |  | 283 | 20°9'29.04" | 86°2'52.42" | 17.65 |  | SBARNA PUR | Pile
240
82 | 34/1 | OA+0 |  |  |  | 20°9'24.42" | 86°2'59.09" | 17.689 |  | SBARNA PUR | Open Cast | PS
262
83 | 34/2 | OA+0 |  |  |  | 20°9'19.41" | 86°3'6.33" | 17.577 |  | NUAGAON | Open Cast | PS
280
84 | 34/3 | OA+0 |  |  |  | 20°9'14.02" | 86°3'14.11" | 17.711 |  | NUAGAON | Open Cast | FS
274
85 | 34/4 | OA+0 |  |  |  | 20°9'8.76" | 86°3'21.71" | 17.545 |  | BADA KAR KAR | Open Cast | FS
300
86 | 34/5 | OA+3 |  |  |  | 20°9'2.99" | 86°3'30.04" | 17.554 |  | BADA KAR KAR | Pile
|  |  |  | 224 |  |  |  |  | TAR ROAD,11KV LINE
87 | AP-35 | OB+0 | 3°30'50"LT |  | 1580 | 20°8'58.7" | 86°3'36.24" | 18.14 |  | BADA KAR KAR | Pile
|  |  |  | 302 |  |  |  |  | PUMP HOUSE
88 | 35/1 | OA+0 |  |  |  | 20°8'53.39" | 86°3'44.98" | 18.171 |  | MAJHI KHANDA | Pile
300
89 | 35/2 | OA+3 |  |  |  | 20°8'48.14" | 86°3'53.63" | 17.929 |  | MAJHI KHANDA | Open Cast | PS
|  |  |  | 271 |  |  |  |  | 11KV LINE,TAR ROAD
90 | 35/3 | OA+0 |  |  |  | 20°8'43.37" | 86°4'1.49" | 17.543 |  | NIALI | Open Cast | PS
311
91 | 35/4 | OA+0 |  |  |  | 20°8'37.89" | 86°4'10.5" | 17.316 |  | NIALI | Pile
298
92 | 35/5 | OA+0 |  |  |  | 20°8'32.66" | 86°4'19.12" | 17.111 |  | NIALI | Open Cast | WET
288
93 | 35/6 | OA+0 |  |  |  | 20°8'27.58" | 86°4'27.48" | 17.123 |  | PUBA KHANDA | Open Cast | WET
|  |  |  | 280 |  |  |  |  | 11KV LINE,LT LINE,TAR ROAD
94 | AP-36 | OB+3 | 14°16'22"LT |  | 2050 | 20°8'22.68" | 86°4'35.56" | 16.98 |  | PUBA KHANDA | Pile
|  |  |  | 269 |  |  |  |  | LT LINE
95 | 36/1 | OA+0 |  |  |  | 20°8'19.9" | 86°4'44.36" | 16.829 |  | WAUPALI | Pile
250
96 | 36/2 | OA+0 |  |  |  | 20°8'17.33" | 86°4'52.51" | 16.949 |  | WAUPALI | Pile
|  |  |  | 239 |  |  |  |  | NALA
97 | 36/3 | OA+0 |  |  |  | 20°8'14.86" | 86°5'0.33" | 17.138 |  | WAUPALI | Open Cast | WET
281
98 | 36/4 | OA+0 |  |  |  | 20°8'11.97" | 86°5'9.49" | 17.112 |  | WAUPALI | Open Cast | PS
|  |  |  | 247 |  |  |  |  | NALA
99 | AP-37 | OB+0 | 18°13'12"LT |  | 1286 | 20°8'9.43" | 86°5'17.55" | 17.21 |  | WAUPALI | Pile
287
100 | 37/1 | OA+0 |  |  |  | 20°8'9.39" | 86°5'27.45" | 17.089 |  | WAUPALI | Pile
|  |  |  | 233 |  |  |  |  | LT LINE,FOOTPATH
101 | 37/2 | OA+0 |  |  |  | 20°8'9.35" | 86°5'35.48" | 17.29 |  | BAHARANA | Pile
264
102 | 37/3 | OA+0 |  |  |  | 20°8'9.32" | 86°5'44.56" | 17.484 |  | BAHARANA | Open Cast | PS
|  |  |  | 231 |  |  |  |  | TAR ROAD,HOUSE
103 | AP-38 | OB+0 | 10°31'37"RT |  | 1015 | 20°8'9.28" | 86°5'52.51" | 17.72 |  | BAHARANA | Pile
|  |  |  | 304 |  |  |  |  | TAR ROAD,CANAL,HOUSE,BOUNDRY
104 | 38/1 | OA+0 |  |  |  | 20°8'7.44" | 86°6'2.78" | 17.885 |  | BARIMUNDEI | Pile
323
105 | 38/2 | OA+0 |  |  |  | 20°8'5.47" | 86°6'13.7" | 18.024 |  | BARIMUNDEI | Pile
311
106 | 38/3 | OA+0 |  |  |  | 20°8'3.58" | 86°6'24.23" | 18.066 |  | ATHANTARA | Pile
331
107 | 38/4 | OA+3 |  |  |  | 20°8'1.56" | 86°6'35.43" | 18.148 |  | ATHANTARA | Pile
|  |  |  | 295 |  |  |  |  | LT LINE,TAR ROAD
108 | AP-39 | OC+6 | 3°21'21"RT |  | 1564 | 20°7'59.76" | 86°6'45.41" | 18.52 |  | ATHANTARA | Pile | Sandy
|  |  |  | 325 |  |  |  |  | HEMSAGAR RIVER,TAR ROAD,CANAL,11KV LINE
109 | AP-40 | OC+6 | 22°11'32"LT |  | 325 | 20°7'57.18" | 86°6'56.26" | 18.55 |  | PODANA | Pile
361
110 | 40/1 | OA+0 |  |  |  | 20°7'58.83" | 86°7'8.58" | 18.279 |  | PODANA | Pile
|  |  |  | 301 |  |  |  |  | FOOTPATH
111 | 40/2 | OA+0 |  |  |  | 20°8'0.2" | 86°7'18.86" | 18.304 |  | BADARO | Pile
|  |  |  | 281 |  |  |  |  | MURRAM ROAD,CANAL,DRAIN
112 | 40/3 | OA+0 |  |  |  | 20°8'1.48" | 86°7'28.45" | 18.258 |  | BADARO | Pile
|  |  |  | 327 |  |  |  |  | 11KV LINE,TAR ROAD
113 | AP-41 | OB+0 | 8°35'45"RT |  | 1270 | 20°8'2.97" | 86°7'39.6" | 18.21 |  | KAPASI | Pile
|  |  |  | 339 |  |  |  |  | 11KV LINE,TAR ROAD
114 | 41/1 | OA+0 |  |  |  | 20°8'2.861" | 86°7'51.27" | 17.921 |  | KAPASI | Pile
330
115 | 41/2 | OA+3 |  |  |  | 20°8'2.76" | 86°8'2.63" | 17.919 |  | KAPASI | Pile
|  |  |  | 343 |  |  |  |  | BORE WELL,LT LINE
116 | 41/3 | OA+3 |  |  |  | 20°8'2.65" | 86°8'14.44" | 17.807 |  | TIHUDI | Pile
|  |  |  | 278 |  |  |  |  | NALA
117 | AP-42 | OB+0 | 6°26'50"RT |  | 1290 | 20°8'2.56" | 86°8'24.02" | 17.92 |  | TIHUDI | Pile
|  |  |  | 291 |  |  |  |  | NALA
118 | 42/1 | OA+0 |  |  |  | 20°8'1.41" | 86°8'33.96" | 17.885 |  | TIHUDI | Pile
227
119 | 42/2 | OA+0 |  |  |  | 20°8'0.51" | 86°8'41.71" | 17.824 |  | PARIMALA | Pile
|  |  |  | 264 |  |  |  |  | LOWLAND AREA,LT LINE,TAR ROAD
120 | 42/3 | OA+3 |  |  |  | 20°7'59.46" | 86°8'50.73" | 17.682 |  | PARIMALA | Pile
265
121 | AP-43 | OC+6 | 6°18'53"RT |  | 1047 | 20°7'58.41" | 86°8'59.8" | 17.613 |  | PARIMALA | Pile
|  |  |  | 342 |  |  |  |  | LOWLAND AREA,NALA,CART TRACK, DEVI RIVER
122 | 43/1 | OA+6 |  |  |  | 20°7'55.84" | 86°9'11.26" | 14.214 | 7 MTR RC | PARIMALA | Pile | River
|  |  |  | 315 |  |  |  |  | DEVI RIVER
123 | 43/2 | OA+6 |  |  |  | 20°7'53.48" | 86°9'21.81" | 14.924 | 7 MTR RC | PARIMALA | Pile | River
|  |  |  | 359 |  |  |  |  | DEVI RIVER,NALA,CART TRACK
124 | AP-44 | OC+6 | 7°41'26"LT |  | 1016 | 20°7'50.79" | 86°9'33.83" | 16.08 |  | POHALA | Pile
|  |  |  | 287 |  |  |  |  | NALA
125 | 44/1 | OA+0 |  |  |  | 20°7'49.88" | 86°9'43.66" | 15.775 |  | KORANIA | Pile
|  |  |  | 285 |  |  |  |  | TAR ROAD,LT LINE
126 | AP-45 | OC+0 | 38°25'41"LT |  | 572 | 20°7'48.97" | 86°9'53.44" | 15.712 |  | KORANIA | Pile
|  |  |  | 292 |  |  |  |  | DRAIN,TAR ROAD,11KV LINE,CANAL,LT LINE
127 | 45/1 | OA+6 |  |  |  | 20°7'54.1" | 86°10'1.88" | 15.517 |  | ROHIA | Pile
|  |  |  | 250 |  |  |  |  | 11KV LINE
128 | 45/2 | OA+6 |  |  |  | 20°7'58.52" | 86°10'9.13" | 15.373 |  | ROHIA | Pile
|  |  |  | 354 |  |  |  |  | DRAIN,11KV LINE,CANAL,TAR ROAD
129 | AP-46 | OB+0 | 29°26'24"LT |  | 896 | 20°8'4.74" | 86°10'19.36" | 15.485 |  | ROHIA | Pile
|  |  |  | 281 |  |  |  |  | TAR ROAD,CANAL,11KV LINE,33KV LINE
130 | 46/1 | OA+6 |  |  |  | 20°8'12.82" | 86°10'23.86" | 15.471 |  | ARAKHAKUDA | Pile
327
131 | 46/2 | OA+0 |  |  |  | 20°8'22.25" | 86°10'29.12" | 15.506 |  | GANDHAN | Pile
267
132 | 46/3 | OA+0 |  |  |  | 20°8'29.92" | 86°10'33.4" | 15.537 |  | GANDHAN | Pile
270
133 | 46/4 | OA+0 |  |  |  | 20°8'37.66" | 86°10'37.71" | 15.324 |  | GANDHAN | Pile
285
134 | 46/5 | OA+0 |  |  |  | 20°8'45.87" | 86°10'42.29" | 15.451 |  | GANDHAN | Pile
|  |  |  | 340 |  |  |  |  | DRAIN,11KV LINE
135 | AP-47 | OB+3 | 11°15'48"RT |  | 1770 | 20°8'55.65" | 86°10'47.75" | 16.145 |  | GANDHAN | Pile
|  |  |  | 271 |  |  |  |  | TAR ROAD,NALA
136 | AP-48 | OB+3 | 27°06'16"RT |  | 271 | 20°9'2.51" | 86°10'53.64" | 16.362 |  | GANDHAN | Pile
|  |  |  | 300 |  |  |  |  | CC ROAD,LT LINE,11KV LINE,NALA,TAR ROAD
137 | AP-49 | OB+3 | 6°11'21"LT |  | 300 | 20°9'6.45" | 86°11'3.09" | 15.796 |  | NAUGAON | Pile
|  |  |  | 317 |  |  |  |  | CANAL
138 | 49/1 | OA+0 |  |  |  | 20°9'11.61" | 86°11'12.53" | 15.593 |  | NAUGAON | Pile
285
139 | 49/2 | OA+0 |  |  |  | 20°9'16.26" | 86°11'21.04" | 15.478 |  | NAUGAON | Pile
296
140 | 49/3 | OA+0 |  |  |  | 20°9'21.08" | 86°11'29.86" | 15.325 |  | NAUGAON | Pile
281
141 | 49/4 | OA+0 |  |  |  | 20°9'25.65" | 86°11'38.23" | 15.269 |  | KHAERA BASTA | Pile
314
142 | AP-50 | OC+6 | 40°13'29"RT |  | 1493 | 20°9'30.76" | 86°11'47.59" | 15.221 |  | KHAERA BASTA | Pile
|  |  |  | 327 |  |  |  |  | TAR ROAD,CANAL,33KV LINE,11KV LINE,NALA
143 | 50/1 | OA+6 |  |  |  | 20°9'28.88" | 86°11'58.66" | 15.213 |  | MUNDALO | Pile
|  |  |  | 353 |  |  |  |  | DRAIN,11KV LINE,TAR ROAD
144 | AP-51 | OC+3 | 29°07'27"LT |  | 680 | 20°9'26.85" | 86°12'10.64" | 14.801 |  | MUNDALO | Pile | Clay
|  |  |  | 221 |  |  |  |  | LT LINE,TAR ROAD,POND
145 | AP-52 | OB+0 | 22°19'29"RT |  | 221 | 20°9'29.18" | 86°12'17.82" | 14.692 |  | MUNDALO | Pile
|  |  |  | 303 |  |  |  |  | POND
146 | 52/1 | OA+3 |  |  |  | 20°9'28.59" | 86°12'28.25" | 14.579 |  | MUNDALO | Pile
|  |  |  | 364 |  |  |  |  | DEAD LINE,DRAIN,CC ROAD
147 | 52/2 | OA+3 |  |  |  | 20°9'27.89" | 86°12'40.75" | 15.083 |  | KUNDHESWAR | Pile
|  |  |  | 304 |  |  |  |  | 11KV LINE,POND
148 | AP-53 | OC+0 | 57°23'31"LT |  | 971 | 20°9'27.31" | 86°12'51.21" | 14.814 |  | KUNDHESWAR | Pile
|  |  |  | 304 |  |  |  |  | POND,11KV LINE,TAR ROAD,FENCING, HAND PUMP
149 | 53/1 | OA+0 |  |  |  | 20°9'35.31" | 86°12'57.37" | 14.336 |  | MADHUPUR | Pile
|  |  |  | 306 |  |  |  |  | 11KV LINE,MORRUM ROAD,CANAL
150 | AP-54 | OB+3 | 7°36'28"RT |  | 610 | 20°9'43.37" | 86°13'3.57" | 14.213 |  | KUNDHESWAR | Pile
|  |  |  | 252 |  |  |  |  | CANAL,MURRUM ROAD,11KV LINE, ALAKA RIVER
151 | AP-55 | OC+3 | 40°06'20"LT |  | 252 | 20°9'49.32" | 86°13'9.57" | 13.981 |  | CHANR PUR | Pile
|  |  |  | 326 |  |  |  |  | 11KV LINE,FOOTPATH
152 | 55/1 | OA+6 |  |  |  | 20°9'59.9" | 86°13'10.25" | 13.236 |  | CHANR PUR | Pile
|  |  |  | 297 |  |  |  |  | 11KV LINE,CART TRACK,CANAL,NALA,TAR ROAD
153 | AP-56 | OB+3 | 9°06'30"RT |  | 623 | 20°10'9.55" | 86°13'10.88" | 12.991 |  | CHANR PUR | Pile
|  |  |  | 276 |  |  |  |  | TAR ROAD,NALA
154 | 56/1 | OA+0 |  |  |  | 20°10'18.3" | 86°13'12.95" | 12.889 |  | GARAMA | Pile
|  |  |  | 245 |  |  |  |  | DRAIN
155 | 56/2 | OA+0 |  |  |  | 20°10'26.08" | 86°13'14.79" | 12.641 |  | GARAMA | Pile
261
156 | 56/3 | OA+0 |  |  |  | 20°10'34.36" | 86°13'16.75" | 12.769 |  | GARAMA | Pile
264
157 | AP-57 | OC+0 | 58°16'38"RT |  | 1046 | 20°10'42.74" | 86°13'18.74" | 13.311 |  | GARAMA | Pile
276
158 | 57/1 | OA+0 |  |  |  | 20°10'45.68" | 86°13'27.74" | 12.544 |  | GARAMA | Pile
|  |  |  | 256 |  |  |  |  | NALA,CC ROAD,11KV LINE,FOOTPATH
159 | AP-58 | OB+0 | 12°23'26"LT |  | 532 | 20°10'48.41" | 86°13'36.08" | 13.678 |  | MALAPUR | Pile
|  |  |  | 291 |  |  |  |  | NALA,LOWLAND
160 | AP-59 | OB+0 | 29°14'34"LT |  | 291 | 20°10'53.36" | 86°13'44.63" | 12.876 |  | MALAPUR | Pile
|  |  |  | 279 |  |  |  |  | NALA
161 | 59/1 | OA+0 |  |  |  | 20°11'1.26" | 86°13'49.32" | 12.383 |  | GARAMA | Pile
283
162 | 59/2 | OA+0 |  |  |  | 20°11'9.3" | 86°13'54.09" | 12.4 |  | GARAMA | Pile
|  |  |  | 305 |  |  |  |  | DRAIN
163 | AP-60 | OC+0 | 28°15'25"RT |  | 867 | 20°11'17.95" | 86°13'59.22" | 12.221 |  | SADEIPUR | Pile
|  |  |  | 245 |  |  |  |  | PROPOSED NH
164 | AP-61 | OC+3 | 39°58'47"LT |  | 245 | 20°11'22.23" | 86°14'6.34" | 12.288 |  | SADEIPUR | Pile
|  |  |  | 254 |  |  |  |  | -
165 | 61/1 | OA+0 |  |  |  | 20°11'30.12" | 86°14'8.98" | 12.548 |  | SADEIPUR | Pile
|  |  |  | 243 |  |  |  |  | -
166 | 61/2 | OA+0 |  |  |  | 20°11'37.67" | 86°14'11.51" | 12.459 |  | SADEIPUR | Pile
|  |  |  | 204 |  |  |  |  | 11 KV LINE
167 | 61/3 | OA+0 |  |  |  | 20°11'44" | 86°14'13.63" | 12.546 |  | SADEIPUR | Pile
|  |  |  | 243 |  |  |  |  | 11KV,CC ROAD
168 | AP-62 | OB+3 | 25°00'09"RT |  | 944 | 20°11'51.5" | 86°14'16.14" | 12.992 |  | BENUPUR | Pile
|  |  |  | 290 |  |  |  |  | -
169 | 62/1 | OA+0 |  |  |  | 20°11'59.08" | 86°14'23.51" | 12.89 |  | BENUPUR | Pile
|  |  |  | 282 |  |  |  |  | -
170 | 62/2 | OA+0 |  |  |  | 20°12'6.53" | 86°14'30.75" | 12.847 |  | BENUPUR | Pile
|  |  |  | 325 |  |  |  |  | DRAIN
171 | AP-63 | OB+6 | 6°33'33"RT |  | 897 | 20°12'14.47" | 86°14'38.47" | 12.815 |  | BENUPUR | Pile | Sandy
|  |  |  | 344 |  |  |  |  | TAR RD, 11KV LINE
172 | AP-64 | OB+6 | 9°43'56"RT |  | 344 | 20°12'20.44" | 86°14'45.78" | 13.162 |  | SAHADA | Pile | Clay
|  |  |  | 280 |  |  |  |  | -
173 | 64/1 | OA+3 |  |  |  | 20°12'25.16" | 86°14'54.03" | 12.929 |  | SAHADA | Pile | Sandy
|  |  |  | 280 |  |  |  |  | DRAIN, CART TRACK
174 | 64/2 | OA+0 |  |  |  | 20°12'29.87" | 86°15'2.29" | 12.764 |  | SINGIRI | Pile | Clay
|  |  |  | 267 |  |  |  |  | -
175 | 64/3 | OA+0 |  |  |  | 20°12'34.37" | 86°15'10.17" | 12.637 |  | JALISO | Pile | Clay
|  |  |  | 293 |  |  |  |  | DRAIN
176 | 64/4 | OA+0 |  |  |  | 20°12'39.3" | 86°15'18.8" | 12.795 |  | JALISO | Pile
|  |  |  | 290 |  |  |  |  | POND,NALA
177 | 64/5 | OB+0 | 00°00'00" |  | 1410 | 20°12'44.17" | 86°15'27.33" | 12.216 |  | MULUGAN | Pile
|  |  |  | 271 |  |  |  |  | CANAL
178 | 64/6 | OA+0 |  |  |  | 20°12'48.72" | 86°15'35.31" | 12.11 |  | MULUGAN | Pile
280
179 | 64/7 | OA+0 |  |  |  | 20°12'53.44" | 86°15'43.57" | 11.843 |  | MULUGAN | Pile
279
180 | 64/8 | OA+0 |  |  |  | 20°12'58.13" | 86°15'51.79" | 11.742 |  | MULUGAN | Pile
|  |  |  | 268 |  |  |  |  | INDIAN OIL PIPE LINE
181 | 64/9 | OA+0 |  |  |  | 20°13'2.64" | 86°15'59.68" | 11.528 |  | MULUGAN | Pile
|  |  |  | 256 |  |  |  |  | CANAL
182 | AP-65 | OB+6 | 15°49'45"RT |  | 1354 | 20°13'6.95" | 86°16'7.24" | 11.352 |  | MULUGAN | Pile | Clay
|  |  |  | 280 |  |  |  |  | TAR ROAD,POND
183 | AP-66 | OB+0 | 26°23'31"RT |  | 280 | 20°13'9.36" | 86°16'16.56" | 10.962 |  | MULUGAN | Pile | Clay
|  |  |  | 230 |  |  |  |  | -
184 | 66/1 | OA+0 |  |  |  | 20°13'7.93" | 86°16'24.31" | 10.882 |  | MULUGAN | Pile
|  |  |  | 200 |  |  |  |  | CANAL
185 | 66/2 | OA+0 |  |  |  | 20°13'6.68" | 86°16'31.1" | 10.704 |  | MULUGAN | Pile
|  |  |  | 300 |  |  |  |  | INDIAN OIL PIPE LINE
186 | 66/3 | OA+0 |  |  |  | 20°13'4.8" | 86°16'41.25" | 10.229 |  | MULUGAN | Pile
|  |  |  | 300 |  |  |  |  | FOOTPATH
187 | 66/4 | OA+0 |  |  |  | 20°13'2.93" | 86°16'51.39" | 10.327 |  | MULUGAN | Pile
|  |  |  | 300 |  |  |  |  | NALA
188 | 66/5 | OA+0 |  |  |  | 20°13'1.06" | 86°17'1.54" | 10.556 |  | ASARANA | Pile
|  |  |  | 272 |  |  |  |  | FOOTPATH
189 | AP-67 | OB+0 | 0°00'00"RT |  | 1602 | 20°12'59.37" | 86°17'10.69" | 10.162 |  | SARANA | Pile
|  |  |  | 282 |  |  |  |  | FOOTPATH
190 | 67/1 | OA+0 |  |  |  | 20°12'57.61" | 86°17'20.23" | 9.935 |  | SARANA | Pile
|  |  |  | 245 |  |  |  |  | -
191 | 67/2 | OA+0 |  |  |  | 20°12'56.08" | 86°17'28.49" | 9.905 |  | SARANA | Pile
|  |  |  | 262 |  |  |  |  | NALA,CART TRACK
192 | 67/3 | OA+0 |  |  |  | 20°12'54.44" | 86°17'37.36" | 9.537 |  | SARANA | Pile
|  |  |  | 247 |  |  |  |  | -
193 | 67/4 | OA+0 |  |  |  | 20°12'52.9" | 86°17'45.71" | 9.273 |  | SARANA | Pile
|  |  |  | 237 |  |  |  |  | NALA
194 | 67/5 | OA+0 |  |  |  | 20°12'51.41" | 86°17'53.74" | 9.285 |  | DIGODA | Pile
|  |  |  | 270 |  |  |  |  | TAR ROAD
195 | AP-68 | OB+3 | 4°50'53"LT |  | 1543 | 20°12'49.72" | 86°18'2.88" | 9.461 |  | DIGODA | Pile | Clay
|  |  |  | 292 |  |  |  |  | CANAL,LT LINE
196 | 68/1 | OA+3 |  |  |  | 20°12'48.69" | 86°18'12.9" | 9.444 |  | RANKEI | Pile
|  |  |  | 320 |  |  |  |  | -
197 | 68/2 | OA+0 |  |  |  | 20°12'47.56" | 86°18'23.86" | 9.322 |  | RANKEI | Pile
|  |  |  | 282 |  |  |  |  | POND
198 | 68/3 | OA+0 |  |  |  | 20°12'46.56" | 86°18'33.53" | 9.13 |  | RANKEI | Pile
|  |  |  | 292 |  |  |  |  | NALA
199 | 68/4 | OA+0 |  |  |  | 20°12'45.53" | 86°18'43.53" | 9.016 |  | POLO | Pile
|  |  |  | 239 |  |  |  |  | POND,CART TRACK
200 | 68/5 | OA+0 |  |  |  | 20°12'44.7" | 86°18'51.65" | 9.049 |  | ARADEI | Pile
|  |  |  | 265 |  |  |  |  | CART TRACK
201 | AP-69 | OB+0 | 12°04'35"RT |  | 1690 | 20°12'43.76" | 86°19'0.73" | 9.111 |  | ARADEI | Pile
|  |  |  | 300 |  |  |  |  | -
202 | 69/1 | OA+3 |  |  |  | 20°12'40.69" | 86°19'10.55" | 9.311 |  | ARADEI | Pile
|  |  |  | 261 |  |  |  |  | 11KV LINE
203 | 69/2 | OA+0 |  |  |  | 20°12'38.03" | 86°19'19.09" | 9.541 |  | ARADEI | Pile
|  |  |  | 219 |  |  |  |  | TAR ROAD
204 | 69/3 | OA+0 |  |  |  | 20°12'35.79" | 86°19'26.23" | 9.567 |  | NAULA | Pile
|  |  |  | 282 |  |  |  |  | -
205 | AP-70 | OB+0 | 12°36'08"RT |  | 1062 | 20°12'32.91" | 86°19'35.47" | 9.365 |  | NAULA | Pile | Clay
|  |  |  | 238 |  |  |  |  | NALA,CART TRACK,11KV LINE
206 | 70/1 | OA+0 |  |  |  | 20°12'28.93" | 86°19'42.5" | 9.584 |  | NAULA | Pile
|  |  |  | 221 |  |  |  |  | 11KV LINE
207 | 70/2 | OA+0 |  |  |  | 20°12'25.23" | 86°19'49.04" | 9.639 |  | NAULA | Pile
|  |  |  | 304 |  |  |  |  | -
208 | AP-71 | OB+0 | 29°24'07"LT |  | 763 | 20°12'20.15" | 86°19'58.04" | 9.689 |  | TULANGA | Pile | Clay
|  |  |  | 279 |  |  |  |  | -
209 | 71/1 | OA+0 |  |  |  | 20°12'19.91" | 86°20'7.63" | 9.821 |  | TULANGA | Pile
|  |  |  | 284 |  |  |  |  | -
210 | 71/2 | OA+0 |  |  |  | 20°12'19.66" | 86°20'17.41" | 9.596 |  | SHERPUR | Pile
|  |  |  | 284 |  |  |  |  | -
211 | 71/3 | OA+0 |  |  |  | 20°12'19.42" | 86°20'27.21" | 9.771 |  | SHERPUR | Pile
|  |  |  | 292 |  |  |  |  | DRAIN
212 | 71/4 | OA+0 |  |  |  | 20°12'19.16" | 86°20'37.26" | 9.649 |  | TULANGA | Pile
|  |  |  | 286 |  |  |  |  | NALA
213 | 71/5 | OA+0 |  |  |  | 20°12'18.92" | 86°20'47.12" | 9.562 |  | SANILO | Pile
|  |  |  | 256 |  |  |  |  | NALA
214 | 71/6 | OA+0 |  |  |  | 20°12'18.7" | 86°20'55.95" | 9.537 |  | SANILO | Pile
|  |  |  | 286 |  |  |  |  | POND,11KV LINE,TAR ROAD
215 | AP-72 | OB+3 | 15°47'03"LT |  | 1967 | 20°12'18.45" | 86°21'5.79" | 9.552 |  | SANILO | Pile
|  |  |  | 288 |  |  |  |  | -
216 | 72/1 | OA+0 |  |  |  | 20°12'20.75" | 86°21'15.39" | 9.561 |  | IBRISING | Pile
|  |  |  | 278 |  |  |  |  | -
217 | 72/2 | OA+0 |  |  |  | 20°12'22.98" | 86°21'24.68" | 9.477 |  | IBRISING | Pile
|  |  |  | 280 |  |  |  |  | -
218 | AP-73 | OB+0 | 6°37'48"LT |  | 846 | 20°12'25.22" | 86°21'34.02" | 9.347 |  | JABEDHUAN | Pile
|  |  |  | 244 |  |  |  |  | LOW LAND,TAR ROAD
219 | AP-74 | OC+0 | 43°16'49"LT |  | 244 | 20°12'28.05" | 86°21'41.86" | 9.233 |  | JABEDHUAN | Pile
|  |  |  | 100 |  |  |  |  | -
220 | AP-75 | OC+0 | 0°59'50"RT |  | 100 | 20°12'30.98" | 86°21'43.37" | 9.272 |  | JABEDHUAN | Pile
53
221 | GANTRY | GANTRY |  |  | 53 | 20°12'32.51" | 86°21'44.19" | 9.261 |  | JABEDHUAN
TOTAL LENGTH = 61.177 KM
[11 empty] | Open Cast | 64 | 29.22%
[11 empty] | Pile | 155 | 70.78%
219
[11 empty] | All Balance | FS

## 220_Welding
Transrail Lighting Limited
Bolt Nut Calculation for Tack Welding (400 kV)
|  |  | Qty in Sets | 142 | 26 | 11 | 48 | 13 | 5 | 32 | 8 | 10 |  | Total Requirement
Sl. No. | Item Description | Size | Unit Weight (Kgs) | TOWERS | [8 empty] | Pipe Type Earthing
|  |  |  | OA |  |  | OB |  |  | OC
|  |  |  | Normal Tower | +3MBE | +6MBE | Normal Tower | +3MBE | +6MBE | Normal Tower | +3MBE | +6MBE
1 | 16 dia Bolts | 16X35 | 0.119 | 690 | 76 | 208 | 492 | 132 | 184 | 771 | 144 | 232 |  | 156640
2 |  | 16X40 | 0.126 | 518 | 92 | 196 | 676 | 116 | 156 | 775 | 180 | 204 |  | 141120
3 |  | 16X45 | 0.134 | 343 | 48 | 128 | 630 | 144 | 292 | 864 | 232 | 324 |  | 117678
4 |  | 16X50 | 0.142 | 230 | 4 | 68 | 273 |  | 16 | 386 | 4 | 44 |  | 59520
5 |  | 16X55 | 0.15 | 148 | 80 |  | 402 | 96 | 96 | 520 | 88 | 76 |  | 62224
6 |  | 16X60 | 0.158 | 36 | 16 | 24 | 4 | 8 | 8 | 46 | 24 | 24 |  | 8032
7 |  | 16X65 | 0.164 | 4 |  |  | 36 | 16 | 24 | 6 |  |  |  | 2816
8 |  | 16X70 | 0.173 |  |  |  | 4 |  |  | 2 |  |  |  | 256
9 |  | 16X75 | 0.18 | [10 empty] | 0
10 |  | 16X80 | 0.185 | [10 empty] | 0
11 |  | 16X85 | 0.193 | [10 empty] | 0
12 | 24 dia Bolts | 24X60 | 0.416 | [10 empty] | 0
13 |  | 24X65 | 0.434 | [10 empty] | 0
14 |  | 24X70 | 0.452 | [10 empty] | 0
15 |  | 24X80 | 0.488 | [10 empty] | 0
16 |  | 24X85 | 0.506 | [10 empty] | 0
17 |  | 24X90 | 0.524 | [10 empty] | 0
18 |  | 24X95 | 0.541 | [10 empty] | 0
19 |  | 24X100 | 0.56 | [10 empty] | 0
20 |  | 24X105 | 0.575 | [10 empty] | 0
548286

## new weight chat 220KV
TRANSRAIL LIGHTING LIMITED
TOWER & BOLT NUT WEIGHTS
G-487: | 220kV D/C line from Ersama, Paradeep to Pratapsasan Transmission Line
Type of Tower | Structure | Qty (Sets) | Unit Weight (Kg)
|  |  | HT | MS | Tower Parts | Bolt Nut | Total | Total weight | N&B weight
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=6+7 | 9=6*3 | 10=7*3
OA | Stub | 142 | 331.24 |  | 331.24 | 10.52 | 341.76 | 47.0361 | 1.4938
OB | Stub | 48 | 429.4 |  | 429.4 | 10.81 | 440.21 | 20.6112 | 0.51888
OC | Stub | 29 | 507.48 |  | 507.48 | 10.81 | 518.29 | 14.7169 | 0.31349
OA | Template | 15 |  | 1135.04 | 1135.04 | 34.27 | 1169.31 | 17.0256 | 0.51405
OB | Template | 5 |  | 1446.28 | 1446.28 | 41.926 | 1488.206 | 7.2314 | 0.20963
OC | Template | 5 |  | 2190.92 | 2190.92 | 63.67 | 2254.59 | 10.9546 | 0.31835
| stub= | 219 | Templete= | 25 |  | Sub Total (MT) |  | 117.5758 | 3.3682
OA | Normal Tower | 142 | 2729.55 | 3819.38 | 6548.93 | 302.94 | 6851.87 | 929.9481 | 43.0175
| +3MBE | 26 | 448.96 | 741.25 | 1190.21 | 47.99 | 1238.2 | 30.9455 | 1.2477
| +6MBE | 11 | 777 | 1483.28 | 2260.28 | 91.28 | 2351.56 | 24.8631 | 1.0041
OB | Normal Tower | 48 | 4872.59 | 3846.96 | 8719.55 | 385.14 | 9104.69 | 418.5384 | 18.4867
| +3MBE | 13 | 670.16 | 1053.14 | 1723.3 | 74.76 | 1798.06 | 22.4029 | 0.97188
| +6MBE | 5 | 1026.68 | 1692.52 | 2719.2 | 114.4 | 2833.6 | 13.596 | 0.572
OC | Normal Tower | 29 | 6049.76 | 5582.89 | 11632.65 | 510.21 | 12142.86 | 337.3469 | 14.7961
| +3MBE | 8 | 734.56 | 2145.65 | 2880.21 | 97.14 | 2977.35 | 23.0417 | 0.77712
| +6MBE | 10 | 1238.64 | 2680.58 | 3919.22 | 132.29 | 4051.51 | 39.1922 | 1.3229
TOTAL Tower SUPPLY |  | 219 |  |  | Sub Total (MT) |  |  | 1839.8746 | 82.196
Total Stub, Template & Tower Supply |  |  |  |  | Grand Total (MT) |  |  | 1957.4504 | 85.5643
[5 empty] | LOA QTY (MT) |  |  | 1326.443 | 66.332
[5 empty] | Deviation wrt LOA |  |  | 47.57% | 28.99%
OA | Stub | 142 | 331.24 |  | 331.24 | 10.52 | 341.76 | 48.5299
OB | Stub | 48 | 429.4 |  | 429.4 | 10.81 | 440.21 | 21.1301
OC | Stub | 29 | 507.48 |  | 507.48 | 10.81 | 518.29 | 15.0304
OC | STUB | 3 |  |  | 330 |  | 330 | 0.99
OA | Template | 142 |  | 1135.04 | 1135.04 | 34.27 | 1169.31 | 166.042
OB | Template | 48 |  | 1446.28 | 1446.28 | 41.926 | 1488.206 | 71.4339
OC | Template | 29 |  | 2190.92 | 2190.92 | 63.67 | 2254.59 | 65.3831
OC | Template | 3 |  |  | 984 |  | 984 | 2.952
TOTAL STUB ERECTION |  | 222 | Templete | 222 | Sub Total (MT) |  |  | 391.4914
TOTAL STUB &TEMPLET SETTING FOR ERECTION |  |  |  |  | LOA QTY (MT) |  |  | 230.01
[5 empty] | Deviation wrt LOA |  |  | 70.21%
OA | Normal Tower | 142 | 2729.55 | 3819.38 | 6548.93 | 302.94 | 6851.87 | 929.9481 | 43.0175
| +3MBE | 26 | 448.96 | 741.25 | 1190.21 | 47.99 | 1238.2 | 30.9455 | 1.2477
| +6MBE | 11 | 777 | 1483.28 | 2260.28 | 91.28 | 2351.56 | 24.8631 | 1.0041
OB | Normal Tower | 48 | 4872.59 | 3846.96 | 8719.55 | 385.14 | 9104.69 | 418.5384 | 18.4867
| +3MBE | 13 | 670.16 | 1053.14 | 1723.3 | 74.76 | 1798.06 | 22.4029 | 0.97188
| +6MBE | 5 | 1026.68 | 1692.52 | 2719.2 | 114.4 | 2833.6 | 13.596 | 0.572
OC | Normal Tower | 29 | 6049.76 | 5582.89 | 11632.65 | 510.21 | 12142.86 | 337.3469 | 14.7961
| +3MBE | 8 | 734.56 | 2145.65 | 2880.21 | 97.14 | 2977.35 | 23.0417 | 0.77712
| +6MBE | 10 | 1238.64 | 2680.58 | 3919.22 | 132.29 | 4051.51 | 39.1922 | 1.3229
| Normal Tower | 3 |  |  | 9180 | 355 | 9535 | 27.54 | 1.065
TOTAL TOWER FOR ERECTION |  | 222
TOTAL TOWER ERECTION |  |  |  |  | Sub Total (MT) |  |  | 1867.4146 | 83.261
[5 empty] | LOA QTY (MT) |  |  | 1231.5 | 61.8
[5 empty] | Deviation wrt LOA |  |  | 51.64% | 34.73%

## New weight chat 400KV
TRANSRAIL LIGHTING LIMITED
TOWER & BOLT NUT WEIGHTS
G-487: | 400KV D/C line from Loc. No. 1 (dead end tower of 400/220 KV AIS S/S at New Duburi) to Loc no. 182
Type of Tower | Structure | Qty (Sets) | Unit Weight (Kg)
|  |  | HT | MS | Tower Parts | Bolt Nut | Total | Total weight(MT) | N&B weight(MT)
1 | 2 | 3 | 4 | 5 | 6=4+5 | 7 | 8=6+7 | 9=6*3 | 10=7*3
DA | Stub upto +9MBE | 97 | 564.16 |  | 564.16 | 13.55 | 577.71 | 54.7235 | 1.3144
DB | Stub upto +9MBE | 20 | 693 |  | 693 | 13.55 | 706.55 | 13.86 | 0.271
DC | Stub upto +9MBE | 14 | 844.08 |  | 844.08 | 17.97 | 862.05 | 11.8171 | 0.25158
DD | Stub upto +9MBE | 25 | 1231.84 |  | 1231.84 | 25.84 | 1257.68 | 30.796 | 0.646
DD | Stub for +12/+18/25MBE | 26 | 1298.56 |  | 1298.56 | 26.08 | 1324.64 | 33.7626 | 0.67808
DA | Template | 5 |  | 1860.45 | 1860.45 | 42.7 | 1903.15 | 9.3023 | 0.2135
DB | Template | 2 |  | 3066.76 | 3066.76 | 72.44 | 3139.2 | 6.1335 | 0.14488
DC | Template | 2 |  | 2349.89 | 2349.89 | 55.73 | 2405.62 | 4.6998 | 0.11146
DD | Template | 2 |  | 3738.52 | 3738.52 | 101.22 | 3839.74 | 7.477 | 0.20244
| Stub= | 182 | Templete= | 11 |  | Sub Total (MT) |  | 172.5718 | 3.8333
DA | Basic Body | 97 | 5396.88 | 6259.47 | 11656.35 | 525.74 | 12182.09 | 1130.666 | 50.9968
| +0MBE | 51 | 1035.4 | 1753.53 | 2788.93 | 108.04 | 2896.97 | 142.2354 | 5.51
| +3MBE | 46 | 1408.36 | 2592.95 | 4001.31 | 135.87 | 4137.18 | 184.0603 | 6.25
| +6MBE | 8 | 1195.68 | 2596.76 | 3792.44 | 131.54 | 3923.98 | 30.3395 | 1.0523
| +9MBE | 2 | 1783.48 | 3335.45 | 5118.93 | 179.6 | 5298.53 | 10.2379 | 0.3592
| +15MBE | 3 | 7449 | 4011 | 11460 | 540 | 12000 | 34.38 | 1.62
DB | Basic Body | 20 | 9194.23 | 6365.9 | 15560.13 | 605.17 | 16165.3 | 311.2026 | 12.1034
| +0MBE | 14 | 1645.64 | 2225.56 | 3871.2 | 135.19 | 4006.39 | 54.1968 | 1.8927
| +3MBE | 6 | 2037.6 | 3242.36 | 5279.96 | 176.21 | 5456.17 | 31.6798 | 1.0573
| +6MBE | 0 | 1940.96 | 3000.68 | 4941.64 | 157.26 | 5098.9 | 0 | 0
| +9MBE | 1 | 2784.64 | 3477.77 | 6262.41 | 199.99 | 6462.4 | 6.2624 | 0.19999
DC | Basic Body | 14 | 11498.63 | 5928.17 | 17426.8 | 671.47 | 18098.27 | 243.9752 | 9.4006
| +0MBE | 12 | 2049.48 | 2425.25 | 4474.73 | 146.05 | 4620.78 | 53.6968 | 1.7526
| +3MBE | 2 | 2621 | 3421.98 | 6042.98 | 191.24 | 6234.22 | 12.086 | 0.38248
| +6MBE | 2 | 1508.52 | 3985.52 | 5494.04 | 168.15 | 5662.19 | 10.9881 | 0.3363
| +9MBE | 0 | 2722.24 | 4346.33 | 7068.57 | 219.57 | 7288.14 | 0 | 0
DD | Basic Body | 51 | 13165.7 | 8021.65 | 21187.35 | 1042.58 | 22229.93 | 1080.5548 | 53.1716
| +0MBE | 43 | 2665.92 | 2905.27 | 5571.19 | 227.33 | 5798.52 | 239.5612 | 9.7752
| +3MBE | 8 | 4061.8 | 3248.6 | 7310.4 | 278.83 | 7589.23 | 58.4832 | 2.2306
| +6MBE | 5 | 2298.52 | 4052.81 | 6351.33 | 227.04 | 6578.37 | 31.7567 | 1.1352
| +9MBE | 5 | 3254.36 | 5539.69 | 8794.05 | 317.91 | 9111.96 | 43.9703 | 1.5896
| +12MBE | 2 | 4515.68 | 7278.35 | 11794.03 | 410.24 | 12204.27 | 23.5881 | 0.82048
| +18MBE | 16 | 6690.48 | 14689.72 | 21380.2 | 720.86 | 22101.06 | 342.0832 | 11.5338
| +25MBE | 8 | 9632.92 | 19846.99 | 29479.91 | 823.18 | 30303.09 | 235.8393 | 6.5854
TOTAL Tower SUPPLY |  | 182 |  |  | Sub Total (MT) |  |  | 4311.8432 | 179.7555
Total Stub, Template & Tower Supply |  |  |  |  | Grand Total (MT) |  |  | 4484.415 | 183.5888
[5 empty] | LOA QTY (MT) |  |  | 4446.7 | 178
[5 empty] | Deviation wrt LOA |  |  | 0.8482% | 3.14%
DA | Stub upto +9MBE | 97 | 564.16 |  | 564.16 | 13.55 | 577.71 | 54.7235 | 1.3144
DB | Stub upto +9MBE | 20 | 693 |  | 693 | 13.55 | 706.55 | 13.86 | 0.271
DC | Stub upto +9MBE | 14 | 844.08 |  | 844.08 | 17.97 | 862.05 | 11.8171 | 0.25158
DD | Stub upto +9MBE | 25 | 1231.84 |  | 1231.84 | 25.84 | 1257.68 | 30.796 | 0.646
DD | Stub for +12/+18/25MBE | 26 | 1298.56 |  | 1298.56 | 26.08 | 1324.64 | 33.7626 | 0.67808
DA | Template | 97 |  | 1860.45 | 1860.45 | 42.7 | 1903.15 | 180.4637 | 4.1419
DB | Template | 20 |  | 3066.76 | 3066.76 | 72.44 | 3139.2 | 61.3352 | 1.4488
DC | Template | 14 |  | 2349.89 | 2349.89 | 55.73 | 2405.62 | 32.8985 | 0.78022
DD | Template | 51 |  | 3738.52 | 3738.52 | 101.22 | 3839.74 | 190.6645 | 5.1622
| Stub= | 182 | Templete= | 182 |  | Sub Total (MT) |  | 610.321 | 14.6942
TOTAL STUB ERECTION |  | 162 | Templete | 267 | Sub Total (MT) |  |  | 625.0152
TOTAL STUB &TEMPLET SETTING FOR ERECTION |  |  |  |  | LOA QTY (MT) |  |  | 594
[5 empty] | Deviation wrt LOA |  |  | 5.221%
DA | Basic Body | 97 | 5396.88 | 6259.47 | 11656.35 | 525.74 | 12182.09 | 1130.666 | 50.9968
| +0MBE | 51 | 1035.4 | 1753.53 | 2788.93 | 108.04 | 2896.97 | 142.2354 | 5.51
| +3MBE | 46 | 1408.36 | 2592.95 | 4001.31 | 135.87 | 4137.18 | 184.0603 | 6.25
| +6MBE | 8 | 1195.68 | 2596.76 | 3792.44 | 131.54 | 3923.98 | 30.3395 | 1.0523
| +9MBE | 2 | 1783.48 | 3335.45 | 5118.93 | 179.6 | 5298.53 | 10.2379 | 0.3592
| +15MBE | 3 | 7449 | 4011 | 11460 | 540 | 12000 | 34.38 | 1.62
DB | Basic Body | 20 | 9194.23 | 6365.9 | 15560.13 | 605.17 | 16165.3 | 311.2026 | 12.1034
| +0MBE | 14 | 1645.64 | 2225.56 | 3871.2 | 135.19 | 4006.39 | 54.1968 | 1.8927
| +3MBE | 6 | 2037.6 | 3242.36 | 5279.96 | 176.21 | 5456.17 | 31.6798 | 1.0573
| +6MBE | 0 | 1940.96 | 3000.68 | 4941.64 | 157.26 | 5098.9 | 0 | 0
| +9MBE | 1 | 2784.64 | 3477.77 | 6262.41 | 199.99 | 6462.4 | 6.2624 | 0.19999
DC | Basic Body | 14 | 11498.63 | 5928.17 | 17426.8 | 671.47 | 18098.27 | 243.9752 | 9.4006
| +0MBE | 12 | 2049.48 | 2425.25 | 4474.73 | 146.05 | 4620.78 | 53.6968 | 1.7526
| +3MBE | 2 | 2621 | 3421.98 | 6042.98 | 191.24 | 6234.22 | 12.086 | 0.38248
| +6MBE | 2 | 1508.52 | 3985.52 | 5494.04 | 168.15 | 5662.19 | 10.9881 | 0.3363
| +9MBE | 0 | 2722.24 | 4346.33 | 7068.57 | 219.57 | 7288.14 | 0 | 0
DD | Basic Body | 51 | 13165.7 | 8021.65 | 21187.35 | 1042.58 | 22229.93 | 1080.5548 | 53.1716
| +0MBE | 43 | 2665.92 | 2905.27 | 5571.19 | 227.33 | 5798.52 | 239.5612 | 9.7752
| +3MBE | 8 | 4061.8 | 3248.6 | 7310.4 | 278.83 | 7589.23 | 58.4832 | 2.2306
| +6MBE | 5 | 2298.52 | 4052.81 | 6351.33 | 227.04 | 6578.37 | 31.7567 | 1.1352
| +9MBE | 5 | 3254.36 | 5539.69 | 8794.05 | 317.91 | 9111.96 | 43.9703 | 1.5896
| +12MBE | 2 | 4515.68 | 7278.35 | 11794.03 | 410.24 | 12204.27 | 23.5881 | 0.82048
| +18MBE | 16 | 6690.48 | 14689.72 | 21380.2 | 720.86 | 22101.06 | 342.0832 | 11.5338
| +25MBE | 8 | 9632.92 | 19846.99 | 29479.91 | 823.18 | 30303.09 | 235.8393 | 6.5854
TOTAL Tower SUPPLY |  | 182 |  |  | Sub Total (MT) |  |  | 4311.8432 | 179.7555
TOTAL TOWER ERECTION |  |  |  |  | Sub Total (MT) |  |  | 4311.8432 | 179.7555
[5 empty] | LOA QTY (MT) |  |  | 4226.429 | 178
[5 empty] | Deviation wrt LOA |  |  | 2.021% | 0.9862%

## HWH 220KV
Sl. No | Loc. No. | Tower of Type | Deviation Angle (DMS) | Span (m) | Section Length (m) | GPS Co-ordinate |  | Elevation (m) | Major Crossings / Remarks (With in ROW) | VILLAGE NAME | Foundation Type | Tentative Soil Classification
[6 empty] | Latitude | Longitude | [5 empty] | 160KN | 90KN | S/S | D/S | S/T | D/T | EARTHING | DB | NP | PP | BG | ACD | CP | VD | HANGER | U BOLT
EXT 1 | GANTRY | [11 empty] | 24 |  |  |  | 18
EXT 172 | AP-1 | OC+0 | [10 empty] | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
EXT 171 | AP-2 | OC+0 | [10 empty] | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
EXT 170 | AP-3 | OC+0 | [10 empty] | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
EXT 169 | AP-3(EXT) | OC+6 | [6 empty] | NALA CROSSING |  |  |  | 24 |  |  |  |  | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
1 (Ext 170) | AP-3 | OC+0 | 4°01'23 LT" |  |  | 20°11'40.417" | 85°52'33.74" | 24.634 | EXISTING LOC, OF NUAPADA-PRATAPSASAN LINE | PRATAPSASAN |  |  | 24 |  |  |  |  | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 221 |  |  |  |  | TAR ROAD,CART TRACK,FENCING,HOUSE,LT LINE
2 | AP-4 | OB+3 | 3°19'50"LT |  | 221 | 20°11'36.54" | 85°52'40.17" | 24.977 | 2 MTR RC | PRATAPSASAN | Pile | Sandy | 48 |  |  |  |  | 12 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 283 |  |  |  |  | TAR ROAD,CART TRACK,HUT,LT LINE
3 | AP-5 | OB+6 | 16°40'15"LT |  | 283 | 20°11'32.04" | 85°52'48.68" | 24.148 | 2 MTR RC | CHADHEIBAR | Pile | Sandy | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 322 |  |  |  |  | CART TRACK,CANAL,11KV LINE
4 | AP-5A | OC+3 | 32°53'48"LT |  | 322 | 20°11'29.76" | 85°52'59.51" | 22.518 |  | CHADHEIBAR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 300 |  |  |  |  | CART TRACK,LT LINE
5 | AP-6 | OC+3 | 31°27'37"RT |  | 300 | 20°11'33.15" | 85°53'9.2" | 22.307 |  | BAYAN PADA | Pile | Sandy | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 362 |  |  |  |  | POND
6 | 6/1 | OA+3 |  |  |  | 20°11'31.08" | 85°53'21.47" | 21.471 |  | BAYAN PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 307 |  |  |  |  | CANAL
7 | 6/2 | OA+0 |  |  |  | 20°11'29.32" | 85°53'31.87" | 21.303 |  | BAYAN PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
278
8 | AP-7 | OC+0 | 31°56'43"LT |  | 947 | 20°11'27.73" | 85°53'41.29" | 21.119 |  | SINGIRI SASAN | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 287 |  |  |  |  | 11KV LINE,CANAL,BOUNDARY
9 | 7/1 | OA+6 |  |  |  | 20°11'31.2" | 85°53'50.47" | 20.667 |  | BAYAN PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 293 |  |  |  |  | TAR ROAD,LT LINE,MINI STADIUM,CANAL,WATER LOGGING AREA
10 | AP-8 | OC+3 | 41°27'12"RT |  | 580 | 20°11'34.74" | 85°53'59.84" | 21.355 |  | BISUNIA PADA | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
275
11 | 8/1 | OA+0 |  |  |  | 20°11'31.73" | 85°54'8.76" | 21.132 |  | BISUNIA PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
275
12 | 8/2 | OA+0 |  |  |  | 20°11'28.72" | 85°54'17.68" | 20.985 |  | BISUNIA PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
275
13 | 8/3 | OA+0 |  |  |  | 20°11'25.71" | 85°54'26.61" | 20.86 |  | BISUNIA PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
275
14 | 8/4 | OA+0 |  |  |  | 20°11'22.71" | 85°54'35.53" | 20.738 |  | BISUNIA PADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
275
15 | 8/5 | OA+0 |  |  |  | 20°11'19.7" | 85°54'44.45" | 20.235 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
275
16 | 8/6 | OA+0 |  |  |  | 20°11'16.69" | 85°54'53.37" | 19.548 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 275 |  |  |  |  | LOW LAND
17 | 8/7 | OA+3 |  |  |  | 20°11'13.68" | 85°55'2.29" | 19.226 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 262 |  |  |  |  | 11KV LINE,TAR ROAD,CANAL
18 | AP-9 | OB+3 | 3°45'12"RT |  | 2187 | 20°11'10.82" | 85°55'10.79" | 19.705 |  | BODHA KHANDI | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 264 |  |  |  |  | 11KV LINE,LT LINE,PUMP HOUSE
19 | 9/1 | OA+6 |  |  |  | 20°11'7.4" | 85°55'19.15" | 19.681 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 316 |  |  |  |  | CC ROAD,11KV LINE
20 | 9/2 | OA+3 |  |  |  | 20°11'3.32" | 85°55'29.14" | 19.247 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 328 |  |  |  |  | DHANUA RIVER,LT LINE
21 | 9/3 | OA+3 |  |  |  | 20°10'59.07" | 85°55'39.52" | 19.619 |  | BODHA KHANDI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
337
22 | AP-10 | OB+0 | 6°25'03"LT |  | 1245 | 20°10'54.71" | 85°55'50.19" | 18.912 |  | NUAPADA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 238 |  |  |  |  | WATER PIPE LINE
23 | 10/1 | OA+0 |  |  |  | 20°10'52.45" | 85°55'58.03" | 19.102 |  | NUAPADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 251 |  |  |  |  | CART TRACK,LT LINE
24 | 10/2 | OA+0 |  |  |  | 20°10'50.07" | 85°56'6.28" | 19.186 |  | NUAPADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
266
25 | 10/3 | OA+0 |  |  |  | 20°10'47.54" | 85°56'15.04" | 18.932 |  | NUAPADA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 283 |  |  |  |  | 11KV LINE
26 | AP-11 | OB+6 | 16°18'41"RT |  | 1038 | 20°10'44.85" | 85°56'24.35" | 19.122 |  | PAMPALO | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 299 |  |  |  |  | NALA,POND,11KV LINE,CANAL,TAR ROAD,LT LINE
27 | AP-12 | OC+0 | 40°48'43"LT |  | 299 | 20°10'39.5" | 85°56'32.97" | 18.929 |  | PAMPALO | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 330 |  |  |  |  | CC ROAD,LT LINE
28 | 12/1 | OA+6 |  |  |  | 20°10'40.91" | 85°56'44.24" | 18.734 |  | PAMPALO | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 324 |  |  |  |  | CC ROAD,11KV LINE,TAR ROAD,CANAL
29 | 12/2 | OA+3 |  |  |  | 20°10'42.28" | 85°56'55.31" | 18.814 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
256
30 | AP-13 | OB+0 | 7°28'35"LT |  | 910 | 20°10'43.36" | 85°57'4.02" | 18.863 |  | SARAT | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
272
31 | 13/1 | OA+3 |  |  |  | 20°10'45.65" | 85°57'13.07" | 18.684 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 295 |  |  |  |  | CANAL,DRAIN
32 | 13/2 | OA+3 |  |  |  | 20°10'48.13" | 85°57'22.89" | 18.782 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 289 |  |  |  |  | DRAIN
33 | 13/3 | OA+3 |  |  |  | 20°10'50.56" | 85°57'32.51" | 18.883 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 280 |  |  |  |  | 11KV LINE,TAR ROAD,BOUNDRY
34 | 13/4 | OA+3 |  |  |  | 20°10'52.91" | 85°57'41.8" | 19.341 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
303
35 | 13/5 | OA+0 |  |  |  | 20°10'55.45" | 85°57'51.87" | 19.32 |  | SARAT | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
288
36 | AP-14 | OB+0 | 26°05'59"RT |  | 1727 | 20°10'57.87" | 85°58'1.46" | 19.322 |  | SARAT | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 233 |  |  |  |  | TAR ROAD,CANAL,POND
37 | AP-15 | OB+0 | 19°05'21"LT |  | 233 | 20°10'56.41" | 85°58'9.33" | 19.771 |  | ATHANTARA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 290 |  |  |  |  | POND
38 | AP-16 | OC+0 | 46°42'05"LT |  | 290 | 20°10'57.71" | 85°58'19.21" | 19.598 |  | ATHANTARA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 216 |  |  |  |  | 11KV LINE,CANAL,TAR ROAD,LT LINE,WATER LOGGING AREA
39 | AP-17 | OC+0 | 3°33'21"LT |  | 216 | 20°11'3.43" | 85°58'23.51" | 19.528 |  | ATHANTARA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 187 |  |  |  |  | WATER LOGGING AREA
40 | 17/1 | OA+3 |  |  |  | 20°11'8.59" | 85°58'26.9" | 19.742 |  | ATHANTARA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 191 |  |  |  |  | WATER LOGGING AREA
41 | AP-18 | OB+0 | 20°03'25"RT |  | 378 | 20°11'13.88" | 85°58'30.37" | 19.901 |  | ATHANTARA | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 292 |  |  |  |  | TEMPLE,CART TRACK,11KV LINE,NALA,RIVER BUND,LOW LAND AREA
42 | AP-19 | OC+6 | 0°34'15"LT |  | 292 | 20°11'19.75" | 85°58'38.28" | 22.541 |  | ATHANTARA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 399 |  |  |  |  | KUSABHADRA RIVER,RIVER BUND,CANAL,11KV LINE,TAR ROAD
43 | AP-20 | OC+6 | 7°42'36"RT |  | 399 | 20°11'27.87" | 85°58'49" | 18.034 |  | MAHUKHANDA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 289 |  |  |  |  | POND,FOOTPATH
44 | 20/1 | OA+0 |  |  |  | 20°11'32.71" | 85°58'57.53" | 18.403 |  | MAHUKHANDA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
228
45 | 20/2 | OA+0 |  |  |  | 20°11'36.53" | 85°59'4.26" | 18.415 |  | MAHUKHANDA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
216
46 | AP-21 | OB+0 | 19°54'47"RT |  | 733 | 20°11'40.15" | 85°59'10.64" | 18.498 |  | MAHUKHANDA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 297 |  |  |  |  | NALA
47 | 21/1 | OA+0 |  |  |  | 20°11'42.01" | 85°59'20.69" | 18.453 |  | UPAR SAHI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 290 |  |  |  |  | CART TRACK
48 | 21/2 | OA+0 |  |  |  | 20°11'43.83" | 85°59'30.48" | 18.781 |  | PRATAP RUDRA PUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 305 |  |  |  |  | NALA
49 | 21/3 | OA+0 |  |  |  | 20°11'45.74" | 85°59'40.8" | 18.544 |  | PRATAP RUDRA PUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
288
50 | 21/4 | OA+0 |  |  |  | 20°11'47.54" | 85°59'50.52" | 18.517 |  | PRATAP RUDRA PUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 250 |  |  |  |  | LT LINE,CART TRACK,CANAL
51 | AP-22 | OB+0 | 18°59'22"RT |  | 1430 | 20°11'49.11" | 85°59'58.99" | 18.921 |  | PRATAP RUDRA PUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 236 |  |  |  |  | LT LINE,CART TRACK,CANAL
52 | 22/1 | OA+3 |  |  |  | 20°11'48.05" | 86°0'7.05" | 19.397 |  | PRATAP RUDRA PUR | Open Cast | PS |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 244 |  |  |  |  | 11KV LINE,TAR ROAD
53 | AP-23 | OB+0 | 11°56'11"RT |  | 480 | 20°11'46.96" | 86°0'15.37" | 19.931 |  | PRATAP RUDRA PUR | Open Cast | FS | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 310 |  |  |  |  | 11KV LINE,NALA,TAR ROAD,LT LINE
54 | AP-24 | OB+0 | 21°17'56"RT |  | 310 | 20°11'43.54" | 86°0'25.42" | 19.939 |  | PRATAP RUDRA PUR | Open Cast | FS | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
280
55 | 24/1 | OA+0 |  |  |  | 20°11'37.54" | 86°0'32.7" | 19.816 |  | PRATAP RUDRA PUR | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
301
56 | 24/2 | OA+3 |  |  |  | 20°11'31.1" | 86°0'40.51" | 19.402 |  | PRATAP RUDRA PUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 254 |  |  |  |  | CART TRACK,11KV LINE
57 | 24/3 | OA+3 |  |  |  | 20°11'25.66" | 86°0'47.1" | 19.104 |  | BHAKAR SAHI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
278
58 | 24/4 | OA+0 |  |  |  | 20°11'19.72" | 86°0'54.3" | 18.701 |  | BHAKAR SAHI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
257
59 | AP-25 | OC+0 | 40°39'30"RT |  | 1370 | 20°11'14.23" | 86°1'0.96" | 18.439 |  | BHAKAR SAHI | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 296 |  |  |  |  | LT LINE
60 | 25/1 | OA+0 |  |  |  | 20°11'4.7" | 86°1'2.42" | 18.115 |  | BHAKAR SAHI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 265 |  |  |  |  | LT LINE
61 | AP-26 | OB+0 | 20°02'21"RT |  | 561 | 20°10'56.17" | 86°1'3.72" | 18.156 |  | BHAKAR SAHI | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 271 |  |  |  |  | CART TRACK,LT LINE
62 | 26/1 | OA+0 |  |  |  | 20°10'47.55" | 86°1'1.81" | 18.765 |  | BHAKAR SAHI | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
252
63 | 26/2 | OA+0 |  |  |  | 20°10'39.52" | 86°1'0.03" | 19.055 |  | BHAPUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 245 |  |  |  |  | CANAL,NALA
64 | 26/3 | OA+0 |  |  |  | 20°10'31.72" | 86°0'58.3" | 19.003 |  | BHAPUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 248 |  |  |  |  | 11KV LINE
65 | AP-27 | OB+3 | 18°02'03"LT |  | 1016 | 20°10'23.82" | 86°0'56.55" | 19.516 |  | BHAPUR | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 299 |  |  |  |  | 11KV LINE,TAR ROAD,NALA
66 | 27/1 | OA+6 |  |  |  | 20°10'14.14" | 86°0'57.66" | 19.266 |  | BHAPUR | Open Cast | FS |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 208 |  |  |  |  | 11KV LINE
67 | AP-28 | OC+3 | 44°14'14"LT |  | 507 | 20°10'7.41" | 86°0'58.43" | 18.956 |  | BHAPUR | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 279 |  |  |  |  | CC ROAD,11KV LINE,POND
68 | 28/1 | OA+0 |  |  |  | 20°10'1.62" | 86°1'5.85" | 19.137 |  | BHAPUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 247 |  |  |  |  | DRAIN
69 | 28/2 | OA+0 |  |  |  | 20°9'56.51" | 86°1'12.41" | 18.888 |  | BHAPUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 263 |  |  |  |  | DRAIN
70 | 28/3 | OA+0 |  |  |  | 20°9'51.05" | 86°1'19.41" | 18.659 |  | BHAPUR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 275 |  |  |  |  | BORE WELL
71 | AP-29 | OB+0 | 7°22'36"LT |  | 1064 | 20°9'45.36" | 86°1'26.7" | 18.45 |  | BHANRA NIGADA | Open Cast | PS | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 252 |  |  |  |  | TAR ROAD,CANAL,11KV LINE,LT LINE
72 | 29/1 | OA+3 |  |  |  | 20°9'40.99" | 86°1'34.06" | 18.243 |  | AMANA KUDA | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
256
73 | AP-30 | OB+0 | 13°14'59"LT |  | 508 | 20°9'36.56" | 86°1'41.51" | 18.15 |  | AMANA KUDA | Open Cast | FS | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 359 |  |  |  |  | NALA
74 | 30/1 | OA+3 |  |  |  | 20°9'32.77" | 86°1'53.2" | 18.334 |  | AMANA KUDA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 245 |  |  |  |  | 11KV LINE
75 | 30/2 | OA+0 |  |  |  | 20°9'30.18" | 86°2'1.17" | 18.513 |  | AMANA KUDA | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 330 |  |  |  |  | NALA
76 | AP-31 | OB+0 | 21°52'40"LT |  | 934 | 20°9'26.7" | 86°2'11.92" | 18.65 |  | AMANA KUDA | Open Cast | WBC | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 256 |  |  |  |  | TAR ROAD,CANAL
77 | 31/1 | OA+0 |  |  |  | 20°9'27.13" | 86°2'20.74" | 18.339 |  | AMANA KUDA | Open Cast | PS |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
242
78 | 31/2 | OA+0 |  |  |  | 20°9'27.53" | 86°2'29.06" | 18.261 |  | KHULISO | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 230 |  |  |  |  | DRAIN,11KV LINE
79 | AP-32 | OB+3 | 28°07'06"LT |  | 728 | 20°9'27.91" | 86°2'36.96" | 17.52 |  | KHULISO | Pile | Sandy Clay | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 204 |  |  |  |  | TAR ROAD,LT LINE
80 | AP-33 | OC+3 | 45°26'43"RT |  | 204 | 20°9'31.33" | 86°2'42.96" | 17.09 |  | KHULISO | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 283 |  |  |  |  | 33KV LINE
81 | AP-34 | OB+0 | 21°51'03"RT |  | 283 | 20°9'29.04" | 86°2'52.42" | 17.65 |  | SBARNA PUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
240
82 | 34/1 | OA+0 |  |  |  | 20°9'24.42" | 86°2'59.09" | 17.689 |  | SBARNA PUR | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
262
83 | 34/2 | OA+0 |  |  |  | 20°9'19.41" | 86°3'6.33" | 17.577 |  | NUAGAON | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
280
84 | 34/3 | OA+0 |  |  |  | 20°9'14.02" | 86°3'14.11" | 17.711 |  | NUAGAON | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
274
85 | 34/4 | OA+0 |  |  |  | 20°9'8.76" | 86°3'21.71" | 17.545 |  | BADA KAR KAR | Open Cast | FS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
300
86 | 34/5 | OA+3 |  |  |  | 20°9'2.99" | 86°3'30.04" | 17.554 |  | BADA KAR KAR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 224 |  |  |  |  | TAR ROAD,11KV LINE
87 | AP-35 | OB+0 | 3°30'50"LT |  | 1580 | 20°8'58.7" | 86°3'36.24" | 18.14 |  | BADA KAR KAR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 302 |  |  |  |  | PUMP HOUSE
88 | 35/1 | OA+0 |  |  |  | 20°8'53.39" | 86°3'44.98" | 18.171 |  | MAJHI KHANDA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
300
89 | 35/2 | OA+3 |  |  |  | 20°8'48.14" | 86°3'53.63" | 17.929 |  | MAJHI KHANDA | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 271 |  |  |  |  | 11KV LINE,TAR ROAD
90 | 35/3 | OA+0 |  |  |  | 20°8'43.37" | 86°4'1.49" | 17.543 |  | NIALI | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
311
91 | 35/4 | OA+0 |  |  |  | 20°8'37.89" | 86°4'10.5" | 17.316 |  | NIALI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
298
92 | 35/5 | OA+0 |  |  |  | 20°8'32.66" | 86°4'19.12" | 17.111 |  | NIALI | Open Cast | WET |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
288
93 | 35/6 | OA+0 |  |  |  | 20°8'27.58" | 86°4'27.48" | 17.123 |  | PUBA KHANDA | Open Cast | WET |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 280 |  |  |  |  | 11KV LINE,LT LINE,TAR ROAD
94 | AP-36 | OB+3 | 14°16'22"LT |  | 2050 | 20°8'22.68" | 86°4'35.56" | 16.98 |  | PUBA KHANDA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 269 |  |  |  |  | LT LINE
95 | 36/1 | OA+0 |  |  |  | 20°8'19.9" | 86°4'44.36" | 16.829 |  | WAUPALI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
250
96 | 36/2 | OA+0 |  |  |  | 20°8'17.33" | 86°4'52.51" | 16.949 |  | WAUPALI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 239 |  |  |  |  | NALA
97 | 36/3 | OA+0 |  |  |  | 20°8'14.86" | 86°5'0.33" | 17.138 |  | WAUPALI | Open Cast | WET |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
281
98 | 36/4 | OA+0 |  |  |  | 20°8'11.97" | 86°5'9.49" | 17.112 |  | WAUPALI | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 247 |  |  |  |  | NALA
99 | AP-37 | OB+0 | 18°13'12"LT |  | 1286 | 20°8'9.43" | 86°5'17.55" | 17.21 |  | WAUPALI | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
287
100 | 37/1 | OA+0 |  |  |  | 20°8'9.39" | 86°5'27.45" | 17.089 |  | WAUPALI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 233 |  |  |  |  | LT LINE,FOOTPATH
101 | 37/2 | OA+0 |  |  |  | 20°8'9.35" | 86°5'35.48" | 17.29 |  | BAHARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
264
102 | 37/3 | OA+0 |  |  |  | 20°8'9.32" | 86°5'44.56" | 17.484 |  | BAHARANA | Open Cast | PS |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 231 |  |  |  |  | TAR ROAD,HOUSE
103 | AP-38 | OB+0 | 10°31'37"RT |  | 1015 | 20°8'9.28" | 86°5'52.51" | 17.72 |  | BAHARANA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 304 |  |  |  |  | TAR ROAD,CANAL,HOUSE,BOUNDRY
104 | 38/1 | OA+0 |  |  |  | 20°8'7.44" | 86°6'2.78" | 17.885 |  | BARIMUNDEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
323
105 | 38/2 | OA+0 |  |  |  | 20°8'5.47" | 86°6'13.7" | 18.024 |  | BARIMUNDEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
311
106 | 38/3 | OA+0 |  |  |  | 20°8'3.58" | 86°6'24.23" | 18.066 |  | ATHANTARA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
331
107 | 38/4 | OA+3 |  |  |  | 20°8'1.56" | 86°6'35.43" | 18.148 |  | ATHANTARA | Pile |  |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 295 |  |  |  |  | LT LINE,TAR ROAD
108 | AP-39 | OC+6 | 3°21'21"RT |  | 1564 | 20°7'59.76" | 86°6'45.41" | 18.52 |  | ATHANTARA | Pile | Sandy | 48 |  |  |  |  | 12 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 325 |  |  |  |  | HEMSAGAR RIVER,TAR ROAD,CANAL,11KV LINE
109 | AP-40 | OC+6 | 22°11'32"LT |  | 325 | 20°7'57.18" | 86°6'56.26" | 18.55 |  | PODANA | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
361
110 | 40/1 | OA+0 |  |  |  | 20°7'58.83" | 86°7'8.58" | 18.279 |  | PODANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 301 |  |  |  |  | FOOTPATH
111 | 40/2 | OA+0 |  |  |  | 20°8'0.2" | 86°7'18.86" | 18.304 |  | BADARO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 281 |  |  |  |  | MURRAM ROAD,CANAL,DRAIN
112 | 40/3 | OA+0 |  |  |  | 20°8'1.48" | 86°7'28.45" | 18.258 |  | BADARO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 327 |  |  |  |  | 11KV LINE,TAR ROAD
113 | AP-41 | OB+0 | 8°35'45"RT |  | 1270 | 20°8'2.97" | 86°7'39.6" | 18.21 |  | KAPASI | Pile |  | 48 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 339 |  |  |  |  | 11KV LINE,TAR ROAD
114 | 41/1 | OA+0 |  |  |  | 20°8'2.861" | 86°7'51.27" | 17.921 |  | KAPASI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
330
115 | 41/2 | OA+3 |  |  |  | 20°8'2.76" | 86°8'2.63" | 17.919 |  | KAPASI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 343 |  |  |  |  | BORE WELL,LT LINE
116 | 41/3 | OA+3 |  |  |  | 20°8'2.65" | 86°8'14.44" | 17.807 |  | TIHUDI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 278 |  |  |  |  | NALA
117 | AP-42 | OB+0 | 6°26'50"RT |  | 1290 | 20°8'2.56" | 86°8'24.02" | 17.92 |  | TIHUDI | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 291 |  |  |  |  | NALA
118 | 42/1 | OA+0 |  |  |  | 20°8'1.41" | 86°8'33.96" | 17.885 |  | TIHUDI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
227
119 | 42/2 | OA+0 |  |  |  | 20°8'0.51" | 86°8'41.71" | 17.824 |  | PARIMALA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 264 |  |  |  |  | LOWLAND AREA,LT LINE,TAR ROAD
120 | 42/3 | OA+3 |  |  |  | 20°7'59.46" | 86°8'50.73" | 17.682 |  | PARIMALA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
265
121 | AP-43 | OC+6 | 6°18'53"RT |  | 1047 | 20°7'58.41" | 86°8'59.8" | 17.613 |  | PARIMALA | Pile |  | 36 |  |  |  | 6 | 6 | 2 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 342 |  |  |  |  | LOWLAND AREA,NALA,CART TRACK, DEVI RIVER
122 | 43/1 | OA+6 |  |  |  | 20°7'55.84" | 86°9'11.26" | 14.214 | 7 MTR RC | PARIMALA | Pile | River |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 315 |  |  |  |  | DEVI RIVER
123 | 43/2 | OA+6 |  |  |  | 20°7'53.48" | 86°9'21.81" | 14.924 | 7 MTR RC | PARIMALA | Pile | River |  | 24 |  | 6 |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 |  | 6
|  |  |  | 359 |  |  |  |  | DEVI RIVER,NALA,CART TRACK
124 | AP-44 | OC+6 | 7°41'26"LT |  | 1016 | 20°7'50.79" | 86°9'33.83" | 16.08 |  | POHALA | Pile |  | 36 |  |  |  | 6 | 6 | 2 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 287 |  |  |  |  | NALA
125 | 44/1 | OA+0 |  |  |  | 20°7'49.88" | 86°9'43.66" | 15.775 |  | KORANIA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 285 |  |  |  |  | TAR ROAD,LT LINE
126 | AP-45 | OC+0 | 38°25'41"LT |  | 572 | 20°7'48.97" | 86°9'53.44" | 15.712 |  | KORANIA | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 292 |  |  |  |  | DRAIN,TAR ROAD,11KV LINE,CANAL,LT LINE
127 | 45/1 | OA+6 |  |  |  | 20°7'54.1" | 86°10'1.88" | 15.517 |  | ROHIA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 250 |  |  |  |  | 11KV LINE
128 | 45/2 | OA+6 |  |  |  | 20°7'58.52" | 86°10'9.13" | 15.373 |  | ROHIA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 354 |  |  |  |  | DRAIN,11KV LINE,CANAL,TAR ROAD
129 | AP-46 | OB+0 | 29°26'24"LT |  | 896 | 20°8'4.74" | 86°10'19.36" | 15.485 |  | ROHIA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 281 |  |  |  |  | TAR ROAD,CANAL,11KV LINE,33KV LINE
130 | 46/1 | OA+6 |  |  |  | 20°8'12.82" | 86°10'23.86" | 15.471 |  | ARAKHAKUDA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
327
131 | 46/2 | OA+0 |  |  |  | 20°8'22.25" | 86°10'29.12" | 15.506 |  | GANDHAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
267
132 | 46/3 | OA+0 |  |  |  | 20°8'29.92" | 86°10'33.4" | 15.537 |  | GANDHAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
270
133 | 46/4 | OA+0 |  |  |  | 20°8'37.66" | 86°10'37.71" | 15.324 |  | GANDHAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
285
134 | 46/5 | OA+0 |  |  |  | 20°8'45.87" | 86°10'42.29" | 15.451 |  | GANDHAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 340 |  |  |  |  | DRAIN,11KV LINE
135 | AP-47 | OB+3 | 11°15'48"RT |  | 1770 | 20°8'55.65" | 86°10'47.75" | 16.145 |  | GANDHAN | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 271 |  |  |  |  | TAR ROAD,NALA
136 | AP-48 | OB+3 | 27°06'16"RT |  | 271 | 20°9'2.51" | 86°10'53.64" | 16.362 |  | GANDHAN | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 300 |  |  |  |  | CC ROAD,LT LINE,11KV LINE,NALA,TAR ROAD
137 | AP-49 | OB+3 | 6°11'21"LT |  | 300 | 20°9'6.45" | 86°11'3.09" | 15.796 |  | NAUGAON | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 317 |  |  |  |  | CANAL
138 | 49/1 | OA+0 |  |  |  | 20°9'11.61" | 86°11'12.53" | 15.593 |  | NAUGAON | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
285
139 | 49/2 | OA+0 |  |  |  | 20°9'16.26" | 86°11'21.04" | 15.478 |  | NAUGAON | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
296
140 | 49/3 | OA+0 |  |  |  | 20°9'21.08" | 86°11'29.86" | 15.325 |  | NAUGAON | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
281
141 | 49/4 | OA+0 |  |  |  | 20°9'25.65" | 86°11'38.23" | 15.269 |  | KHAERA BASTA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
314
142 | AP-50 | OC+6 | 40°13'29"RT |  | 1493 | 20°9'30.76" | 86°11'47.59" | 15.221 |  | KHAERA BASTA | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 327 |  |  |  |  | TAR ROAD,CANAL,33KV LINE,11KV LINE,NALA
143 | 50/1 | OC+6 |  |  |  | 20°9'28.88" | 86°11'58.66" | 15.213 |  | MUNDALO | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 353 |  |  |  |  | DRAIN,11KV LINE,TAR ROAD
144 | AP-51 | OC+3 | 29°07'27"LT |  | 680 | 20°9'26.85" | 86°12'10.64" | 14.801 |  | MUNDALO | Pile | Clay | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 221 |  |  |  |  | LT LINE,TAR ROAD,POND
145 | AP-52 | OB+0 | 22°19'29"RT |  | 221 | 20°9'29.18" | 86°12'17.82" | 14.692 |  | MUNDALO | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 303 |  |  |  |  | POND
146 | 52/1 | OA+3 |  |  |  | 20°9'28.59" | 86°12'28.25" | 14.579 |  | MUNDALO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 364 |  |  |  |  | DEAD LINE,DRAIN,CC ROAD
147 | 52/2 | OA+3 |  |  |  | 20°9'27.89" | 86°12'40.75" | 15.083 |  | KUNDHESWAR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 304 |  |  |  |  | 11KV LINE,POND
148 | AP-53 | OC+0 | 57°23'31"LT |  | 971 | 20°9'27.31" | 86°12'51.21" | 14.814 |  | KUNDHESWAR | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 304 |  |  |  |  | POND,11KV LINE,TAR ROAD,FENCING, HAND PUMP
149 | 53/1 | OA+0 |  |  |  | 20°9'35.31" | 86°12'57.37" | 14.336 |  | MADHUPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 306 |  |  |  |  | 11KV LINE,MORRUM ROAD,CANAL
150 | AP-54 | OB+3 | 7°36'28"RT |  | 610 | 20°9'43.37" | 86°13'3.57" | 14.213 |  | KUNDHESWAR | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 252 |  |  |  |  | CANAL,MURRUM ROAD,11KV LINE, ALAKA RIVER
151 | AP-55 | OC+3 | 40°06'20"LT |  | 252 | 20°9'49.32" | 86°13'9.57" | 13.981 |  | CHANR PUR | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 326 |  |  |  |  | 11KV LINE,FOOTPATH
152 | 55/1 | OA+6 |  |  |  | 20°9'59.9" | 86°13'10.25" | 13.236 |  | CHANR PUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 297 |  |  |  |  | 11KV LINE,CART TRACK,CANAL,NALA,TAR ROAD
153 | AP-56 | OB+3 | 9°06'30"RT |  | 623 | 20°10'9.55" | 86°13'10.88" | 12.991 |  | CHANR PUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 276 |  |  |  |  | TAR ROAD,NALA
154 | 56/1 | OA+0 |  |  |  | 20°10'18.3" | 86°13'12.95" | 12.889 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 245 |  |  |  |  | DRAIN
155 | 56/2 | OA+0 |  |  |  | 20°10'26.08" | 86°13'14.79" | 12.641 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
261
156 | 56/3 | OA+0 |  |  |  | 20°10'34.36" | 86°13'16.75" | 12.769 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
264
157 | AP-57 | OC+0 | 58°16'38"RT |  | 1046 | 20°10'42.74" | 86°13'18.74" | 13.311 |  | GARAMA | Pile |  | 24 | 6 | 3 |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
276
158 | 57/1 | OA+0 |  |  |  | 20°10'45.68" | 86°13'27.74" | 12.544 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 256 |  |  |  |  | NALA,CC ROAD,11KV LINE,FOOTPATH
159 | AP-58 | OB+0 | 12°23'26"LT |  | 532 | 20°10'48.41" | 86°13'36.08" | 13.678 |  | MALAPUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 291 |  |  |  |  | NALA,LOWLAND
160 | AP-59 | OB+0 | 29°14'34"LT |  | 291 | 20°10'53.36" | 86°13'44.63" | 12.876 |  | MALAPUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 279 |  |  |  |  | NALA
161 | 59/1 | OA+0 |  |  |  | 20°11'1.26" | 86°13'49.32" | 12.383 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
283
162 | 59/2 | OA+0 |  |  |  | 20°11'9.3" | 86°13'54.09" | 12.4 |  | GARAMA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 305 |  |  |  |  | DRAIN
163 | AP-60 | OC+0 | 28°15'25"RT |  | 867 | 20°11'17.95" | 86°13'59.22" | 12.221 |  | SADEIPUR | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 245 |  |  |  |  | PROPOSED NH
164 | AP-61 | OC+3 | 39°58'47"LT |  | 245 | 20°11'22.23" | 86°14'6.34" | 12.288 |  | SADEIPUR | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 254 |  |  |  |  | -
165 | 61/1 | OA+0 |  |  |  | 20°11'30.12" | 86°14'8.98" | 12.548 |  | SADEIPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 243 |  |  |  |  | -
166 | 61/2 | OA+0 |  |  |  | 20°11'37.67" | 86°14'11.51" | 12.459 |  | SADEIPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 204 |  |  |  |  | 11 KV LINE
167 | 61/3 | OA+0 |  |  |  | 20°11'44" | 86°14'13.63" | 12.546 |  | SADEIPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 243 |  |  |  |  | 11KV,CC ROAD
168 | AP-62 | OB+3 | 25°00'09"RT |  | 944 | 20°11'51.5" | 86°14'16.14" | 12.992 |  | BENUPUR | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 290 |  |  |  |  | -
169 | 62/1 | OA+0 |  |  |  | 20°11'59.08" | 86°14'23.51" | 12.89 |  | BENUPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 282 |  |  |  |  | -
170 | 62/2 | OA+0 |  |  |  | 20°12'6.53" | 86°14'30.75" | 12.847 |  | BENUPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 325 |  |  |  |  | DRAIN
171 | AP-63 | OB+6 | 6°33'33"RT |  | 897 | 20°12'14.47" | 86°14'38.47" | 12.815 |  | BENUPUR | Pile | Sandy | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 344 |  |  |  |  | TAR RD, 11KV LINE
172 | AP-64 | OB+6 | 9°43'56"RT |  | 344 | 20°12'20.44" | 86°14'45.78" | 13.162 |  | SAHADA | Pile | Clay | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 280 |  |  |  |  | -
173 | 64/1 | OA+3 |  |  |  | 20°12'25.16" | 86°14'54.03" | 12.929 |  | SAHADA | Pile | Sandy |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 280 |  |  |  |  | DRAIN, CART TRACK
174 | 64/2 | OA+0 |  |  |  | 20°12'29.87" | 86°15'2.29" | 12.764 |  | SINGIRI | Pile | Clay |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 267 |  |  |  |  | -
175 | 64/3 | OA+0 |  |  |  | 20°12'34.37" | 86°15'10.17" | 12.637 |  | JALISO | Pile | Clay |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 293 |  |  |  |  | DRAIN
176 | 64/4 | OA+0 |  |  |  | 20°12'39.3" | 86°15'18.8" | 12.795 |  | JALISO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 290 |  |  |  |  | POND,NALA
177 | 64/5 | OB+0 | 00°00'00" |  | 1410 | 20°12'44.17" | 86°15'27.33" | 12.216 |  | MULUGAN | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 271 |  |  |  |  | CANAL
178 | 64/6 | OA+0 |  |  |  | 20°12'48.72" | 86°15'35.31" | 12.11 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
280
179 | 64/7 | OA+0 |  |  |  | 20°12'53.44" | 86°15'43.57" | 11.843 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
279
180 | 64/8 | OA+0 |  |  |  | 20°12'58.13" | 86°15'51.79" | 11.742 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 2 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 268 |  |  |  |  | INDIAN OIL PIPE LINE
181 | 64/9 | OA+0 |  |  |  | 20°13'2.64" | 86°15'59.68" | 11.528 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 2 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 256 |  |  |  |  | CANAL
182 | AP-65 | OB+6 | 15°49'45"RT |  | 1354 | 20°13'6.95" | 86°16'7.24" | 11.352 |  | MULUGAN | Pile | Clay | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 280 |  |  |  |  | TAR ROAD,POND
183 | AP-66 | OB+0 | 26°23'31"RT |  | 280 | 20°13'9.36" | 86°16'16.56" | 10.962 |  | MULUGAN | Pile | Clay | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 230 |  |  |  |  | -
184 | 66/1 | OA+0 |  |  |  | 20°13'7.93" | 86°16'24.31" | 10.882 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 200 |  |  |  |  | CANAL
185 | 66/2 | OA+0 |  |  |  | 20°13'6.68" | 86°16'31.1" | 10.704 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 2 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 300 |  |  |  |  | INDIAN OIL PIPE LINE
186 | 66/3 | OA+0 |  |  |  | 20°13'4.8" | 86°16'41.25" | 10.229 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 2 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 300 |  |  |  |  | FOOTPATH
187 | 66/4 | OA+0 |  |  |  | 20°13'2.93" | 86°16'51.39" | 10.327 |  | MULUGAN | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 300 |  |  |  |  | NALA
188 | 66/5 | OA+0 |  |  |  | 20°13'1.06" | 86°17'1.54" | 10.556 |  | ASARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 272 |  |  |  |  | FOOTPATH
189 | AP-67 | OB+0 | 0°00'00"RT |  | 1602 | 20°12'59.37" | 86°17'10.69" | 10.162 |  | SARANA | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 282 |  |  |  |  | FOOTPATH
190 | 67/1 | OA+0 |  |  |  | 20°12'57.61" | 86°17'20.23" | 9.935 |  | SARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 245 |  |  |  |  | -
191 | 67/2 | OA+0 |  |  |  | 20°12'56.08" | 86°17'28.49" | 9.905 |  | SARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 262 |  |  |  |  | NALA,CART TRACK
192 | 67/3 | OA+0 |  |  |  | 20°12'54.44" | 86°17'37.36" | 9.537 |  | SARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 247 |  |  |  |  | -
193 | 67/4 | OA+0 |  |  |  | 20°12'52.9" | 86°17'45.71" | 9.273 |  | SARANA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 237 |  |  |  |  | NALA
194 | 67/5 | OA+0 |  |  |  | 20°12'51.41" | 86°17'53.74" | 9.285 |  | DIGODA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 270 |  |  |  |  | TAR ROAD
195 | AP-68 | OB+3 | 4°50'53"LT |  | 1543 | 20°12'49.72" | 86°18'2.88" | 9.461 |  | DIGODA | Pile | Clay | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 292 |  |  |  |  | CANAL,LT LINE
196 | 68/1 | OA+3 |  |  |  | 20°12'48.69" | 86°18'12.9" | 9.444 |  | RANKEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 320 |  |  |  |  | -
197 | 68/2 | OA+0 |  |  |  | 20°12'47.56" | 86°18'23.86" | 9.322 |  | RANKEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 282 |  |  |  |  | POND
198 | 68/3 | OA+0 |  |  |  | 20°12'46.56" | 86°18'33.53" | 9.13 |  | RANKEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 292 |  |  |  |  | NALA
199 | 68/4 | OA+0 |  |  |  | 20°12'45.53" | 86°18'43.53" | 9.016 |  | POLO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 239 |  |  |  |  | POND,CART TRACK
200 | 68/5 | OA+0 |  |  |  | 20°12'44.7" | 86°18'51.65" | 9.049 |  | ARADEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 265 |  |  |  |  | CART TRACK
201 | AP-69 | OB+0 | 12°04'35"RT |  | 1690 | 20°12'43.76" | 86°19'0.73" | 9.111 |  | ARADEI | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 300 |  |  |  |  | -
202 | 69/1 | OA+3 |  |  |  | 20°12'40.69" | 86°19'10.55" | 9.311 |  | ARADEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 261 |  |  |  |  | 11KV LINE
203 | 69/2 | OA+0 |  |  |  | 20°12'38.03" | 86°19'19.09" | 9.541 |  | ARADEI | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 219 |  |  |  |  | TAR ROAD
204 | 69/3 | OA+0 |  |  |  | 20°12'35.79" | 86°19'26.23" | 9.567 |  | NAULA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 282 |  |  |  |  | -
205 | AP-70 | OB+0 | 12°36'08"RT |  | 1062 | 20°12'32.91" | 86°19'35.47" | 9.365 |  | NAULA | Pile | Clay | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 238 |  |  |  |  | NALA,CART TRACK,11KV LINE
206 | 70/1 | OA+0 |  |  |  | 20°12'28.93" | 86°19'42.5" | 9.584 |  | NAULA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 221 |  |  |  |  | 11KV LINE
207 | 70/2 | OA+0 |  |  |  | 20°12'25.23" | 86°19'49.04" | 9.639 |  | NAULA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 304 |  |  |  |  | -
208 | AP-71 | OB+0 | 29°24'07"LT |  | 763 | 20°12'20.15" | 86°19'58.04" | 9.689 |  | TULANGA | Pile | Clay | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 279 |  |  |  |  | -
209 | 71/1 | OA+0 |  |  |  | 20°12'19.91" | 86°20'7.63" | 9.821 |  | TULANGA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 284 |  |  |  |  | -
210 | 71/2 | OA+0 |  |  |  | 20°12'19.66" | 86°20'17.41" | 9.596 |  | SHERPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 284 |  |  |  |  | -
211 | 71/3 | OA+0 |  |  |  | 20°12'19.42" | 86°20'27.21" | 9.771 |  | SHERPUR | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 292 |  |  |  |  | DRAIN
212 | 71/4 | OA+0 |  |  |  | 20°12'19.16" | 86°20'37.26" | 9.649 |  | TULANGA | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 286 |  |  |  |  | NALA
213 | 71/5 | OA+0 |  |  |  | 20°12'18.92" | 86°20'47.12" | 9.562 |  | SANILO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 256 |  |  |  |  | NALA
214 | 71/6 | OA+0 |  |  |  | 20°12'18.7" | 86°20'55.95" | 9.537 |  | SANILO | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 286 |  |  |  |  | POND,11KV LINE,TAR ROAD
215 | AP-72 | OB+3 | 15°47'03"LT |  | 1967 | 20°12'18.45" | 86°21'5.79" | 9.552 |  | SANILO | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 288 |  |  |  |  | -
216 | 72/1 | OA+0 |  |  |  | 20°12'20.75" | 86°21'15.39" | 9.561 |  | IBRISING | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 278 |  |  |  |  | -
217 | 72/2 | OA+0 |  |  |  | 20°12'22.98" | 86°21'24.68" | 9.477 |  | IBRISING | Pile |  |  | 12 | 6 |  |  |  | 1 | 1 | 1 | 6 | 6 | 1 | 2 | 12 | 6
|  |  |  | 280 |  |  |  |  | -
218 | AP-73 | OB+0 | 6°37'48"LT |  | 846 | 20°12'25.22" | 86°21'34.02" | 9.347 |  | JABEDHUAN | Pile |  | 36 |  |  |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 244 |  |  |  |  | LOW LAND,TAR ROAD
219 | AP-74 | OC+0 | 43°16'49"LT |  | 244 | 20°12'28.05" | 86°21'41.86" | 9.233 |  | JABEDHUAN | Pile |  | 36 | 6 | 3 |  | 6 | 6 | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
|  |  |  | 100 |  |  |  |  | -
220 | AP-75 | OC+0 | 0°59'50"RT |  | 100 | 20°12'30.98" | 86°21'43.37" | 9.272 |  | JABEDHUAN | Pile |  | 24 |  |  |  | 12 |  | 1 | 1 | 1 | 6 |  | 1 | 2 | 24
53
221 | GANTRY | GANTRY |  |  | 53 | 20°12'32.51" | 86°21'44.19" | 9.261 |  | JABEDHUAN |  |  | 24 |  |  |  | 12
TOTAL LENGTH = 61.177 KM | [12 empty] | 2388 | 1890 | 861 | 42 | 768 | 210 | 230 | 224 | 224 | 1344 | 864 | 224 | 448 | 3648 | 822 | 42
TOTAL WITH 3% EXTRA | [12 empty] | 2459.64 | 1946.7 | 886.83 | 43.26 | 791.04 | 216.3 | 236.9 | 230.72 | 230.72 | 1384.32 | 889.92 | 230.72 | 461.44 | 3757.44 | 846.66 | 43.26
[11 empty] | Open Cast | 64
[11 empty] | Pile | 155
219
[11 empty] | All Balance | FS