## Summary
Project Name: 2x500 MVA, 400/220/33KV Gas (SF6) Insulated Sub-station (GIS) with SAS and 1X125 MVAr (400 KV) bus reactor with control at Ersama, Paradeep. (ii) 400KV AIS feeder bay extension with SAS (to be integrated with the existing SAS) and 2 nos. 80 MVAr (400 KV) line reactors with suitable NGR & its control (One dia) at 400KV New Duburi gird sub-station for connectivity with proposed GIS S/S at Ersama, Paradeep.
ABSTRACT
Overall Summary (Overall Contract Value Change)
|  |  | Original Order Value |  |  | Total Order Value after 1st Amendment
New Amendment Price Schedule | Sl. No. | Item Description | Ex-Works Price with freight in INR | Total GST in INR (18%) | Total in INR | Total Revised Price | Total GST in INR (18%) | Total in INR | Diffential Value inclusive of GST (between original BOQ and Amended BOQ) | Percentage Variation
| 1 | Supply Schedules | 1418108433.8754 | 255259518.0976 | 1673367951.9729 | 1553588816.6423 | 279645986.9956 | 1833234803.6379 | 159866851.665 | 9.554%
| 2 | Erection (Electrical) | 40045462.0123 | 7208183.1622 | 47253645.1745 | 52563286.2335 | 9461391.522 | 62024677.7556 | 14771032.581 | 31.26%
| 3 | CIVIL | 315768140.2982 | 56838265.2537 | 372606405.5518 | 629971068.5894 | 113394792.3461 | 743365860.9355 | 370759455.3837 | 99.5%
|  | Total | 1773922036.1858 | 319305966.5135 | 2093228002.6993 | 2236123171.4652 | 402502170.8637 | 2638625342.329 | 545397339.6297 | 26.06%

## SUPPLY_SCHEDULE_VIIA
ODISHA POWER TRANSMISSION CORPORATION LIMITED
LOA No. - SGM-CPC-Construction-400/220kV GIS Ersama (Pkg-49/2021-22)-08/2020/828
LOA No. - SGM-CPC-Construction-400/220kV GIS Ersama (Pkg-49/2021-22)-08/2020/828
|  |  | Quantity |  |  |  |  | Unit Price |  | Amount As per Original BOQ |  |  | Amount As per Amendment-1 BOQ | [5 empty] | REMARKS | Item Category
Sl. No. | DESCRIPTION OF ITEMS | UNIT | QTY during Original Order | Total QTY as per actual | Differential Qty | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Unit Price as per BOQ | Unit Price as per least cost | Original BOQ Amount | Total GST @ 18% (Works contract), in INR | Total Amount including GST, in INR | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Total Amount | Total GST @ 18% , in INR | Total Amount inclusive GST after Amendment-1 | Differential Amount (BOQ Amount and Amended Amount) inclusive of GST
1 | 2 | 3 | 4 | 5 | 6=5-4 | 7 | 8 | 9 | 10 | 11=4*9 | 12 | 13=11+12 | 14=7*9 | 15=8*10 | 16=14+15 | 17 | 18=16+17 | 19=18-13
A | SUPPLY COMPONENT OF THE WORKS CONTRACT FOR SUBSTATION ERSAMA
1 | 3150A, 63kA for 3s, one and half Circuit Breaker (Circuit breaker shall be C2 - M2 class as per IEC 62271-100) arrangement. 420KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. | [18 empty] | GIS 400kV
1.1 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector,grounding switches & line PT), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated Single Phase Busbar, circuit breaker , current transformer (6 core), line Potential transformer (3 cores), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 23167434.8904 |  | 46334869.7809 | 8340276.5606 | 54675146.3415 | 46334869.7809 | 0 | 46334869.7809 | 8340276.5606 | 54675146.3415 | 0 |  | GIS 400kV | A | =
1.2 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector,grounding switches etc), SF6 gas insulated (Bus Reactor) bay module each comprising of SF6 gas insulated Single Phase Busbar, circuit breaker with CSD (Control Switching Device), current transformer (6 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through, different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Bus reactor bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 1 | 2 | 1 | 1 | 1 | 25027868.0947 | 25027868.0947 | 25027868.0947 | 4505016.2571 | 29532884.3518 | 25027868.0947 | 25027868.0947 | 50055736.1894 | 9010032.5141 | 59065768.7035 | 29532884.3518 | Revised qty as per approved SLD (Drg. No. TB-3-420-510-001) Cost Data Rate for 400kV GIS not available. Hence, BoQ rate considered. | GIS 400kV | B | 162669708.7558
1.3 | 420kV, 3150A, 63KA for (3 sec for CB & 1 sec for CT,Disconnector,grounding switches etc) SF6 gas insulated ICT feeder bay module each comprising of SF6 gas insulated Single Phase Busbar, circuit breaker with CSD (Control Switching Device), current transformer (6 cores), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through, different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete ICT feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. . | Set | 2 | 2 | 0 | 2 | 0 | 25027868.0947 |  | 50055736.1894 | 9010032.5141 | 59065768.7035 | 50055736.1894 | 0 | 50055736.1894 | 9010032.5141 | 59065768.7035 | 0 |  | GIS 400kV | A
1.4 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector & grounding switches), SF6 gas insulated Tie bay module each comprising of SF6 gas insulated Single Phase Busbar, circuit breaker with CSD (Control Switching Device), current transformer (6 core), Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Tie bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 3 | 3 | 0 | 3 | 0 | 19735446.512 |  | 59206339.5359 | 10657141.1165 | 69863480.6524 | 59206339.5359 | 0 | 59206339.5359 | 10657141.1165 | 69863480.6524 | 0 |  | GIS 400kV | A
1.5 | 420kV, 3150A, 63KA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T) , 3- phase Isolated , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), dis connectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 , different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. . | Set | 2 | 2 | 0 | 2 | 0 | 7520441.2153 |  | 15040882.4305 | 2707358.8375 | 17748241.268 | 15040882.4305 | 0 | 15040882.4305 | 2707358.8375 | 17748241.268 | 0 |  | GIS 400kV | A
1.6 | 420kV, 3150 A, 63kA, 3 Sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed]outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) etc. as per the technical specification. (The GIBus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 1050 | 1400 | 350 | 1312 | 88 | 61393.0685 | 61393.0685 | 64462721.964 | 11603289.9535 | 76066011.9175 | 80547705.9207 | 5402590.0313 | 85950295.952 | 15471053.2714 | 101421349.2233 | 25355337.3058 | Revised qty as per approved LUP (Drg. No. TB-420-316-000) Cost Data Rate for 400kV GIS not available. Hence, BoQ rate considered. | GIS 400kV | B | -10246334.6971
1.7 | 420kV, 3150 A, 63kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with support structure. | NO | 15 | 15 | 0 | 15 | 0 | 650086.3846 |  | 9751295.7685 | 1755233.2383 | 11506529.0069 | 9751295.7685 | 0 | 9751295.7685 | 1755233.2383 | 11506529.0069 | 0 |  | GIS 400kV | A
1.8 | Online continuous Partial Discharge Monitoring System (PDM): For Entire 420 KV & 245 KV GIS equipment system shall have Online continuous Partial Discharge Monitoring System (PDM) system to provide an automatic facility for the simultaneous collection of PD data at multiple points on the GIS & its associated GIB ducts and Voltage Transformers adopting UHF technique & the data stored shall provide a historical record of the progress of PD sources and shall identify the areas of maximum activity. PDM system shall be interfacing with UHF PD couplers provided.The PD Monitoring PC Work Station alongwith all accessories shall be considered. Power supply to PDM PC shall have protection against surges, overload and short circuit. A dedicated on-line UPS system shall also be provided as a backup during supply interruption, to ensure trouble-free & reliable running of the PDM System for a minimum of 15 minutes duration. | SET | 1 | 1 | 0 | 1 | 0 | 48414191.5425 |  | 48414191.5425 | 8714554.4776 | 57128746.0201 | 48414191.5425 | 0 | 48414191.5425 | 8714554.4776 | 57128746.0201 | 0 |  | GIS 400kV | A
2 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | GIS 220kV | A
2.1 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T ) SF6 gas insulated ICT feeder bay module each comprising of SF6 gas insulated, Single Phase Busbar, circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete ICT feeder bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 12076427.8739 |  | 24152855.7477 | 4347514.0346 | 28500369.7823 | 24152855.7477 | 0 | 24152855.7477 | 4347514.0346 | 28500369.7823 | 0 |  | GIS 220kV | A
2.2 | 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated, Single Phase Busbar, circuit breaker, current transformer,Line Potential Transformer (3 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement,PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 4 | 4 | 0 | 4 | 0 | 11481324.6087 |  | 45925298.4348 | 8266553.7183 | 54191852.153 | 45925298.4348 | 0 | 45925298.4348 | 8266553.7183 | 54191852.153 | 0 |  | GIS 220kV | A
2.3 | 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), dis connectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 6196882.8399 |  | 12393765.6797 | 2230877.8224 | 14624643.5021 | 12393765.6797 | 0 | 12393765.6797 | 2230877.8224 | 14624643.5021 | 0 |  | GIS 220kV | A
2.4 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated,Single Phase Busbar, circuit breaker, current transformer, dis connectors switches, disconnector with safety grounding switch(es). Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Bus Coupler bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 1 | 1 | 0 | 1 | 0 | 11724776.1708 |  | 11724776.1708 | 2110459.7108 | 13835235.8816 | 11724776.1708 | 0 | 11724776.1708 | 2110459.7108 | 13835235.8816 | 0 |  | GIS 220kV | A
2.5 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed] outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. (The GIBus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 750 | 1000 | 250 | 937 | 63 | 43709.1793 | 43709.1793 | 32781884.4703 | 5900739.2047 | 38682623.6749 | 40955500.9982 | 2753678.2955 | 43709179.2937 | 7867652.2729 | 51576831.5666 | 12894207.8916 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Cost Data Rate for 220kV GIS not available. Hence, BoQ rate considered. | GIS 220kV | B
2.6 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462) FOR CONNECTING GIS TO AIS along with support structure. | NO | 18 | 18 | 0 | 18 | 0 | 293042.7538 |  | 5274769.5689 | 949458.5224 | 6224228.0913 | 5274769.5689 | 0 | 5274769.5689 | 949458.5224 | 6224228.0913 | 0 |  | GIS 220kV | A
3 | 420KV 1 phase Solid core bus post insulator (AIS) as per technical specification. | NOS | 16 | 21 | 5 | 20 | 1 | 53512.8653 | 53512.8653 | 856205.845 | 154117.0521 | 1010322.8971 | 1070257.3063 | 53512.8653 | 1123770.1716 | 202278.6309 | 1326048.8025 | 315725.9054 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Cost Data Rate for 400kV BPI not available. Hence, BoQ rate considered | Pos Insulator | B
4 | 245KV 1 phase Solid core bus post insulator (AIS) as per technical specification. | NOS | 24 | 18 | -6 | 18 | 0 | 26462.5811 | 0 | 635101.9456 | 114318.3502 | 749420.2958 | 476326.4592 | 0 | 476326.4592 | 85738.7626 | 562065.2218 | -187355.0739 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | Pos Insulator | B
5 | 390KV metal oxide polymer housed surge arrrestor, 20 KA , Long duration discharge class IV ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 24 | 15 | -9 | 15 | 0 | 216754.8959 | 0 | 5202117.5019 | 936381.1503 | 6138498.6523 | 3251323.4387 | 0 | 3251323.4387 | 585238.219 | 3836561.6577 | -2301936.9946 | Revised qty as per approved SLD (Drg. No. TB-3-420-510-001) | Surge Arrestor | B
6 | 216KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 216KV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 18 | 18 | 0 | 18 | 0 | 81092.0824 |  | 1459657.4838 | 262738.3471 | 1722395.8309 | 1459657.4838 | 0 | 1459657.4838 | 262738.3471 | 1722395.8309 | 0 |  | Surge Arrestor | A
7 | 30KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 30kV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 12 | 12 | 0 | 12 | 0 | 26109.9592 |  | 313319.5098 | 56397.5118 | 369717.0216 | 313319.5098 | 0 | 313319.5098 | 56397.5118 | 369717.0216 | 0 |  | Surge Arrestor | A
8 | 36 KV ,1250A, 31.5 KA for 1 sec, isolator (single isolator with earth switch) including post insulators as per technical specification | SET | 2 | 0 | -2 | 0 | 0 | 107083.5048 | 0 | 214167.0097 | 38550.0617 | 252717.0714 | 0 | 0 | 0 | 0 | 0 | -252717.0714 | 33kV Isolator with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | Isolator | B
9 | 36 KV,1250 A,31.5 KA 3 Sec,Vacuum Circuit Breaker with supporting GI structures as per technical specification. | SET | 2 | 0 | -2 | 0 | 0 | 489173.2524 | 0 | 978346.5047 | 176102.3708 | 1154448.8756 | 0 | 0 | 0 | 0 | 0 | -1154448.8756 | 33kV SF6 Circuit Breaker with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | Circuit Breaker | B
10 | 36 KV , 31.5 KA for 1 sec ,1200-600/1-1-1-1 A, Current Transformer as per technical specification | Nos | 6 | 0 | -6 | 0 | 0 | 56453.3735 | 0 | 338720.2407 | 60969.6433 | 399689.8841 | 0 | 0 | 0 | 0 | 0 | -399689.8841 | 33kV CT with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | Current Transformer (CT) | B
11 | 36 KV , 31.5 KA for 1 sec , 50-25/1-1 A, Current Transformer as per technical specification | Nos | 6 | 0 | -6 | 0 | 0 | 37635.9143 | 0 | 225815.486 | 40646.7875 | 266462.2735 | 0 | 0 | 0 | 0 | 0 | -266462.2735 | 33kV CT with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | Current Transformer (CT) | B
11.1 | CT Console Box for above 36 KV CTs | Nos | 4 | 4 | 0 | 4 | 0 | 29873.2518 |  | 119493.007 | 21508.7413 | 141001.7483 | 119493.007 | 0 | 119493.007 | 21508.7413 | 141001.7483 | 0 |  | Current Transformer (CT) | A
12 | 36 KV Bus Post Insulator as per technical specification | Nos | 12 | 0 | -12 | 0 | 0 | 3351.9004 | 0 | 40222.8045 | 7240.1048 | 47462.9093 | 0 | 0 | 0 | 0 | 0 | -47462.9093 | 33kV Post Insulator with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | Pos Insulator | B
13 | All type of Terminal clamp & connectors suitable for 36 KV, 1250 A for station transformers. | LOT | 1 | 1 | 0 | 1 | 0 | 56453.3735 |  | 56453.3735 | 10161.6072 | 66614.9807 | 56453.3735 | 0 | 56453.3735 | 10161.6072 | 66614.9807 | 0 |  |  | A
14 | BUS BAR & CIRCUIT MATERIALS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
14.1 | 160 KN LR Antifog Porcelain INSULATOR STRINGS (SUSPENSION & TENSION) 400 KV side suitable for the arrangement as expalined below. Brief description regarding use: (a) Provision of suspension insulators to hold the Quad conductor arrangement from the other end of Aluminium tube to 400 KV gantry for 400 KV line feeder. | SET | 12 | 33 | 21 | 15 | 18 | 93064.2936 | 93064.2936 | 1116771.5232 | 201018.8742 | 1317790.3973 | 1395964.404 | 1675157.2848 | 3071121.6887 | 552801.904 | 3623923.5927 | 2306133.1953 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Cost Data Rate for 160kN LR AF Porcelain insulator not available. Hence, BoQ rate considered. | String Insulator | B
14.2 | 160 KN LR Antifog Porcelain INSULATOR STRINGS for Single Suspension Single/ Moose cond (SUSPENSION & TENSION) 245 KV side for the arrangement as explained below. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | String Insulator | A
14.2.1 | (a) Provision of suspension insulators to hold the single conductor arrangement from the other end of the Aluminium tube to 220 KV gantry for 220 KV line feeder.=12 sets | SET | 12 | 12 | 0 | 12 | 0 | 28632.1023 |  | 343585.2278 | 61845.341 | 405430.5688 | 343585.2278 | 0 | 343585.2278 | 61845.341 | 405430.5688 | 0 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | String Insulator | A
14.2.2 | (b) Provision of suspension insulators to hold the Quad conductor arrangement from other end of Aluminium tube to 220 KV gantry both side of the road near ICT 220 KV side for 220 KV ICT feeder.= 12 sets | SET | 12 | 0 | -12 | 0 | 0 | 45144.5696 | 0 | 541734.8354 | 97512.2704 | 639247.1058 | 0 | 0 | 0 | 0 | 0 | -639247.1058 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | String Insulator | B
14.2.3 | (c) Provision of tension insulators for holding the Quad conductor arrangement from 220 KV gantry near the ICT to cross the road & to other end gantry for 220 KV ICT feeder.=12 sets. | SET | 12 | 0 | -12 | 0 | 0 | 58475.4709 | 0 | 701705.6503 | 126307.0171 | 828012.6674 | 0 | 0 | 0 | 0 | 0 | -828012.6674 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | String Insulator | B
14.3 | ACSR MOOSE CONDUCTOR | Mtrs | 1500 | 3600 | 2100 | 1875 | 1725 | 465.182 | 409.923 | 697773.0195 | 125599.1435 | 823372.163 | 872216.2744 | 707117.175 | 1579333.4494 | 284280.0209 | 1863613.4702 | 1040241.3072 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Latest Cost Data Rate for ACSR Moose conductor lower than BoQ rate, hence considered. | Overhead Conductor | B
14.4 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. Brief description regarding use: (a) Upto the 400 KV Gantry from SF6 to Air Bushing for 400 KV Line. (b) Upto 400 KV SA near ICT from SF6 to Air Bushing for ICT. (c) Upto the 220 KV Gantry from SF6 to Air Bushing for 220 KV side of ICT. (d) Upto the 220 KV Gantry from SF6 to Air Bushing for 220 KV Line. | MTR | 650 | 650 | 0 | 650 | 0 | 3633.7987 |  | 2361969.1418 | 425154.4455 | 2787123.5873 | 2361969.1418 | 0 | 2361969.1418 | 425154.4455 | 2787123.5873 | 0 |  | Aliminium Tube | A
14.5 | All types of HARDWARES & FITTINGS/SPACERS/CLAMPS & CONNECTORS FOR 400KV SIDE OF THE GIS S/S. | Lot | 1 | 1 | 0 | 1 | 0 | 999777.7488 |  | 999777.7488 | 179959.9948 | 1179737.7436 | 999777.7488 | 0 | 999777.7488 | 179959.9948 | 1179737.7436 | 0 |  |  | A
14.6 | All types of HARDWARES & FITTINGS/SPACERS/CLAMPS & CONNECTORS FOR 220 KV SIDE OF THE GIS S/S. | Lot | 1 | 1 | 0 | 1 | 0 | 668014.3201 |  | 668014.3201 | 120242.5776 | 788256.8977 | 668014.3201 | 0 | 668014.3201 | 120242.5776 | 788256.8977 | 0 |  |  | A
15 | SUBSTATION EARTHING SYSTEMS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
15.1 | EARTHING CONDUCTOR FOR BURRIAL & RAISER FROM MAT UPTO THE REQUIRED HEIGHT BELOW GROUND : 40 mm MS Rod for laying (Mat spacing maximum 5m both way) | Mtrs | 7500 | 35000 | 27500 | 9375 | 25625 | 615.5942 | 615.5942 | 4616956.3816 | 831052.1487 | 5448008.5303 | 5771195.4771 | 15774600.9706 | 21545796.4477 | 3878243.3606 | 25424039.8082 | 19976031.2779 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) Latest Cost Data rate for substation structures higher than BoQ rate. So BoQ rate considered. | MS Rod | B
15.2 | EARTHING CONDUCTOR: 75X 10 mm GI (HDG) Flat for Raiser from the burial earth mat to equipment,structure etc) | Mtrs | 1500 | 5300 | 3800 | 1875 | 3425 | 467.1742 | 467.1742 | 700761.3408 | 126137.0413 | 826898.3821 | 875951.676 | 1600071.7281 | 2476023.4041 | 445684.2127 | 2921707.6168 | 2094809.2347 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) Rate Contract 2023 Sl. No. 21.1 vi(a-b) rate is higher than BoQ rate. Hence BoQ Rate is considered. |  | B
15.3 | EARTHING CONDUCTOR: 50X6mm GI (HDG) Flat for Raiser for console box,LT panels,DC panels,Marshalling boxes,cable trench etc) | Mtrs | 750 | 8900 | 8150 | 937 | 7963 | 190.2565 | 190.2565 | 142692.3412 | 25684.6214 | 168376.9627 | 178270.2983 | 1515012.1511 | 1693282.4494 | 304790.8409 | 1998073.2903 | 1829696.3277 | Revised qty as per proposed Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) Rate Contract 2020-21 Sl. No. 21.1 v(a-b) rate is higher than BoQ rate. Hence BoQ Rate is considered. |  | B
15.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos | 150 | 380 | 230 | 187 | 193 | 6174.8679 | 3675.65 | 926230.1815 | 166721.4327 | 1092951.6142 | 1154700.293 | 709400.45 | 1864100.743 | 335538.1337 | 2199638.8767 | 1106687.2625 | Revised qty as per proposed Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) Rate Contract 2023 Sl. No. 21.3 (i-ii) rate is lower than BoQ rate. Hence RC Rate is considered. |  | B
15.5 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | Nos | 100 | 0 | -100 | 0 | 0 | 1844.7903 | 0 | 184479.0338 | 33206.2261 | 217685.2599 | 0 | 0 | 0 | 0 | 0 | -217685.2599 |  |  | B
15.6 | 100sqmm copper braid for gate earthing. | Lot | 1 | 1 | 0 | 1 | 0 | 31989.9793 |  | 31989.9793 | 5758.1963 | 37748.1756 | 31989.9793 | 0 | 31989.9793 | 5758.1963 | 37748.1756 | 0 |  |  | A
16 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained. |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
16.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 1500 | 4875 | 3375 | 1875 | 3000 | 3701.534 | 3701.534 | 5552300.9431 | 999414.1698 | 6551715.1129 | 6940376.1789 | 11104601.8862 | 18044978.0651 | 3248096.0517 | 21293074.1168 | 14741359.0039 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) |  | B
16.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 1250 | 1750 | 500 | 1562 | 188 | 2847.8702 | 2847.8702 | 3559837.7279 | 640770.791 | 4200608.5189 | 4448373.2248 | 535399.5943 | 4983772.8191 | 897079.1074 | 5880851.9265 | 1680243.4076 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) |  | B
16.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 1000 | 250 | -750 | 250 | 0 | 1993.2103 | 0 | 1993210.2955 | 358777.8532 | 2351988.1487 | 498302.5739 | 0 | 498302.5739 | 89694.4633 | 587997.0372 | -1763991.1115 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) |  | B
16.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 5 | 13.3 | 8.3 | 6 | 7.3 | 89336.8609 | 89336.8609 | 446684.3043 | 80403.1748 | 527087.479 | 536021.1651 | 652159.0842 | 1188180.2493 | 213872.4449 | 1402052.6942 | 874965.2152 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) Latest Cost Data rate for substation structures higher than BoQ rate. So BoQ rate considered.. |  | B
17 | SWITCH YARD AC CONSOLE (Al alloy box painted with enamel gray colour) FOR LIGHTING (01 nos each on 400KV side & 220 kv side and other area ) as per Technical Specification. | NOS | 3 | 3 | 0 | 3 | 0 | 19711.9633 |  | 59135.8899 | 10644.4602 | 69780.35 | 59135.8899 | 0 | 59135.8899 | 10644.4602 | 69780.35 | 0 |  |  | A
18 | SWITCH YARD RECEPTACLE BOARD (Al alloy box painted with enamel gray colour) FOR TFR OIL FILTERATION (01 no. near 400/220KV ICT) as per Technical Specification. | NOS | 1 | 1 | 0 | 1 | 0 | 32836.6704 |  | 32836.6704 | 5910.6007 | 38747.271 | 32836.6704 | 0 | 32836.6704 | 5910.6007 | 38747.271 | 0 |  |  | A
19 | SWITCH YARD RECEPTACLE BOARD (Al alloy box painted with enamel gray colour) FOR WELDING & OTHER EMERGENCY as per Technical Specification. | NOS | 1 | 1 | 0 | 1 | 0 | 11761.0365 |  | 11761.0365 | 2116.9866 | 13878.023 | 11761.0365 | 0 | 11761.0365 | 2116.9866 | 13878.023 | 0 |  |  | A
20 | HDG SWITCH YARD STRUCTURES (INCLUDING FOUNDATION BOLTS) FOR 400Kv & 220KV CLASS (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
20.1 | DIFFERENT TYPES OF LATICE TYPE COLUMNS & DIFFERENT TYPE OF BEAMS AND LIGHTING CUM LIGHTNING MAST.(Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Lattice Structure | A
20.1.1 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 52 | 186.2 | 134.2 | 65 | 121.2 | 97167.2587 | 97167.2587 | 5052697.4534 | 909485.5416 | 5962182.995 | 6315871.8167 | 11776671.7567 | 18092543.5734 | 3256657.8432 | 21349201.4166 | 15387018.4216 | No. of towers & beams as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) BoQ rate considered for higher Zinc galvanization of 910 gms/sqmm instead of 610 gsm/sqmm as per TS. | Lattice Structure | B
20.2 | DIFFERENT TYPE OF SUPPORT STRUCTURES (HDG) OF PIPE TYPE FOR ALL 400KV, 220KV & 33 KV EQUIPMENT INCLUDING HIGH LEVEL SA NEAR TRANSFORMER. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Lattice Structure | A
20.2.1 | TOTAL WEIGHT OF PIPE TYPE SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 55 | 55 | 0 | 55 | 0 | 101110.8467 |  | 5561096.5687 | 1000997.3824 | 6562093.9511 | 5561096.5687 | 0 | 5561096.5687 | 1000997.3824 | 6562093.9511 | 0 |  | Lattice Structure | A
20.2.2 | 40 Mtrs heigh Monopole Lighting cum Lightning Mast including LED lighting fixtures with control gear panel etc suitable for wind zone-VI. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). The lights to be controlled by lux meter for variable lux output of the luminaire as per ambient light. | Nos | 3 | 3 | 0 | 3 | 0 | 1580670.5502 |  | 4742011.6507 | 853562.0971 | 5595573.7478 | 4742011.6507 | 0 | 4742011.6507 | 853562.0971 | 5595573.7478 | 0 |  | Lattice Structure | A
21 | Total weight of different type of GI Nuts and bolts for the above structures. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). | MT | 5.6 | 9 | 3.4 | 7 | 2 | 119981.0995 | 119981.0995 | 671894.1572 | 120940.9483 | 792835.1055 | 839867.6965 | 239962.199 | 1079829.8955 | 194369.3812 | 1274199.2767 | 481364.1712 | No. of towers & beams as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) BoQ rate considered for higher Zinc galvanization of 910 gms/sqmm instead of 610 gsm/sqmm as per TS. | Lattice Structure | B
22 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
22.1 | POWER CABLES,1.1KV,XLPE & PVC FRLS ,FLAT STRIP ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Cable | A
22.1.1 | XLPE-1CX 630 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 718.1932 |  | 2154579.6448 | 387824.3361 | 2542403.9808 | 2154579.6448 | 0 | 2154579.6448 | 387824.3361 | 2542403.9808 | 0 |  | Cable | A
22.1.2 | XLPE-1CX 300 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 347.6414 |  | 347641.3759 | 62575.4477 | 410216.8235 | 347641.3759 | 0 | 347641.3759 | 62575.4477 | 410216.8235 | 0 |  | Cable | A
22.1.3 | XLPE-3.5 CX185 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 1097.71 |  | 548855.0089 | 98793.9016 | 647648.9105 | 548855.0089 | 0 | 548855.0089 | 98793.9016 | 647648.9105 | 0 |  | Cable | A
22.1.4 | XLPE-3.5 CX120 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 531.9212 |  | 265960.5942 | 47872.9069 | 313833.5011 | 265960.5942 | 0 | 265960.5942 | 47872.9069 | 313833.5011 | 0 |  | Cable | A
22.1.5 | PVC-3.5 CX70 mm2 | Mtrs | 250 | 250 | 0 | 250 | 0 | 421.3533 |  | 105338.3252 | 18960.8985 | 124299.2238 | 105338.3252 | 0 | 105338.3252 | 18960.8985 | 124299.2238 | 0 |  | Cable | A
22.1.6 | PVC-3.5 CX35 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 206.1942 |  | 103097.0843 | 18557.4752 | 121654.5594 | 103097.0843 | 0 | 103097.0843 | 18557.4752 | 121654.5594 | 0 |  | Cable | A
22.1.7 | PVC-4 CX 16 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 153.4005 |  | 153400.4925 | 27612.0887 | 181012.5812 | 153400.4925 | 0 | 153400.4925 | 27612.0887 | 181012.5812 | 0 |  | Cable | A
22.1.8 | PVC-4 CX 6 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 143.4394 |  | 143439.4216 | 25819.0959 | 169258.5174 | 143439.4216 | 0 | 143439.4216 | 25819.0959 | 169258.5174 | 0 |  | Cable | A
22.1.9 | PVC-2CX 6 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 71.7197 |  | 143439.4216 | 25819.0959 | 169258.5174 | 143439.4216 | 0 | 143439.4216 | 25819.0959 | 169258.5174 | 0 |  | Cable | A
22.2 | CONTROL CABLES,1.1 KV,PVC FRLS , COPPER STRANDED ARMOURED STRANDED(As per specification). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Cable | A
22.2.1 | 2 CX 2.5 mm2 | Mtrs | 2500 | 2500 | 0 | 2500 | 0 | 103.5951 |  | 258987.8445 | 46617.812 | 305605.6565 | 258987.8445 | 0 | 258987.8445 | 46617.812 | 305605.6565 | 0 |  | Cable | A
22.2.2 | 4 CX 4 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 219.1436 |  | 438287.1215 | 78891.6819 | 517178.8033 | 438287.1215 | 0 | 438287.1215 | 78891.6819 | 517178.8033 | 0 |  | Cable | A
22.2.3 | 4 CX 2.5 mm2 | Mtrs | 6000 | 6000 | 0 | 6000 | 0 | 171.3304 |  | 1027982.5212 | 185036.8538 | 1213019.375 | 1027982.5212 | 0 | 1027982.5212 | 185036.8538 | 1213019.375 | 0 |  | Cable | A
22.2.4 | 5 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 184.2798 |  | 737119.2497 | 132681.4649 | 869800.7147 | 737119.2497 | 0 | 737119.2497 | 132681.4649 | 869800.7147 | 0 |  | Cable | A
22.2.5 | 7CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 238.0696 |  | 952278.3821 | 171410.1088 | 1123688.4908 | 952278.3821 | 0 | 952278.3821 | 171410.1088 | 1123688.4908 | 0 |  | Cable | A
22.2.6 | 10 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 314.7698 |  | 1259079.3671 | 226634.2861 | 1485713.6531 | 1259079.3671 | 0 | 1259079.3671 | 226634.2861 | 1485713.6531 | 0 |  | Cable | A
22.2.7 | 12 CX 2.5 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 397.4467 |  | 794893.4612 | 143080.823 | 937974.2842 | 794893.4612 | 0 | 794893.4612 | 143080.823 | 937974.2842 | 0 |  | Cable | A
22.2.8 | 16 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 473.1509 |  | 1892603.479 | 340668.6262 | 2233272.1052 | 1892603.479 | 0 | 1892603.479 | 340668.6262 | 2233272.1052 | 0 |  | Cable | A
22.2.9 | 19 CX 2.5 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 562.8005 |  | 1688401.5247 | 303912.2744 | 1992313.7991 | 1688401.5247 | 0 | 1688401.5247 | 303912.2744 | 1992313.7991 | 0 |  | Cable | A
22.2.10 | 27 CX 2.5 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 741.1037 |  | 2223311.0343 | 400195.9862 | 2623507.0204 | 2223311.0343 | 0 | 2223311.0343 | 400195.9862 | 2623507.0204 | 0 |  | Cable | A
22.2.11 | 1CX 150 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 300 | 300 | 0 | 300 | 0 | 206.1942 |  | 61858.2506 | 11134.4851 | 72992.7356 | 61858.2506 | 0 | 61858.2506 | 11134.4851 | 72992.7356 | 0 |  |  | A
22.3 | Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building,GIS Building etc as per TS | LOT | 1 | 1 | 0 | 1 | 0 | 1146691.592 |  | 1146691.592 | 206404.4866 | 1353096.0785 | 1146691.592 | 0 | 1146691.592 | 206404.4866 | 1353096.0785 | 0 |  |  | A
23 | HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better & ITS ACCESSORIES LIKE ALL TYPE OF SOCKETS & BENDS FOR TAKING CABLE FROM TRENCH TO EQUIPMENT MB etc | LOT | 1 | 1 | 0 | 1 | 0 | 2035583.6952 |  | 2035583.6952 | 366405.0651 | 2401988.7603 | 2035583.6952 | 0 | 2035583.6952 | 366405.0651 | 2401988.7603 | 0 |  |  | A
24 | SUPPLY OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION AS PER TECHNICAL SPECIFICATION |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Station Transformer | A
24.1 | STATION TRANSFORMER 33KV/433V,1000 KVA (AS PER SPECIFICATION) | NOS | 2 | 2 | 0 | 2 | 0 | 2212232.3312 |  | 4424464.6623 | 796403.6392 | 5220868.3015 | 4424464.6623 | 0 | 4424464.6623 | 796403.6392 | 5220868.3015 | 0 |  | Station Transformer | A
24.2 | OUT DOOR KIOSK MADE OUT OF 3mm thick Al alloy box painted with enamel gray colour having gland plates OR BETTER quality WITH 3 NOS. OF CUT-OUTS(1000 AMPS) AT THE INCOMING SIDE , 1No. OF 3 PHASE SFU (500/1000 AMPS) AT THE OUTGOING SIDE AND SUITABLE BUS BAR ARRANGEMENT FOR TERMINATION of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 2 | 0 | 2 | 0 | 90136.7348 |  | 180273.4697 | 32449.2245 | 212722.6942 | 180273.4697 | 0 | 180273.4697 | 32449.2245 | 212722.6942 | 0 |  |  | A
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area)(Including provision of the fittings on the LM).The switchyard lights to be controlled by lux meter for variable lux output of the luminaire as per ambient light. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Illumination | A
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | SET | 40 | 40 | 0 | 40 | 0 | 61135.0768 |  | 2445403.072 | 440172.553 | 2885575.6249 | 2445403.072 | 0 | 2445403.072 | 440172.553 | 2885575.6249 | 0 |  | Illumination | A
26 | STREET LIGHTING: IT INCLUDES SUPPLY OF GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). (GI Tubular pole shall have Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Illumination | A
26.1 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | SET | 40 | 40 | 0 | 40 | 0 | 9362.4106 |  | 374496.4231 | 67409.3562 | 441905.7793 | 374496.4231 | 0 | 374496.4231 | 67409.3562 | 441905.7793 | 0 |  | Illumination | A
26.2 | GI Tubular Pole: (410-SP-24: IS 2713-Part-II-1980 or latest) Length of pole 8.5 mtrs(minimum weight 158 Kgs). (GI Tubular pole shall have Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). (ALL THE STREET LIGHT POLE SHALL BE OF GI TUBULAR POLE AND PROVISION OF A GI JUNCTION BOX WITH SUITABLE COVERS AT A HEIGHT OF 1 METRE FROM THE GROUND. THE JUNCTION BOX SHALL HAVE PROVISION OF FUSES, BUSES, CONNECTORS FOR CABLE IN AND OUT. | SET | 40 | 40 | 0 | 40 | 0 | 26668.7752 |  | 1066751.0093 | 192015.1817 | 1258766.191 | 1066751.0093 | 0 | 1066751.0093 | 192015.1817 | 1258766.191 | 0 |  | Illumination | A
26.3 | (a) OUTDOOR KIOSK of 3 mm thick Al alloy box painted with enamel gray colour FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB.(1 No.) (b) OUTDOOR KIOSK of 3 mm thick Al alloy box painted with enamel gray colour for colony power supply with 200A SFU & ten out-going feeder of 32A rating fitted with MCB. (1 No.) | NO | 2 | 2 | 0 | 2 | 0 | 99263.068 |  | 198526.1361 | 35734.7045 | 234260.8406 | 198526.1361 | 0 | 198526.1361 | 35734.7045 | 234260.8406 | 0 |  | Illumination | A
27 | INDOOR LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS ) (GIS, Control room building,Store shed,store room,Security room cum Visitors room and other area) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Illumination | A
27.1 | 400KV GIS BUILDING INDOOR LIGHTING, IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 1876858.0142 |  | 1876858.0142 | 337834.4425 | 2214692.4567 | 2627601.2198 | 0 | 2627601.2198 | 472968.2196 | 3100569.4394 | 885876.9827 | Size of 400kV GIS Building increased by 40% as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A). Building dimensions changed from 55m x 15.5m to 77m x 15.5m. Unit Rate to be increased by 40% on pro rata basis against the change in LOT quantity. | Illumination | B
27.2 | 220KV GIS BUILDING INDOOR LIGHTING, IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 1651942.0128 |  | 1651942.0128 | 297349.5623 | 1949291.5751 | 3023053.8835 | 0 | 3023053.8835 | 544149.699 | 3567203.5825 | 1617912.0074 | Size of 220kV GIS Building increased by 83% as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A). Building dimensions changed from 23.5m x 12m to 43m x 12m. Unit Rate to be increased by 83% on pro rata basis against the change in LOT quantity. | Illumination | B
27.3 | CONTROL ROOM BUILDING INDOOR LIGHTING, IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 4471965.0252 |  | 4471965.0252 | 804953.7045 | 5276918.7298 | 4471965.0252 | 0 | 4471965.0252 | 804953.7045 | 5276918.7298 | 0 |  | Illumination | A
27.4 | INDOOR LIGHTING OF SECURITY SHED CUM VISITORS ROOM,PUMP HOUSE,STORE SHED,STORE ROOM, FFPH BUILDING, DG SET BUILDING, PARKING SHED: IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 1053258.7387 |  | 1053258.7387 | 189586.573 | 1242845.3117 | 1053258.7387 | 0 | 1053258.7387 | 189586.573 | 1242845.3117 | 0 |  | Illumination | A
27.5 | INDOOR LIGHTING OF D type & E type quarter: IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 836515.7961 |  | 836515.7961 | 150572.8433 | 987088.6394 | 836515.7961 | 0 | 836515.7961 | 150572.8433 | 987088.6394 | 0 |  | Illumination | A
28 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS (5 star Inverter type) WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR CONTROL ROOM, CARRIER ROOM & CONFERENCE ROOM.,OFFICE ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. (Note: considering the AC unit shall run continuously therefore provision shall be there for stand by AC unit. The calculation of nos. of AC units along with stand by as required shall be based on standard code of practice & the unit shall be as per IS 1391 (Part 2): 2018 and its latest). | LOT | 1 | 1 | 0 | 1 | 0 | 1883700.2738 |  | 1883700.2738 | 339066.0493 | 2222766.3231 | 1883700.2738 | 0 | 1883700.2738 | 339066.0493 | 2222766.3231 | 0 |  | Air Conditioning | A
29 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS (5 star Inverter type) WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR 400KV GIS HALL LCC ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. (Note: considering the AC unit shall run continuously therefore provision shall be there for stan by AC unit. The calculation of nos. of AC units along with stand by as required shall be based on standard code of practice & the unit shall be as per IS 1391 (Part 2): 2018 and its latest). | LOT | 1 | 1 | 0 | 1 | 0 | 941850.1369 |  | 941850.1369 | 169533.0246 | 1111383.1615 | 941850.1369 | 0 | 941850.1369 | 169533.0246 | 1111383.1615 | 0 |  | Air Conditioning | A
30 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS (5 star Inverter type) WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR 220KV GIS HALL LCC ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. (Note: considering the AC unit shall run continuously therefore provision shall be there for stan by AC unit. The calculation of nos. of AC units along with stand by as required shall be based on standard code of practice & the unit shall be as per IS 1391 (Part 2): 2018 and its latest). | LOT | 1 | 1 | 0 | 1 | 0 | 502320.8699 |  | 502320.8699 | 90417.7566 | 592738.6265 | 502320.8699 | 0 | 502320.8699 | 90417.7566 | 592738.6265 | 0 |  | Air Conditioning | A
31 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTEDFIRE EXTINGUSHERS SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE - I) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Fire Fighting System | A
31.1 | FOAM TYPE-9 LTRS | NOS | 4 | 4 | 0 | 4 | 0 | 4008.3349 |  | 16033.3398 | 2886.0012 | 18919.341 | 16033.3398 | 0 | 16033.3398 | 2886.0012 | 18919.341 | 0 |  | Fire Fighting System | A
31.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 6 | 6 | 0 | 6 | 0 | 17002.552 |  | 102015.3119 | 18362.7562 | 120378.0681 | 102015.3119 | 0 | 102015.3119 | 18362.7562 | 120378.0681 | 0 |  | Fire Fighting System | A
31.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 6 | 0 | 6 | 0 | 5580.1919 |  | 33481.1517 | 6026.6073 | 39507.7589 | 33481.1517 | 0 | 33481.1517 | 6026.6073 | 39507.7589 | 0 |  | Fire Fighting System | A
31.4 | CO2 - 4.5 KGS | NOS | 10 | 10 | 0 | 10 | 0 | 6186.8212 |  | 61868.2116 | 11136.2781 | 73004.4897 | 61868.2116 | 0 | 61868.2116 | 11136.2781 | 73004.4897 | 0 |  | Fire Fighting System | A
31.5 | CO2 - 9 KGS | NOS | 10 | 10 | 0 | 10 | 0 | 13028.0847 |  | 130280.8469 | 23450.5524 | 153731.3993 | 130280.8469 | 0 | 130280.8469 | 23450.5524 | 153731.3993 | 0 |  | Fire Fighting System | A
31.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 4 | 0 | 4 | 0 | 26132.8696 |  | 104531.4785 | 18815.6661 | 123347.1446 | 104531.4785 | 0 | 104531.4785 | 18815.6661 | 123347.1446 | 0 |  | Fire Fighting System | A
31.7 | 9 litre water type | Nos. | 4 | 4 | 0 | 4 | 0 | 14810.1203 |  | 59240.4811 | 10663.2866 | 69903.7677 | 59240.4811 | 0 | 59240.4811 | 10663.2866 | 69903.7677 | 0 |  | Fire Fighting System | A
31.8 | 4.5 kg DCP type | Nos. | 4 | 4 | 0 | 4 | 0 | 5021.3759 |  | 20085.5034 | 3615.3906 | 23700.8941 | 20085.5034 | 0 | 20085.5034 | 3615.3906 | 23700.8941 | 0 |  | Fire Fighting System | A
31.9 | 50 Litres Mechanical Foam type | Nos. | 2 | 2 | 0 | 2 | 0 | 40135.147 |  | 80270.2941 | 14448.6529 | 94718.947 | 80270.2941 | 0 | 80270.2941 | 14448.6529 | 94718.947 | 0 |  | Fire Fighting System | A
31.1 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 5 | 5 | 0 | 5 | 0 | 17642.0527 |  | 88210.2637 | 15877.8475 | 104088.1112 | 88210.2637 | 0 | 88210.2637 | 15877.8475 | 104088.1112 | 0 |  | Fire Fighting System | A
32 | SUBSTATION AUTOMATION SYSTEM FOR 400/220 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 400, 220, 132 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.1 | Gate way panel for Sub-Station Automation (in PRP as per the specification & indicative drg ) system (for All 400 , 220 & 33 KV side bays including the future bays),other accessories (comprising servers, engg. Station, works station (Main & standby), Remote station control, Colour Laser jet Printers & dot matrix printer for local station as per requirement and also for remote station, Ethernet Switches , LIU, Red Box, Multimode glass fibre Doublle jacket armoured optical cables, special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system in all respect as per latest IEC 61850 standard, Inverters of required capacity & rating (Input shall be both A.C & D.C and output shall be A.C) etc as per TS. A large vedio screen of 67 inches or more for display including all type of accessories & as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 6857659.4458 |  | 6857659.4458 | 1234378.7002 | 8092038.146 | 6857659.4458 | 0 | 6857659.4458 | 1234378.7002 | 8092038.146 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.2 | BCU for Substation Auxilliary System (Station,AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) | SET | 1 | 1 | 0 | 1 | 0 | 353535.3416 |  | 353535.3416 | 63636.3615 | 417171.703 | 353535.3416 | 0 | 353535.3416 | 63636.3615 | 417171.703 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) for substation automation system. | NOS | 2 | 2 | 0 | 2 | 0 | 1160427.9088 |  | 2320855.8176 | 417754.0472 | 2738609.8647 | 2320855.8176 | 0 | 2320855.8176 | 417754.0472 | 2738609.8647 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3.2 | TRANSFORMER PROTECTION PANEL (DIFFERENTIAL I &II , REF I & II & BACK-UP PROTECTION for HV & IV side CONSIDERING HV ,IV & LV side for 500 MVA 400/220/33 KV ICT) with Bay control units (BCU) for substation automation system. | SET | 2 | 2 | 0 | 2 | 0 | 1603960.5302 |  | 3207921.0604 | 577425.7909 | 3785346.8513 | 3207921.0604 | 0 | 3207921.0604 | 577425.7909 | 3785346.8513 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3.3 | TIE BREAKER PROTECTION PANEL with Bay control unit (BCU) for substation automation system. | NOS | 3 | 3 | 0 | 3 | 0 | 602848.9939 |  | 1808546.9818 | 325538.4567 | 2134085.4386 | 1808546.9818 | 0 | 1808546.9818 | 325538.4567 | 2134085.4386 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3.4 | BUS-BAR PROTECTION PANEL ( Provision of bus bar modules for the future bays and to be integrated with the Automation system) | NOS | 1 | 1 | 0 | 1 | 0 | 2545120.3649 |  | 2545120.3649 | 458121.6657 | 3003242.0305 | 2545120.3649 | 0 | 2545120.3649 | 458121.6657 | 3003242.0305 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
32.3.5 | REACTOR PROTECTION PANEL for 125MVAR Bus Reactor with Bay Control Unit (BCU) for Substation Automation System as per Technical Specification | NOS | 1 | 2 | 1 | 1 | 1 | 1305874.4861 | 1305874.4861 | 1305874.4861 | 235057.4075 | 1540931.8937 | 1305874.4861 | 1305874.4861 | 2611748.9723 | 470114.815 | 3081863.7873 | 1540931.8937 | Additional panel for one no. equipped GIS Bay for future Reactor added as per the approved SLD (Drg. No. TB-3-420-510-001) Cost Data rate not avaialable, so, BoQ rate considered. | SUBSTATION AUTOMATION SYSTEM (SAS) | B
32.4 | 220 KV SIDE PROTECTION & OTHER PANELS |  |  |  | 0 | 0 | 0 | [6 empty] | 0 | [6 empty] | A
32.4.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) for substation automation system. | NOS | 4 | 4 | 0 | 4 | 0 | 1081618.9038 |  | 4326475.6153 | 778765.6107 | 5105241.226 | 4326475.6153 | 0 | 4326475.6153 | 778765.6107 | 5105241.226 | 0 |  |  | A
32.4.2 | BUS COUPLER PROTECTION PANEL with Bay control unit (BCU) for substation automation system. | NOS | 1 | 1 | 0 | 1 | 0 | 558564.0648 |  | 558564.0648 | 100541.5317 | 659105.5964 | 558564.0648 | 0 | 558564.0648 | 100541.5317 | 659105.5964 | 0 |  |  | A
32.4.3 | BUS-BAR PROTECTION PANEL ( Provision of bus bar modules for the future bays and to be integrated with the Automation system) | NOS | 1 | 1 | 0 | 1 | 0 | 1902902.2302 |  | 1902902.2302 | 342522.4014 | 2245424.6317 | 1902902.2302 | 0 | 1902902.2302 | 342522.4014 | 2245424.6317 | 0 |  |  | A
32.5 | 33 KV SIDE PROTECTION PANELS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
32.5.1 | STATION TRANSFORMER PROTECTION PANEL ( BACK-UP & other Unit PROTECTION CONSIDERING 1000 KVA 33/0.43 KV ) with Bay control units (BCU) for substation automation system.(33 KV of ICT shall be used for station supply. Therefore considering all protection in all respect ICT & Station Trafo, the protection philosophy to be considered) | Nos | 2 | 2 | 0 | 2 | 0 | 391009.8865 |  | 782019.7731 | 140763.5592 | 922783.3322 | 782019.7731 | 0 | 782019.7731 | 140763.5592 | 922783.3322 | 0 |  |  | A
33 | AC & DC SYSTEM (suitable for SCADA operation) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
33.1 | AC SYSTEM (suitable for SCADA operation) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
33.1.1 | MAIN AC DB,(HAVING A 1600 A,50KA,DRAWOUT TYPE ACB WITH 3 O/C,E/F,U/V RELAYING FACILITY and MECH& ELECT INTERLOCK FACILITY CONSIDERING Main-1,2 & DG INDOOR TYPE AS PER SPECIFICATION.(MAIN DB-1,MAIN DB-2 WITH B/C & PROVISION FOR D.G INCOMING) | SET | 1 | 1 | 0 | 1 | 0 | 1566768.8796 |  | 1566768.8796 | 282018.3983 | 1848787.2779 | 1566768.8796 | 0 | 1566768.8796 | 282018.3983 | 1848787.2779 | 0 |  |  | A
33.1.2 | ACDB (HAVING 800A MCCB) AS PER SPECIFICATION (AC DB-1,AC DB-2 WITH B/C) | SET | 1 | 1 | 0 | 1 | 0 | 1579094.7088 |  | 1579094.7088 | 284237.0476 | 1863331.7564 | 1579094.7088 | 0 | 1579094.7088 | 284237.0476 | 1863331.7564 | 0 |  |  | A
33.1.3 | MAIN LIGHTING DISTRIBUTION BOARD (HAVING 250A MCCB AS INCOMER)AS PER SPECIFICATION (WITH DB-1,DB-2 & B/C) | SET | 1 | 1 | 0 | 1 | 0 | 1379429.0262 |  | 1379429.0262 | 248297.2247 | 1627726.2509 | 1379429.0262 | 0 | 1379429.0262 | 248297.2247 | 1627726.2509 | 0 |  |  | A
33.1.4 | INDOOR LIGHTING DISTRIBUTION BOARD AS PER SPECIFICATION. (WITH DB-1,DB-2 & B/C) | SET | 1 | 1 | 0 | 1 | 0 | 52925.1621 |  | 52925.1621 | 9526.5292 | 62451.6913 | 52925.1621 | 0 | 52925.1621 | 9526.5292 | 62451.6913 | 0 |  |  | A
33.1.5 | EMERGENCY LIGHTING DISTRIBUTION BOARD | SET | 1 | 1 | 0 | 1 | 0 | 341832.0793 |  | 341832.0793 | 61529.7743 | 403361.8536 | 341832.0793 | 0 | 341832.0793 | 61529.7743 | 403361.8536 | 0 |  |  | A
33.1.6 | INDOOR RECEPTACLE BOARD | SET | 2 | 2 | 0 | 2 | 0 | 19588.446 |  | 39176.892 | 7051.8406 | 46228.7326 | 39176.892 | 0 | 39176.892 | 7051.8406 | 46228.7326 | 0 |  |  | A
33.2 | DC SYSTEM (suitable for SCADA operation) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
33.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). Consider separate source(DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered. | SET | 1 | 1 | 0 | 1 | 0 | 1411806.4912 |  | 1411806.4912 | 254125.1684 | 1665931.6596 | 1411806.4912 | 0 | 1411806.4912 | 254125.1684 | 1665931.6596 | 0 |  |  | A
33.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 1 | 1 | 0 | 1 | 0 | 29403.0892 |  | 29403.0892 | 5292.5561 | 34695.6453 | 29403.0892 | 0 | 29403.0892 | 5292.5561 | 34695.6453 | 0 |  |  | A
33.2.3 | BATTERY (645 AH PLANTE TYPE) for 220 V DC | SET | 2 | 2 | 0 | 2 | 0 | 4049290.8864 |  | 8098581.7727 | 1457744.7191 | 9556326.4918 | 8098581.7727 | 0 | 8098581.7727 | 1457744.7191 | 9556326.4918 | 0 |  |  | A
33.2.4 | BATTERY CHARGER FOR 645 AH, 220 V DC (FLOAT & FLOAT CUM BOOST) (including provision of series dropper diodes with heat sinks & other protection facility at the DC Load terminal end in order to feed 220 V to the load). | SET | 2 | 2 | 0 | 2 | 0 | 579579.9322 |  | 1159159.8645 | 208648.7756 | 1367808.6401 | 1159159.8645 | 0 | 1159159.8645 | 208648.7756 | 1367808.6401 | 0 |  |  | A
34 | DE MINERALISED PLANT of 30 L/Hr FOR MAKING DISTLED WATER FOR BATTERY BANKS | SET | 1 | 1 | 0 | 1 | 0 | 176414.5508 |  | 176414.5508 | 31754.6191 | 208169.17 | 176414.5508 | 0 | 176414.5508 | 31754.6191 | 208169.17 | 0 |  |  | A
35 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16) | NOS | 2 | 2 | 0 | 2 | 0 | 41164.1257 |  | 82328.2513 | 14819.0852 | 97147.3366 | 82328.2513 | 0 | 82328.2513 | 14819.0852 | 97147.3366 | 0 |  |  | A
36 | CARTWHEEL MOUNTED ALUMINIUM LADDER OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT . | NOS | 1 | 1 | 0 | 1 | 0 | 91882.9106 |  | 91882.9106 | 16538.9239 | 108421.8345 | 91882.9106 | 0 | 91882.9106 | 16538.9239 | 108421.8345 | 0 |  |  | A
37 | WATER COOLER WITH WATER PURIFIER (with R.O & ultra violet purification system of ISI mark) SYSTEM | NOS | 1 | 1 | 0 | 1 | 0 | 136427.8237 |  | 136427.8237 | 24557.0083 | 160984.832 | 136427.8237 | 0 | 136427.8237 | 24557.0083 | 160984.832 | 0 |  |  | A
38 | MAINTENANCE & TESTING EQUIPMENT (REFER TS-VOL-II-E-25 TESTING INSTRUMENTS AND MAINTENANCE KITS, OTHER TOOLS & PLANTS & FURNITURE ANNEXURE - II & III and IV) INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
38.1 | SCHEDULE OF REQUIREMENTS OF MAINTENANCE TESTING EQUIPMENT as per ANNEXURE – II (except (1) 5/10 KV IR Tester & (2) SF6 Leak Detector). | LOT | 1 | 1 | 0 | 1 | 0 | 22121636.9938 |  | 22121636.9938 | 3981894.6589 | 26103531.6527 | 22121636.9938 | 0 | 22121636.9938 | 3981894.6589 | 26103531.6527 | 0 |  |  | A
38.2 | Supply of following Testing Equipment |  |  |  | 0 | 0 | 0 | [6 empty] | 0 | [5 empty] | Instruments | A
38.2.1 | Universal Relay Testing Kit (Omicron/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 2857907.9535 |  | 2857907.9535 | 514423.4316 | 3372331.3852 | 2857907.9535 | 0 | 2857907.9535 | 514423.4316 | 3372331.3852 | 0 |  | Instruments | A
38.2.2 | Capacitance Tan-Delta Testing Kit (Omicron/Dovel/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 3139480.5342 |  | 3139480.5342 | 565106.4961 | 3704587.0303 | 3139480.5342 | 0 | 3139480.5342 | 565106.4961 | 3704587.0303 | 0 |  | Instruments | A
38.2.3 | Contact Resistance Measurement Kit- (Milli volt drop measurement (Contact resistance measurement -200Amp DC) (Omicron/Dovel/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 1009203.9103 |  | 1009203.9103 | 181656.7039 | 1190860.6141 | 1009203.9103 | 0 | 1009203.9103 | 181656.7039 | 1190860.6141 | 0 |  | Instruments | A
38.2.4 | 10KV IR Test Kit (Omicron/Dovel/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 809710.5542 |  | 809710.5542 | 145747.8998 | 955458.454 | 809710.5542 | 0 | 809710.5542 | 145747.8998 | 955458.454 | 0 |  | Instruments | A
38.2.5 | TTR Testing Kit (Omicron/Dovel/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 1793341.4071 |  | 1793341.4071 | 322801.4533 | 2116142.8603 | 1793341.4071 | 0 | 1793341.4071 | 322801.4533 | 2116142.8603 | 0 |  | Instruments | A
38.2.6 | Winding Resistance Testing Kit (Omicron/Dovel/Megger make) | Set | 1 | 1 | 0 | 1 | 0 | 1906299.9515 |  | 1906299.9515 | 343133.9913 | 2249433.9428 | 1906299.9515 | 0 | 1906299.9515 | 343133.9913 | 2249433.9428 | 0 |  | Instruments | A
38.2.7 | Third Harmonic Resistive Current Measurement Kit for SA (Omicron/Dovel/Megger/Becon Energy Solutn. make) | Set | 1 | 1 | 0 | 1 | 0 | 1020682.0523 |  | 1020682.0523 | 183722.7694 | 1204404.8217 | 1020682.0523 | 0 | 1020682.0523 | 183722.7694 | 1204404.8217 | 0 |  | Instruments | A
38.2.8 | Infra red camera (suitable for SF6 Gas leakage monitoring) (Fluke/Flir make) | Set | 1 | 1 | 0 | 1 | 0 | 1164289.816 |  | 1164289.816 | 209572.1669 | 1373861.9829 | 1164289.816 | 0 | 1164289.816 | 209572.1669 | 1373861.9829 | 0 |  | Instruments | A
38.2 | OTHER TOOLS AND PLANTS (T&P’S) REQUIREMENT: as per (ANNEXURE- III) | LOT | 1 | 1 | 0 | 1 | 0 | 164678.417 |  | 164678.417 | 29642.1151 | 194320.5321 | 164678.417 | 0 | 164678.417 | 29642.1151 | 194320.5321 | 0 |  | Instruments | A
38.3 | Supply of OFFICE FURNITURE (GODREJ MAKE) as per ANNEXURE-IV & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB,SAS Room etc. | LOT | 1 | 1 | 0 | 1 | 0 | 1158452.6284 |  | 1158452.6284 | 208521.4731 | 1366974.1015 | 1158452.6284 | 0 | 1158452.6284 | 208521.4731 | 1366974.1015 | 0 |  | Instruments | A
39 | Essential Tools & Plants as per Technical Specification |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Instruments | A
39.1 | SF6 gas analyzer: Portable type instruments (A). In-built calibration facility. (B). Sensitivity of the equipment shall not be affected by any atmospheric conditions like dust, humidity, heat, wind etc. (C). Equipment shall work on zero gas loss principle i.e. gas should be pumped back to the compartment after measurement without any exposure to the atmosphere.(D). Equipment shall be supplied with suitable regulator which can be used to connect SF6 cylinder if required. (E). Following acidic/impurities products should be detected as per IEC 60480 and IEC 60376 (i) SF6 purity – Range: 0-100 % & Accuracy: +/- 0.5 %, (ii) Dew point - Range : -60 to +20 deg C & Accuracy: +/- 0.5 deg C, (iii) SO2 - Range : 0-150 ppm & Accuracy : +/- 2 %,(iv) CF4 – Range : 0-60% vol & Accuracy : +/- 1 % , (v) HF - Range : 0-200ppm & Accuracy : +/- 5 %, (F). Instrument should work on AC source as well as on rechargeable battery, (G). Input pressure: upto 10 bar h. It should be housed in a robust IP67 case with wheels. | SET | 1 | 1 | 0 | 1 | 0 | 1705336.3414 |  | 1705336.3414 | 306960.5414 | 2012296.8828 | 1705336.3414 | 0 | 1705336.3414 | 306960.5414 | 2012296.8828 | 0 |  | Instruments | A
39.2 | SF6 gas leak detector: The detector shall be portable, battery operated with built in battery charger, hand held type and having a minimum SF6 gas leakage sensitivity of 5gm/year. The sensor shall be connected through a flexible wand for easy accessibility to joints, seals and couplings in GIS equipment and provided with a protection filter. The equipment shall have on/off switch & suitable indicating lamps/LEDs, variable pitch audible signal for leakage indication, and a head phone jack. The equipment shall have automatic zeroing of background signals suitable for detecting SF6 gas leakage in charged switchyard AIS/GIS. The test kit shall be compatible for EMI/EMC environment as per IEC 1000. | SET | 1 | 1 | 0 | 1 | 0 | 29403.0892 |  | 29403.0892 | 5292.5561 | 34695.6453 | 29403.0892 | 0 | 29403.0892 | 5292.5561 | 34695.6453 | 0 |  | Instruments | A
39.3 | SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant with spares for 5 years Operation.(DILO make) The plant necessary for filling and evacuating the SF6 gas in the switchgear shall be supplied to enable any maintenance work to be carried out. This shall include all the necessary gas cylinders for temporarily storing the evacuated SF6 gas. The capacity of the temporary storage facilities shall at least be sufficient for storing the maximum quantity of gas that could be removed from at least one phase of one complete bay. The minimum capacity of evacuation plant shall be: Vacuum Pump: 60 M3/Hour (Nominal suction pressure) Compressor : 15 M3/Hour(Delivery). The evacuation equipment shall be provided with all the necessary pipes, couplings, flexible tubes and valves for coupling up to the switchgear for filling or evacuating all the gases. The gases compartments shall be fitted with permanent non-return valves through which the gas is pumped into or evacuated form the compartments. | SET | 1 | 1 | 0 | 1 | 0 | 6468515.2678 |  | 6468515.2678 | 1164332.7482 | 7632848.016 | 6468515.2678 | 0 | 6468515.2678 | 1164332.7482 | 7632848.016 | 0 |  | Instruments | A
39.4 | SPECIAL TOOLS: i) Box Spanner: 1 Set (suitable for GIS equipment erection) ii) Adjustable Spanner: 1 Set (suitable for GIS equipment erection) iii) Adjustable torque rench with socket of different sizes required for GIS equipment erection | LOT | 1 | 1 | 0 | 1 | 0 | 23522.0729 |  | 23522.0729 | 4233.9731 | 27756.046 | 23522.0729 | 0 | 23522.0729 | 4233.9731 | 27756.046 | 0 |  | Tools | A
40 | EOT Crane for GIS building for 400 kV GIS station (7T Capacity with double girder safe working load & minimum height of crane have shall be 9.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. Sufficient head clearance (1800mm.) above the crane top level to the bottom of the Roof beam shall be provided. | SET | 1 | 1 | 0 | 1 | 0 | 3528281.0552 |  | 3528281.0552 | 635090.5899 | 4163371.6451 | 4022240.4029 | 0 | 4022240.4029 | 724003.2725 | 4746243.6754 | 582872.0303 | As per the revised size of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A), due to extra Down Shop Lead (DSL) & cables, Unit Rate to be increased by 14%. | EOT Crane | B
41 | EOT Crane for GIS building for 220 kV GIS station (5T Capacity with double girder safe working load & minimum height of crane have shall be 8.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. Sufficient head clearance (1800mm.) above the crane top level to the bottom of the Roof beam shall be provided. | SET | 1 | 1 | 0 | 1 | 0 | 2587406.1071 |  | 2587406.1071 | 465733.0993 | 3053139.2064 | 2897894.84 | 0 | 2897894.84 | 521621.0712 | 3419515.9112 | 366376.7048 | As per the revised size of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A) due to extra DSL & cables, Unit Rate to be increased by 12%. | EOT Crane | B
42 | Ventilation System for 400KV GIS Hall as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 7505882.114 |  | 7505882.114 | 1351058.7805 | 8856940.8945 | 10508234.9596 | 0 | 10508234.9596 | 1891482.2927 | 12399717.2523 | 3542776.3578 | Considering revised dimensions of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A), increase in the value of ventilation eqipment from 1 lakh CMH to 1.4 lakh CMH (40%) | Ventilation System | B
43 | Ventilation System for 220KV GIS Hall as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 5094601.6866 |  | 5094601.6866 | 917028.3036 | 6011629.9902 | 7387172.4456 | 0 | 7387172.4456 | 1329691.0402 | 8716863.4858 | 2705233.4956 | Considering revised dimensions of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A), increase in the value of ventilation eqipment from 55,000 CMH to 80,000 CMH (45%). | Ventilation System | B
44 | FIRE FIGHTING EQIPMENT: (Main Pump, Jockey Pump, DG Set cum Pump, Control Panel for Fire Fighting System (HIGH PRESSURE : Hydrant and Mulsifyre system) to take care of 2 Nos 500 MVA ICT, 125 MVAr reactor, switcyard equipment and buildings. HVW system & hydrant sytsem, complete with all overhead piping, valves, fittings etc inside pump house for Fire protection sytem of substation as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 4851646.1858 |  | 4851646.1858 | 873296.3134 | 5724942.4992 | 4851646.1858 | 0 | 4851646.1858 | 873296.3134 | 5724942.4992 | 0 |  | Fire Fighting System | A
45 | Hydrant sytsem, complete overhead piping of different sizes,valves and accessories etc outside the Pump House for Fire protection sytem of of 2 Nos 500 MVA ICT,125 MVAr reactor, switcyard equipment and buildings as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 3357172.7668 |  | 3357172.7668 | 604291.098 | 3961463.8649 | 3357172.7668 | 0 | 3357172.7668 | 604291.098 | 3961463.8649 | 0 |  | Fire Fighting System | A
46 | HVW Spray sytsem, Hydrant System and complete overhead piping,different type of valves,Fire sensor etc and accessories etc near the Transformer for Fire protection of 500 MVA, 400/220/33 KV ICT,125 MVAr reactor, as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 2233071.8877 |  | 2233071.8877 | 401952.9398 | 2635024.8275 | 2233071.8877 | 0 | 2233071.8877 | 401952.9398 | 2635024.8275 | 0 |  | Fire Fighting System | A
47 | Fire Detection and Alarm System for 400KV GIS Hall as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 417503.3469 |  | 417503.3469 | 75150.6024 | 492653.9494 | 668005.3551 | 0 | 668005.3551 | 120240.9639 | 788246.319 | 295592.3696 | Considering revised dimensions of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A), 60% price implication. | Fire Fighting System | B
48 | Fire Detection and Alarm System for 220KV GIS Hall as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 247499.7414 |  | 247499.7414 | 44549.9534 | 292049.6948 | 395999.5862 | 0 | 395999.5862 | 71279.9255 | 467279.5117 | 175229.8169 | Considering revised dimensions of GIS Hall (as per the Layout Plan of 400/220kV GIS, Ersama & Drg. No. TB-0-420-316-001A), 60% price implication. | Fire Fighting System | B
49 | Fire Detection and Alarm System for Control Room Building as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 529814.4218 |  | 529814.4218 | 95366.5959 | 625181.0177 | 529814.4218 | 0 | 529814.4218 | 95366.5959 | 625181.0177 | 0 |  | Fire Fighting System | A
50 | Indoor Fire Detection and Alarm System for Fire Fighting Pump House Building as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 526335.0197 |  | 526335.0197 | 94740.3035 | 621075.3233 | 526335.0197 | 0 | 526335.0197 | 94740.3035 | 621075.3233 | 0 |  | Fire Fighting System | A
51 | BEST QUALITY & APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos | 45 | 45 | 0 | 45 | 0 | 1470.2541 |  | 66161.4332 | 11909.058 | 78070.4912 | 66161.4332 | 0 | 66161.4332 | 11909.058 | 78070.4912 | 0 |  | Fire Fighting System | A
52 | 250 KVA outdoor type silent Generator with control panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature as per Technical spec. | NOS | 1 | 1 | 0 | 1 | 0 | 2631686.0558 |  | 2631686.0558 | 473703.49 | 3105389.5458 | 2631686.0558 | 0 | 2631686.0558 | 473703.49 | 3105389.5458 | 0 |  | Fire Fighting System | A
53 | 400/220/33 KV, 500 MVA ICT with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spare & other accessories etc as per Technical spec. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | ICT | A
53.1 | 400/220/33 KV, 500 MVA ICT with accessories and spares etc but without OLTC as per Technical spec. | NOS | 2 | 2 | 0 | 2 | 0 | 193541089.2492 |  | 387082178.4984 | 69674792.1297 | 456756970.6281 | 387082178.4984 | 0 | 387082178.4984 | 69674792.1297 | 456756970.6281 | 0 |  | ICT | A
53.2 | Type Test Charges on 400/220/33 KV, 500 MVA ICT (on one unit out of the lot) for the following as per Technical Spec.: - Temperature Rise Test - Measurement of Zero Sequence Impedance - Auxiliary Power Consumption - Vacuum Test - Pressure Test - IP 55 Test | Lot | 1 | 1 | 0 | 1 | 0 | 522956.2245 |  | 522956.2245 | 94132.1204 | 617088.3449 | 522956.2245 | 0 | 522956.2245 | 94132.1204 | 617088.3449 | 0 |  | ICT | A
53.3 | Other requirement of 400/220/33 KV, 500 MVA ICT as indicated below as per Technical Spec: (i) Digital RTCC panel with 3 nos. Digital RTCC relays (Panel shall have provision of mounting 04 nos. of digital RTCC relay) as per Technical Specification (1 set for both the ICT). (ii) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (2 sets for both the ICT). (iii) Online insulating oil drying system(As per Technical Specification) (2 sets for both the ICT) (iv) Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) (2 sets for both the ICT) (v) Oil storage Tank as per Technical Specification (2 Nos) | Lot | 1 | 1 | 0 | 1 | 0 | 17035869.7811 |  | 17035869.7811 | 3066456.5606 | 20102326.3417 | 17035869.7811 | 0 | 17035869.7811 | 3066456.5606 | 20102326.3417 | 0 |  | ICT | A
54 | 400 kV 125 MVAr BUS Reactor with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spare & other accessories etc as per Technical spec. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Reactor 125MVAr | A
54.1 | 400 kV 125 MVAr BUS Reactor with accessories and spares etc as per Technical spec. | Nos | 1 | 1 | 0 | 1 | 0 | 71921609.7375 |  | 71921609.7375 | 12945889.7527 | 84867499.4902 | 71921609.7375 | 0 | 71921609.7375 | 12945889.7527 | 84867499.4902 | 0 |  | Reactor 125MVAr | A
54.2 | Type Test Charges on 400 kV 125 MVAr BUS Reactor for the following as per Technical Spec.: - Temperature Rise Test - Top oil and hot spot temperature rise test - Winding temperature rise test - Measurement of Zero Sequence Reactance -IP-55 Test | Lot | 1 | 1 | 0 | 1 | 0 | 418364.9796 |  | 418364.9796 | 75305.6963 | 493670.6759 | 418364.9796 | 0 | 418364.9796 | 75305.6963 | 493670.6759 | 0 |  | Reactor 125MVAr | A
54.3 | Other requirement of 400 kV 125 MVAr BUS Reactoras indicated below as per Technical Spec.: (i) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (ii) Online insulating oil drying system(As per Technical Specification) (iii) Online dissolved gas(Multi gas) & moisture analyser(As per Technical Specification) | Lot | 1 | 1 | 0 | 1 | 0 | 5294617.9989 |  | 5294617.9989 | 953031.2398 | 6247649.2387 | 5294617.9989 | 0 | 5294617.9989 | 953031.2398 | 6247649.2387 | 0 |  | Reactor 125MVAr | A
55 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
55.1 | 24 fibre optic approach cable along with installation hardware including HDPE pipes | KM | 1 | 1 | 0 | 1 | 0 | 198995.3025 |  | 198995.3025 | 35819.1545 | 234814.457 | 198995.3025 | 0 | 198995.3025 | 35819.1545 | 234814.457 | 0 |  |  | A
55.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 6 | 6 | 0 | 6 | 0 | 340831.9878 |  | 2044991.9267 | 368098.5468 | 2413090.4735 | 2044991.9267 | 0 | 2044991.9267 | 368098.5468 | 2413090.4735 | 0 |  |  | A
55.3 | 48V , 800AH, maintenance free VRLA battery set | NO | 1 | 2 | 1 | 1 | 1 | 446445.2386 | 446445.2386 | 446445.2386 | 80360.1429 | 526805.3815 | 446445.2386 | 446445.2386 | 892890.4771 | 160720.2859 | 1053610.763 | 526805.3815 | Quantity revised as per OPTCL comment on Single Line Diagram for Auxiliary Power System for 400/220kV GIS Sub Station at Ersama (Drg. No. TB-0-420-510-003). Cost Data rate not available. BoQ rate considered. |  | B
55.4 | SMPS based battery charger of 125A suitable for 48V VRLA battery | NO | 1 | 2 | 1 | 1 | 1 | 211697.6602 | 125402.1544 | 211697.6602 | 38105.5788 | 249803.239 | 211697.6602 | 125402.1544 | 337099.8146 | 60677.9666 | 397777.7812 | 147974.5422 | Quantity revised as per OPTCL comment on Single Line Diagram for Auxiliary Power System for 400/220kV GIS Sub Station at Ersama (Drg. No. TB-0-420-510-003). Latest Cost Data rate Sl no. 20 lower than BoQ rate. Cost Data rate considered. |  | B
55.5 | 48 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). | SET | 1 | 1 | 0 | 1 | 0 | 259281.6961 |  | 259281.6961 | 46670.7053 | 305952.4014 | 259281.6961 | 0 | 259281.6961 | 46670.7053 | 305952.4014 | 0 |  |  | A
55.6 | Optical Line Terminal Equipent(OLTE), STM4 type SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module L 4.2(2 nos) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 1 | 0 | 1 | 0 | 1721095.7517 |  | 1721095.7517 | 309797.2353 | 2030892.987 | 1721095.7517 | 0 | 1721095.7517 | 309797.2353 | 2030892.987 | 0 |  |  | A
55.7 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 2 | 0 | 2 | 0 | 70918.8407 |  | 141837.6814 | 25530.7826 | 167368.464 | 141837.6814 | 0 | 141837.6814 | 25530.7826 | 167368.464 | 0 |  |  | A
56 | CCTV Surveilance system with Latest Version PC Monitor, DBR with 1TB Hard Disk, (Night Hawk) cameras including all materials for areas in Control room building & Entire Switchyard areas,GIS Buildings, Other areas etc suitable for 180 & 360 deg movement with all necessary hardware fittings for monitoring with SCADA compatibility. No. of such cameras (different type) are to be calculated as per standard practice & its installations at the strategic locations. Additional Information: 1. Fixed type cameras for monitoring of main gate , Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House,Main Entrance door of GIS Hall, Main Entrance door of store shed and indoor areas. 2. The areas (Staretgic Location) to be monitored through CCTV system are : a) 220 and 400 kV GIS hall indoor area b) All the Transformer and Reactors under present scope c) Main Entrance door of Control Room Building, Fire-fighting Pump House, GIS Hall, store shed. d) Main entrance gate of switchyard and all gates of switchyard. e) 400 and 220 kV bays Line side equipment (Surge Arrester) of present scope Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 | 1 | 0 | 1 | 0 | 4987028.0971 |  | 4987028.0971 | 897665.0575 | 5884693.1545 | 4987028.0971 | 0 | 4987028.0971 | 897665.0575 | 5884693.1545 | 0 |  | CCTV | A
A1 | SUPPLY OF ADDITIONAL ITEMS FOR SUBSTATION |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
57 | 420 KV, 3150 A, 63 KA, ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
57.1 | WITH ONE EARTH SWITCH | Nos | 0 | 2 | 2 | 0 | 2 |  | 1086921.19 | 0 | 0 | 0 | 0 | 2173842.38 | 2173842.38 | 391291.6284 | 2565134.0084 | 2565134.0084 | Additional line side Isolators qty as per as per approved SLD (Drg. No. TB-3-420-510-001) Derived from differential price of New Duburi & Ersama Post Insulator unit Rate |  | B
58 | 245 KV, 2000 A, 50 KA, ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
58.1 | WITH ONE EARTH SWITCH | Nos | 0 | 4 | 4 | 0 | 4 |  | 765396.84 | 0 | 0 | 0 | 0 | 3061587.36 | 3061587.36 | 551085.7248 | 3612673.0848 | 3612673.0848 | Additional line side Isolators qty as per as per approved SLD (Drg. No. TB-3-420-510-001) Being a new item, Rate considered from CPC PO no. 2073 dated 20.12.2023. |  | B
59 | 38/66kV XLPE CABLE & ACCESSORIES |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Cable | A
59.1 | 38/66kV, 1C x 240 sq. mm XLPE CABLE | Mtrs | 0 | 1500 | 1500 | 0 | 1500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38/66kV Cable is required for connection between ICT tertiary & Station Transformers as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate considered from BHEL rate from PGCIL | Cable | A
59.2 | 66kV XLPE CABLE Termination Kit suitable for ICT tertiary | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38/66kV Cable is required for connection between ICT tertiary & Station Transformers as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate considered from BHEL rate from PGCIL |  | A
59.3 | 66kV XLPE CABLE Termination Kit suitable for ST | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38/66kV Cable is required for connection between ICT tertiary & Station Transformers as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate considered from BHEL rate from PGCIL |  | A
59.4 | 66kV CABLE Link Box (with SVL) with bonding cable | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38/66kV Cable is required for connection between ICT tertiary & Station Transformers as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate considered from BHEL rate from PGCIL |  | A
59.5 | 66kV CABLE Link Box (without SVL) with bonding cable | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38/66kV Cable is required for connection between ICT tertiary & Station Transformers as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate considered from BHEL rate from PGCIL |  | A
60 | 36 kV, 31.5 kA for 1 sec Voltage Tranformer (with higher BIL - 72.5 kV VT required) | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Rate Considered???? |  | A
61 | 36 KV, 1250A, 31.5 KA for 1 sec, isolator (single isolator with earth switch) including post insulators as per technical specification (with higher BIL - 72.5 kV Isolator required) | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
62 | 36 KV, 1250 A, 31.5 KA 3 Sec, Circuit Breaker with supporting GI structures as per technical specification. (with higher BIL - 72.5 kV CB required) | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
63 | 36 KV, 31.5 KA for 1 sec,1200-600/1-1-1-1 A, Current Transformer as per technical specification (with higher BIL - 72.5 kV CT required) | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
64 | 36 KV, 31.5 KA for 1 sec, 50-25/1-1 A, Current Transformer as per technical specification (with higher BIL - 72.5 kV CT required) | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
65 | 36 KV Bus Post Insulator as per technical specification (with higher BIL - 72.5 kV BPI required) | Nos | 0 | 12 | 12 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
66 | Controlled Switching Device (CSD) for 400kV Line Bays in GIS | Nos. | 0 | 2 | 2 | 0 | 2 |  | 529242.65 | 0 | 0 | 0 | 0 | 1058485.3 | 1058485.3 | 190527.354 | 1249012.654 | 1249012.654 | Additional qty as per approved SLD (Drg. No. TB-3-420-510-001) Derived from New Duburi Circuit Breaker Rate |  | B
B | SUPPLY OF MANDATORY SPARES FOR SUB-STATION AT 400/220 KV GIS S/S AT ERSAMA |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
B.1 | SPARES FOR 420KV GIS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | GIS 400kV Spares | A
1 | 420KV Gas Insulated Single phase voltage transformer with enclosure | Nos | 1 | 1 | 0 | 1 | 0 | 806164.4129 |  | 806164.4129 | 145109.5943 | 951274.0073 | 806164.4129 | 0 | 806164.4129 | 145109.5943 | 951274.0073 | 0 |  | GIS 400kV Spares | A
2 | 420KV Gas Insulated Single phase Current transformer with enclosure | Nos | 1 | 1 | 0 | 1 | 0 | 768956.8247 |  | 768956.8247 | 138412.2284 | 907369.0531 | 768956.8247 | 0 | 768956.8247 | 138412.2284 | 907369.0531 | 0 |  | GIS 400kV Spares | A
3 | SF6 gas Pressure relief devices 1 no each type for 400KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 77516.058 |  | 77516.058 | 13952.8904 | 91468.9484 | 77516.058 | 0 | 77516.058 | 13952.8904 | 91468.9484 | 0 |  | GIS 400kV Spares | A
4 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for 400KV GIS : 1 no. of each type | SET | 1 | 1 | 0 | 1 | 0 | 77516.058 |  | 77516.058 | 13952.8904 | 91468.9484 | 77516.058 | 0 | 77516.058 | 13952.8904 | 91468.9484 | 0 |  | GIS 400kV Spares | A
5 | Trip coil assembly with resistor for 420KV GIS Circuit breaker | Nos | 6 | 6 | 0 | 6 | 0 | 24805.0589 |  | 148830.3532 | 26789.4636 | 175619.8167 | 148830.3532 | 0 | 148830.3532 | 26789.4636 | 175619.8167 | 0 |  | GIS 400kV Spares | A
6 | Closing coil assembly with resistor for 420KV GIS Circuit breaker | Nos | 6 | 6 | 0 | 6 | 0 | 24805.0589 |  | 148830.3532 | 26789.4636 | 175619.8167 | 148830.3532 | 0 | 148830.3532 | 26789.4636 | 175619.8167 | 0 |  | GIS 400kV Spares | A
7 | All types of control valves for SF6 gas of each type for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 38448.7377 |  | 38448.7377 | 6920.7728 | 45369.5105 | 38448.7377 | 0 | 38448.7377 | 6920.7728 | 45369.5105 | 0 |  | GIS 400kV Spares | A
8 | Coupling device for pressure gause cum switch for connecting Gas handling plant | SET | 1 | 1 | 0 | 1 | 0 | 77516.058 |  | 77516.058 | 13952.8904 | 91468.9484 | 77516.058 | 0 | 77516.058 | 13952.8904 | 91468.9484 | 0 |  | GIS 400kV Spares | A
9 | Locking device to keep the Disconnectors and Earthing switches in close or Open position in case of removal of removal of driving mechanism for 420KV GIS. | SET | 1 | 1 | 0 | 1 | 0 | 55811.8805 |  | 55811.8805 | 10046.1385 | 65858.019 | 55811.8805 | 0 | 55811.8805 | 10046.1385 | 65858.019 | 0 |  | GIS 400kV Spares | A
10 | SF6 to Air bushing as applicable for 420KV GIS | Nos | 1 | 1 | 0 | 1 | 0 | 706944.1775 |  | 706944.1775 | 127249.952 | 834194.1295 | 706944.1775 | 0 | 706944.1775 | 127249.952 | 834194.1295 | 0 |  | GIS 400kV Spares | A
11 | Set of spares for local control cabinet including M.C.B., fuses, time relays,all type of auxiliary relay & contactors,lamps,semaphor,terminals, push buttons etc for 400KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 186037.9414 |  | 186037.9414 | 33486.8295 | 219524.7709 | 186037.9414 | 0 | 186037.9414 | 33486.8295 | 219524.7709 | 0 |  | GIS 400kV Spares | A
12 | Auxiliary contacts for 420KV GIS circuit breaker | SET | 1 | 1 | 0 | 1 | 0 | 12402.5294 |  | 12402.5294 | 2232.4553 | 14634.9847 | 12402.5294 | 0 | 12402.5294 | 2232.4553 | 14634.9847 | 0 |  | GIS 400kV Spares | A
13 | Limit switch & Auxiliary contacts for 420KV GIS DS and ES | SET | 1 | 1 | 0 | 1 | 0 | 62012.6471 |  | 62012.6471 | 11162.2765 | 73174.9236 | 62012.6471 | 0 | 62012.6471 | 11162.2765 | 73174.9236 | 0 |  | GIS 400kV Spares | A
14 | SF6 gas in steel bottle 50 Kg / bottle | SET | 2 | 2 | 0 | 2 | 0 | 58292.1872 |  | 116584.3743 | 20985.1874 | 137569.5617 | 116584.3743 | 0 | 116584.3743 | 20985.1874 | 137569.5617 | 0 |  | GIS 400kV Spares | A
15 | spring charge motor for 420KV GIS circuit breakers | SET | 1 | 1 | 0 | 1 | 0 | 37207.5883 |  | 37207.5883 | 6697.3659 | 43904.9542 | 37207.5883 | 0 | 37207.5883 | 6697.3659 | 43904.9542 | 0 |  | GIS 400kV Spares | A
16 | Complete Drive for single phase 420KV GIS circuit breaker: | No. | 1 | 1 | 0 | 1 | 0 | 620126.4715 |  | 620126.4715 | 111622.7649 | 731749.2364 | 620126.4715 | 0 | 620126.4715 | 111622.7649 | 731749.2364 | 0 |  | GIS 400kV Spares | A
17 | Complete drive mechanism for disconnect switches and grounding switches for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 558113.8243 |  | 558113.8243 | 100460.4884 | 658574.3127 | 558113.8243 | 0 | 558113.8243 | 100460.4884 | 658574.3127 | 0 |  | GIS 400kV Spares | A
18 | Motor for disconnect switches and grounding switches for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 74415.1766 |  | 74415.1766 | 13394.7318 | 87809.9084 | 74415.1766 | 0 | 74415.1766 | 13394.7318 | 87809.9084 | 0 |  | GIS 400kV Spares | A
19 | Complete drive mechanism for fast acting grounding switches for 420KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 186037.9414 |  | 186037.9414 | 33486.8295 | 219524.7709 | 186037.9414 | 0 | 186037.9414 | 33486.8295 | 219524.7709 | 0 |  | GIS 400kV Spares | A
20 | Motor for fast acting grounding switches for 420KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 24805.0589 |  | 24805.0589 | 4464.9106 | 29269.9695 | 24805.0589 | 0 | 24805.0589 | 4464.9106 | 29269.9695 | 0 |  | GIS 400kV Spares | A
21 | Rupture disc for circuit breakers for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 124025.2943 |  | 124025.2943 | 22324.553 | 146349.8473 | 124025.2943 | 0 | 124025.2943 | 22324.553 | 146349.8473 | 0 |  | GIS 400kV Spares | A
22 | Rupture disc for potential transformer for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 186037.9414 |  | 186037.9414 | 33486.8295 | 219524.7709 | 186037.9414 | 0 | 186037.9414 | 33486.8295 | 219524.7709 | 0 |  | GIS 400kV Spares | A
23 | Limit switch & Aux for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 62013.6433 |  | 62013.6433 | 11162.4558 | 73176.099 | 62013.6433 | 0 | 62013.6433 | 11162.4558 | 73176.099 | 0 |  | GIS 400kV Spares | A
24 | Rupture disc for other compartments for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 186037.9414 |  | 186037.9414 | 33486.8295 | 219524.7709 | 186037.9414 | 0 | 186037.9414 | 33486.8295 | 219524.7709 | 0 |  | GIS 400kV Spares | A
25 | Bus supplort insulator of each type for 420KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 260453.118 |  | 260453.118 | 46881.5612 | 307334.6793 | 260453.118 | 0 | 260453.118 | 46881.5612 | 307334.6793 | 0 |  | GIS 400kV Spares | A
B.2 | SPARES FOR 245KV GIS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | GIS 220kV Spares | A
1 | 245KV Gas Insulated Single phase voltage transformer with enclosure | No. | 1 | 1 | 0 | 1 | 0 | 455610.4199 |  | 455610.4199 | 82009.8756 | 537620.2955 | 455610.4199 | 0 | 455610.4199 | 82009.8756 | 537620.2955 | 0 |  | GIS 220kV Spares | A
2 | 245KV Gas Insulated Single phase Current transformer with enclosure | No. | 1 | 1 | 0 | 1 | 0 | 513596.8022 |  | 513596.8022 | 92447.4244 | 606044.2266 | 513596.8022 | 0 | 513596.8022 | 92447.4244 | 606044.2266 | 0 |  | GIS 220kV Spares | A
3 | SF6 gas Pressure relief devices 1 no each type for245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 51774.6584 |  | 51774.6584 | 9319.4385 | 61094.097 | 51774.6584 | 0 | 51774.6584 | 9319.4385 | 61094.097 | 0 |  | GIS 220kV Spares | A
4 | SF6 Pressure gauges cum switch or Density Monitors and pressure switches for 245KV GIS : 1 no. of each type | SET | 1 | 1 | 0 | 1 | 0 | 51774.6584 |  | 51774.6584 | 9319.4385 | 61094.097 | 51774.6584 | 0 | 51774.6584 | 9319.4385 | 61094.097 | 0 |  | GIS 220kV Spares | A
5 | Trip coil assembly with resistor for 245KV GIS Circuit breaker | Nos | 6 | 6 | 0 | 6 | 0 | 16568.2493 |  | 99409.4958 | 17893.7092 | 117303.205 | 99409.4958 | 0 | 99409.4958 | 17893.7092 | 117303.205 | 0 |  | GIS 220kV Spares | A
6 | Closing coil assembly with resistor for 245KV GIS Circuit breaker | Nos | 6 | 6 | 0 | 6 | 0 | 16568.2493 |  | 99409.4958 | 17893.7092 | 117303.205 | 99409.4958 | 0 | 99409.4958 | 17893.7092 | 117303.205 | 0 |  | GIS 220kV Spares | A
7 | All types of control valves for SF6 gas of each type for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 25680.637 |  | 25680.637 | 4622.5147 | 30303.1517 | 25680.637 | 0 | 25680.637 | 4622.5147 | 30303.1517 | 0 |  | GIS 220kV Spares | A
8 | Locking device to keep the Disconnectors and Earthing switches in close or Open position in case of removal of removal of driving mechanism for 245KV GIS. | SET | 1 | 1 | 0 | 1 | 0 | 37277.3158 |  | 37277.3158 | 6709.9168 | 43987.2326 | 37277.3158 | 0 | 37277.3158 | 6709.9168 | 43987.2326 | 0 |  | GIS 220kV Spares | A
9 | SF6 to Air bushing as applicable for 245 KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 265083.0238 |  | 265083.0238 | 47714.9443 | 312797.9681 | 265083.0238 | 0 | 265083.0238 | 47714.9443 | 312797.9681 | 0 |  | GIS 220kV Spares | A
10 | Set of spares for local control cabinet including M.C.B., fuses, time relays,all type of auxiliary relay & contactors,lamps,semaphor,terminals, push buttons etc for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 124257.3873 |  | 124257.3873 | 22366.3297 | 146623.717 | 124257.3873 | 0 | 124257.3873 | 22366.3297 | 146623.717 | 0 |  | GIS 220kV Spares | A
11 | Auxiliary contacts for 245KV GIS circuit breaker | SET | 1 | 1 | 0 | 1 | 0 | 8283.6266 |  | 8283.6266 | 1491.0528 | 9774.6794 | 8283.6266 | 0 | 8283.6266 | 1491.0528 | 9774.6794 | 0 |  | GIS 220kV Spares | A
12 | Limit switch & Auxiliary contacts for 245KV GIS DS and ES | SET | 1 | 1 | 0 | 1 | 0 | 41419.1291 |  | 41419.1291 | 7455.4432 | 48874.5723 | 41419.1291 | 0 | 41419.1291 | 7455.4432 | 48874.5723 | 0 |  | GIS 220kV Spares | A
13 | SF6 gas in steel bottle 50 Kg / bottle | SET | 2 | 2 | 0 | 2 | 0 | 38934.838 |  | 77869.676 | 14016.5417 | 91886.2177 | 77869.676 | 0 | 77869.676 | 14016.5417 | 91886.2177 | 0 |  | GIS 220kV Spares | A
14 | spring charge motor for 245KV GIS circuit breakers | SET | 1 | 1 | 0 | 1 | 0 | 24851.8759 |  | 24851.8759 | 4473.3377 | 29325.2136 | 24851.8759 | 0 | 24851.8759 | 4473.3377 | 29325.2136 | 0 |  | GIS 220kV Spares | A
15 | Complete Drive single phase for 245KV GIS circuit breaker: | No. | 1 | 1 | 0 | 1 | 0 | 414191.2908 |  | 414191.2908 | 74554.4324 | 488745.7232 | 414191.2908 | 0 | 414191.2908 | 74554.4324 | 488745.7232 | 0 |  | GIS 220kV Spares | A
16 | Complete drive mechanism for disconnect switches and grounding switches for 245KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 372772.1618 |  | 372772.1618 | 67098.9891 | 439871.1509 | 372772.1618 | 0 | 372772.1618 | 67098.9891 | 439871.1509 | 0 |  | GIS 220kV Spares | A
17 | Motor for disconnect switches and grounding switches for 245KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 49703.7518 |  | 49703.7518 | 8946.6753 | 58650.4271 | 49703.7518 | 0 | 49703.7518 | 8946.6753 | 58650.4271 | 0 |  | GIS 220kV Spares | A
18 | Complete drive mechanism for fast acting grounding switches for 245KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 124257.3873 |  | 124257.3873 | 22366.3297 | 146623.717 | 124257.3873 | 0 | 124257.3873 | 22366.3297 | 146623.717 | 0 |  | GIS 220kV Spares | A
19 | Motor for fast acting grounding switches for 245KV GIS | No. | 1 | 1 | 0 | 1 | 0 | 16568.2493 |  | 16568.2493 | 2982.2849 | 19550.5342 | 16568.2493 | 0 | 16568.2493 | 2982.2849 | 19550.5342 | 0 |  | GIS 220kV Spares | A
20 | Rupture disc for circuit breakers for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 82838.2582 |  | 82838.2582 | 14910.8865 | 97749.1446 | 82838.2582 | 0 | 82838.2582 | 14910.8865 | 97749.1446 | 0 |  | GIS 220kV Spares | A
21 | Rupture disc for potential transformer for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 124257.3873 |  | 124257.3873 | 22366.3297 | 146623.717 | 124257.3873 | 0 | 124257.3873 | 22366.3297 | 146623.717 | 0 |  | GIS 220kV Spares | A
22 | Limit switch & Aux for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 41420.1252 |  | 41420.1252 | 7455.6225 | 48875.7477 | 41420.1252 | 0 | 41420.1252 | 7455.6225 | 48875.7477 | 0 |  | GIS 220kV Spares | A
23 | Rupture disc for other compartments for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 124257.3873 |  | 124257.3873 | 22366.3297 | 146623.717 | 124257.3873 | 0 | 124257.3873 | 22366.3297 | 146623.717 | 0 |  | GIS 220kV Spares | A
24 | Bus supplort insulator of each type for 245KV GIS | SET | 1 | 1 | 0 | 1 | 0 | 132542.01 |  | 132542.01 | 23857.5618 | 156399.5717 | 132542.01 | 0 | 132542.01 | 23857.5618 | 156399.5717 | 0 |  | GIS 220kV Spares | A
[6 empty] | 0 | [7 empty] | 0 | [6 empty] | A
B.3 | SUPPLY OF MANDATORY SPARES FOR 400 KV BAY-EXTENSION AT DUBURI SUB-STATION |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
1 | 420 KV,2000-1000-500A,63KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 1 | 1 | 0 | 1 | 0 | 699765.2337 |  | 699765.2337 | 125957.7421 | 825722.9757 | 699765.2337 | 0 | 699765.2337 | 125957.7421 | 825722.9757 | 0 |  |  | A
2 | 420 KV,2000A,63KA,ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
2.1 | MALE & FEMALE CONTACTS | SET | 2 | 2 | 0 | 2 | 0 | 21170.2641 |  | 42340.5281 | 7621.2951 | 49961.8232 | 42340.5281 | 0 | 42340.5281 | 7621.2951 | 49961.8232 | 0 |  |  | A
2.2 | POWER CONTACTOR, RELAYS, MCBs, SWITCHES, FUSES, PUSH BUTTONS, RESISTORS ETC AS PER APPROVED SCHEMATIC. | SET | 1 | 1 | 0 | 1 | 0 | 11290.8739 |  | 11290.8739 | 2032.3573 | 13323.2312 | 11290.8739 | 0 | 11290.8739 | 2032.3573 | 13323.2312 | 0 |  |  | A
2.3 | LIMIT SWITCH | SET | 2 | 2 | 0 | 2 | 0 | 1411.4838 |  | 2822.9675 | 508.1342 | 3331.1017 | 2822.9675 | 0 | 2822.9675 | 508.1342 | 3331.1017 | 0 |  |  | A
2.4 | MOTOR WITH GEAR ASSEMBLY & BEVEL GEAR ASSEMBLY COMPLETE. | SET | 1 | 1 | 0 | 1 | 0 | 14819.0852 |  | 14819.0852 | 2667.4353 | 17486.5206 | 14819.0852 | 0 | 14819.0852 | 2667.4353 | 17486.5206 | 0 |  |  | A
2.5 | AUXILIARY SWITCH CONTACTS ASSEMBLY | SET | 1 | 1 | 0 | 1 | 0 | 5881.0163 |  | 5881.0163 | 1058.5829 | 6939.5992 | 5881.0163 | 0 | 5881.0163 | 1058.5829 | 6939.5992 | 0 |  |  | A
2.6 | EARTHING ROD & BLADE CONTACT SIDE | SET | 1 | 1 | 0 | 1 | 0 | 52925.1621 |  | 52925.1621 | 9526.5292 | 62451.6913 | 52925.1621 | 0 | 52925.1621 | 9526.5292 | 62451.6913 | 0 |  |  | A
2.7 | HINGE PINS,TERMINAL CONNECTOR,TERMINAL PAD | SET | 1 | 1 | 0 | 1 | 0 | 17642.0527 |  | 17642.0527 | 3175.5695 | 20817.6222 | 17642.0527 | 0 | 17642.0527 | 3175.5695 | 20817.6222 | 0 |  |  | A
3 | 420KV,4000A,63KA,SF6,CIRCUIT BREAKER |  |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | A
3.1 | CLOSING COIL | NOS | 10 | 10 | 0 | 10 | 0 | 4704.6138 |  | 47046.1381 | 8468.3049 | 55514.4429 | 47046.1381 | 0 | 47046.1381 | 8468.3049 | 55514.4429 | 0 |  |  | A
3.2 | TRIPPING COIL | NOS | 10 | 10 | 0 | 10 | 0 | 4704.6138 |  | 47046.1381 | 8468.3049 | 55514.4429 | 47046.1381 | 0 | 47046.1381 | 8468.3049 | 55514.4429 | 0 |  |  | A
3.3 | SF6 GAS FILLING DEVICE | NOS | 1 | 1 | 0 | 1 | 0 | 14113.8414 |  | 14113.8414 | 2540.4915 | 16654.3329 | 14113.8414 | 0 | 14113.8414 | 2540.4915 | 16654.3329 | 0 |  |  | A
3.4 | SET OF GASKETS ,"O" RINGS,SEALS PER CIRCUIT BREAKER | SET | 1 | 1 | 0 | 1 | 0 | 17642.0527 |  | 17642.0527 | 3175.5695 | 20817.6222 | 17642.0527 | 0 | 17642.0527 | 3175.5695 | 20817.6222 | 0 |  |  | A
4 | 390 KV,METAL OXIDE, 10 KA, CLASS III SURGE ARRESTOR COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 1 | 1 | 0 | 1 | 0 | 216754.8959 |  | 216754.8959 | 39015.8813 | 255770.7772 | 216754.8959 | 0 | 216754.8959 | 39015.8813 | 255770.7772 | 0 |  |  | A
5 | 400 KV Bus Post Insulators | NOS | 2 | 2 | 0 | 2 | 0 | 47044.1458 |  | 94088.2917 | 16935.8925 | 111024.1842 | 94088.2917 | 0 | 94088.2917 | 16935.8925 | 111024.1842 | 0 |  |  | A
C | SUPPLY COMPONENT OF THE WORKS CONTRACT FOR New Duburi Bay Extension | [12 empty] | 0 | [6 empty] | A
1 | 420 KV,2000-1000-500A,63 KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 12 | 12 | 0 | 12 | 0 | 699765.2337 |  | 8397182.8041 | 1511492.9047 | 9908675.7089 | 8397182.8041 | 0 | 8397182.8041 | 1511492.9047 | 9908675.7089 | 0 |  | Current Transformer (CT) | A
2 | 420 KV, 3150 A, 63 KA, ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Isolator | A
2.1 | WITH ONE EARTH SWITCH | NOS | 8 | 8 | 0 | 8 | 0 | 975782.5251 |  | 7806260.2004 | 1405126.8361 | 9211387.0365 | 7806260.2004 | 0 | 7806260.2004 | 1405126.8361 | 9211387.0365 | 0 |  | Isolator | A
2.2 | WITH TWO EARTH SWITCH | NOS | 2 | 2 | 0 | 2 | 0 | 1144839.8289 |  | 2289679.6577 | 412142.3384 | 2701821.9961 | 2289679.6577 | 0 | 2289679.6577 | 412142.3384 | 2701821.9961 | 0 |  | Isolator | A
3 | 420 KV,4400pF,63 KA,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | CVT | A
3.1 | SINGLE PHASE LINE CAPACITOR VOLTAGE TRANSFORMER | NOS | 6 | 6 | 0 | 6 | 0 | 438287.1215 |  | 2629722.7287 | 473350.0912 | 3103072.8199 | 2629722.7287 | 0 | 2629722.7287 | 473350.0912 | 3103072.8199 | 0 |  | CVT | A
4 | 420KV,3150A,63KA,SF6,CIRCUIT BREAKER WITH Terminal Connector, SUPPORT STRUCTURE etc. WITH CSD (For Tie & reactor switching) | NOS | 3 | 3 | 0 | 3 | 0 | 3492998.9419 |  | 10478996.8257 | 1886219.4286 | 12365216.2543 | 10478996.8257 | 0 | 10478996.8257 | 1886219.4286 | 12365216.2543 | 0 |  | Circuit Breaker | A
5 | 420KV,3150A,63KA,SF6,CIRCUIT BREAKER WITH Terminal Connector SUPPORT STRUCTURE etc WITH OUT CSD | NOS | 2 | 2 | 0 | 2 | 0 | 2963756.2856 |  | 5927512.5711 | 1066952.2628 | 6994464.8339 | 5927512.5711 | 0 | 5927512.5711 | 1066952.2628 | 6994464.8339 | 0 |  | Circuit Breaker | A
6 | 390KV metal oxide polymer housed surge arrrestor, 20 KA , Long duration discharge class IV ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 12 | 12 | 0 | 12 | 0 | 209227.3146 |  | 2510727.7752 | 451930.9995 | 2962658.7748 | 2510727.7752 | 0 | 2510727.7752 | 451930.9995 | 2962658.7748 | 0 |  | Surge Arrestor | A
7 | 120KV metal oxide polymer housed surge arrrestor, 10 KA , Long duration discharge class III ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 2 | 2 | 0 | 2 | 0 | 47631.849 |  | 95263.6981 | 17147.4657 | 112411.1637 | 95263.6981 | 0 | 95263.6981 | 17147.4657 | 112411.1637 | 0 |  | Surge Arrestor | A
8 | 400 KV Bus Post Insulators | NOS | 48 | 59 | 11 | 59 | 0 | 41164.1257 | 0 | 1975878.0321 | 355658.0458 | 2331536.0778 | 2428683.4144 | 0 | 2428683.4144 | 437163.0146 | 2865846.429 | 534310.3512 | As per approved EKD TB-2-420-316-007-D Rev 00 | BPI | B
9 | 132kV, 2000A, 40kA,ISOLATORS WITHOUT EARTH SWITCH (1-Pole) | NOS | 2 | 2 | 0 | 2 | 0 | 165759.1932 |  | 331518.3865 | 59673.3096 | 391191.696 | 331518.3865 | 0 | 331518.3865 | 59673.3096 | 391191.696 | 0 |  | Isolator | A
10 | 145 KV CT (800-400-200/1-1-1) FOR NGR | NOS | 2 | 2 | 0 | 2 | 0 | 333695.8766 |  | 667391.7531 | 120130.5156 | 787522.2687 | 667391.7531 | 0 | 667391.7531 | 120130.5156 | 787522.2687 | 0 |  | Current Transformer (CT) | A
11 | BUS BAR & CIRCUIT MATERIALS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
11.1 | 160 kN PORCELAIN Antifog LONG ROD INSULATOR (ANTI FOG) for twin Moose cond (Double TENSION)-400 KV | SET | 72 | 54 | -18 | 54 | 0 | 81209.6231 |  | 5847092.861 | 1052476.715 | 6899569.576 | 4385319.6457 | 0 | 4385319.6457 | 789357.5362 | 5174677.182 | -1724892.394 | As per approved EKD TB-2-420-316-007-D Rev 00 |  | B
11.2 | 120 kN PORCELAIN Antifog LONG ROD INSULATOR (ANTI FOG) for Twin Moose cond (SUSPENSION)-400 KV | SET | 30 | 24 | -6 | 24 | 0 | 39847.2721 |  | 1195418.1627 | 215175.2693 | 1410593.432 | 956334.5301 | 0 | 956334.5301 | 172140.2154 | 1128474.7456 | -282118.6864 | As per approved EKD TB-2-420-316-007-D Rev 00 |  | B
11.3 | ACSR MOOSE CONDUCTOR | KM | 3.3 | 4.2 | 0.9 | 4.12 | 0.08 | 464557.4538 | 409923 | 1533039.5977 | 275947.1276 | 1808986.7253 | 1913976.7098 | 32793.84 | 1946770.5498 | 350418.699 | 2297189.2488 | 488202.5235 | As per approved EKD TB-2-420-316-007-D Rev 00 Latest Cost Data 2023 rate Sl. No. 18 is lower than the BoQ rate. Hence, Cost Data rate considered. |  | B
11.4 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including other materials required to complete all connections in complete shape like sleeves,corona bell etc. | MTR | 450 | 750 | 300 | 562.5 | 187.5 | 3633.7987 | 3633.7987 | 1635209.4058 | 294337.6931 | 1929547.0989 | 2044011.7573 | 681337.2524 | 2725349.0097 | 490562.8218 | 3215911.8315 | 1286364.7326 | As per approved EKD TB-2-420-316-007-D Rev 00 Cost Data rate not avaialbe. BoQ rate considered. | Aluminium Tube | B
11.5 | HARDWARES & FITTINGS/SPACERS/CLAMP & CONNECTORS | LOT | 1 | 1 | 0 | 1 | 0 | 1984729.4397 |  | 1984729.4397 | 357251.2991 | 2341980.7389 | 1984729.4397 | 0 | 1984729.4397 | 357251.2991 | 2341980.7389 | 0 |  |  | A
11.6 | EARTH SPIKE & IT'S HARDWARES , FITTING, with copper earth bond | NOS | 14 | 18 | 4 | 17 | 1 | 3529.2074 | 3529.2074 | 49408.9041 | 8893.6027 | 58302.5068 | 59996.5264 | 3529.2074 | 63525.7338 | 11434.6321 | 74960.3659 | 16657.8591 | As per approved DSLP TB-2-420-316-010-D Rev 00 Cost Data rate not avaialbe. BoQ rate considered. |  | B
12 | SUBSTATION EARTHING SYSTEMS |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
12.1 | EARTHING CONDUCTOR FOR BURRIAL & RAISER FROM THE MAT BELOW GROUND :40mm MS Rod for laying as main eartth mat (Mat spacing maximum 5m both way) | MTR | 3960 | 14500 | 10540 | 4950 | 9550 | 615.5942 | 615.5942 | 2437752.9695 | 438795.5345 | 2876548.504 | 3047191.2119 | 5878924.4593 | 8926115.6712 | 1606700.8208 | 10532816.492 | 7656267.988 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 Latest Cost Data rate for substation structures higher than BoQ rate. So BoQ rate considered.. | MS Rod | B
12.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MTR | 2377 | 2850 | 473 | 2850 | 0 | 467.1742 |  | 1110473.138 | 199885.1648 | 1310358.3029 | 1331446.5475 | 0 | 1331446.5475 | 239660.3785 | 1571106.926 | 260748.6232 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 |  | B
12.3 | EARTHING CONDUCTOR: 50X6 mm GI Flat for fencing,cable tray and auxiliary Boards earthing. | MTR | 847 | 2850 | 2003 | 1058 | 1792 | 190.2565 | 190.2565 | 161147.2174 | 29006.4991 | 190153.7165 | 201291.3294 | 340939.5673 | 542230.8967 | 97601.5614 | 639832.4581 | 449678.7416 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 Rate Contract 2023 Sl. No. 21.1 v(a-b) rate is higher than BoQ rate. Hence BoQ Rate is considered. |  | B
12.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | NOS | 60 | 180 | 120 | 75 | 105 | 6174.8679 | 3675.65 | 370492.0726 | 66688.5731 | 437180.6457 | 463115.0908 | 385943.25 | 849058.3408 | 152830.5013 | 1001888.8421 | 564708.1964 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 Rate Contract 2023 Sl. No. 21.3 (i-ii) rate is lower than BoQ rate. Hence RC Rate is considered. |  | B
12.5 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated | NOS | 50 | 0 | -50 | 0 | 0 | 1844.7903 | 0 | 92239.5169 | 16603.113 | 108842.63 | 0 | 0 | 0 | 0 | 0 | -108842.63 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 |  | B
12.6 | GI Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. Sizes of Cable Tray: Section:1-1:G.I Cable Trays(size: 450x75x2500mm) Section:2-2:G.I Cable Trays(size: 300x75x2500mm) Section:3-3 & 4-4:G.I Cable Trays(size: 150x75x2500mm) GI Support Angle:50X50X6 mm | LOT | 1 | 1 | 0 | 1 | 0 | 2374374.6595 |  | 2374374.6595 | 427387.4387 | 2801762.0982 | 2374374.6595 | 0 | 2374374.6595 | 427387.4387 | 2801762.0982 | 0 |  |  | A
13 | BAY MARSHALLING KIOSK | NOS | 2 | 2 | 0 | 2 | 0 | 87246.0321 |  | 174492.0641 | 31408.5715 | 205900.6357 | 174492.0641 | 0 | 174492.0641 | 31408.5715 | 205900.6357 | 0 |  | MK & JB | A
14 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 1 | 1 | 0 | 1 | 0 | 39498.6346 |  | 39498.6346 | 7109.7542 | 46608.3888 | 39498.6346 | 0 | 39498.6346 | 7109.7542 | 46608.3888 | 0 |  |  | A
15 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near Reactor and NGR400/220 KV ICT ) | NOS | 1 | 1 | 0 | 1 | 0 | 53994.9811 |  | 53994.9811 | 9719.0966 | 63714.0778 | 53994.9811 | 0 | 53994.9811 | 9719.0966 | 63714.0778 | 0 |  |  | A
16 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 1 | 1 | 0 | 1 | 0 | 23000.1128 |  | 23000.1128 | 4140.0203 | 27140.1331 | 23000.1128 | 0 | 23000.1128 | 4140.0203 | 27140.1331 | 0 |  |  | A
17 | SWITCH YARD STRUCTURES( including Foundation Bolts and Nuts) GALVANISED (LATTICE) FOR ALL 400 KV |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Lattice Structure | A
17.1 | DIFFERENT TYPES OF COLUMNS (LATTICE TYPE) WITH DETAILS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Lattice Structure | A
17.1.1 | 400 KV COLUMN with peak (4TP) | NOS | 9 | 20 | 11 | 11 | 9 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | Lattice Structure | A
17.1.2 | 400 KV COLUMN without peak (4T) | NOS | 5 | 0 | -5 | 0 | 0 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | Lattice Structure | A
17.2 | DIFFERENT TYPE OF BEAMS (LATTICE TYPE) WITH DETAILS |  |  |  | 0 | 0 | 0 | [6 empty] | 0 | [5 empty] | Lattice Structure | A
17.2.1 | 400 KV BEAM( Nominal Weight 3.5 MT appox) | NOS | 9 | 12 | 3 | 11 | 1 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | Lattice Structure | A
17.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 146 | 205 | 59 | 182 | 23 | 90817.076 | 90817.076 | 13259293.095 | 2386672.7571 | 15645965.852 | 16528707.8307 | 2088792.7478 | 18617500.5785 | 3351150.1041 | 21968650.6827 | 6322684.8306 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 Cost Data 2023 rate higher than BoQ. BoQ rate considered.. | Lattice Structure | B
17.4 | Total weight of different size of GI Nuts and bolts for structures. | MT | 13 | 18.5 | 5.5 | 16 | 2.5 | 112924.6768 | 112924.6768 | 1468020.7989 | 264243.7438 | 1732264.5428 | 1806794.8295 | 282311.6921 | 2089106.5216 | 376039.1739 | 2465145.6955 | 732881.1527 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 Cost Data 2023 rate higher than BoQ. BoQ rate considered.. | Lattice Structure | B
17.5 | SUPPORT STRUCTURES (Including foundation Bolts and Nuts) GALVANISED (PIPE TYPE) FOR ALL 400 KV equipments and 132 KV equipments near NGR |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.1 | ISOLATORS-400KV | SET | 10 | 10 | 0 | 10 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.2 | CTS-400 KV | SET | 12 | 12 | 0 | 12 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.3 | CVTS-400 KV | SET | 6 | 6 | 0 | 6 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.4 | Surge Arrester-400 Kv | SET | 12 | 12 | 0 | 12 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.5 | BPI-400 KV | SET | 48 | 59 | 11 | 59 | 0 | [6 empty] | 0 |  |  |  |  | As per approved Land Usage Plan TB-2-420-316-000-D Rev 00 & EKD TB-2-420-316-007-D Rev 00 | Pipe Structure | A
17.5.6 | ISOLATOR-132 KV | SET | 2 | 2 | 0 | 2 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.7 | CTS-132 KV | SET | 2 | 2 | 0 | 2 | 0 | [6 empty] | 0 | [5 empty] | Pipe Structure | A
17.5.8 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 55 | 75 | 20 | 68 | 7 | 97582.6354 | 97582.6354 | 5367044.9457 | 966068.0902 | 6333113.0359 | 6635619.2056 | 683078.4476 | 7318697.6533 | 1317365.5776 | 8636063.2308 | 2302950.1949 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 BoQ rate considered for higher Zinc galvanization of 910 gms/sqmm instead of 610 gsm/sqmm as per TS. | Pipe Structure | B
17.5.9 | Total weight of different size of GI Nuts and bolts for structures. | MT | 1.5 | 2 | 0.5 | 1 | 1 | 112924.6768 | 112924.6768 | 169387.0153 | 30489.6627 | 199876.678 | 112924.6768 | 112924.6768 | 225849.3537 | 40652.8837 | 266502.2373 | 66625.5593 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 Cost Data 2023 rate higher than BoQ. BoQ rate considered.. | Pipe Structure | B
18 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
18.1 | POWER CABLES,1.1KV,XLPE & PVC,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Cable | A
18.1.1 | PVC 3.5 CX70 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 421.3533 |  | 421353.3008 | 75843.5942 | 497196.895 | 421353.3008 | 0 | 421353.3008 | 75843.5942 | 497196.895 | 0 |  | Cable | A
18.1.2 | PVC 3.5 CX35 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 206.1942 |  | 206194.1685 | 37114.9503 | 243309.1188 | 206194.1685 | 0 | 206194.1685 | 37114.9503 | 243309.1188 | 0 |  | Cable | A
18.1.3 | PVC 4 CX 16 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 153.4005 |  | 153400.4925 | 27612.0887 | 181012.5812 | 153400.4925 | 0 | 153400.4925 | 27612.0887 | 181012.5812 | 0 |  | Cable | A
18.1.4 | PVC 4 CX 6 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 143.4394 |  | 143439.4216 | 25819.0959 | 169258.5174 | 143439.4216 | 0 | 143439.4216 | 25819.0959 | 169258.5174 | 0 |  | Cable | A
18.1.5 | PVC 2CX 6 mm2 | MTRS | 3000 | 3000 | 0 | 3000 | 0 | 71.7197 |  | 215159.1323 | 38728.6438 | 253887.7762 | 215159.1323 | 0 | 215159.1323 | 38728.6438 | 253887.7762 | 0 |  | Cable | A
18.2 | COPPER FLEXIBLE CONTROL CABLES,1.1 KV, PVC,FRLS, ARMOURED STRANDED (As per specification) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Cable | A
18.2.1 | 5 CX 2.5 mm2 | MTRS | 7000 | 7000 | 0 | 7000 | 0 | 184.2798 |  | 1289958.687 | 232192.5637 | 1522151.2507 | 1289958.687 | 0 | 1289958.687 | 232192.5637 | 1522151.2507 | 0 |  | Cable | A
18.2.2 | 10 CX 2.5 mm2 | MTRS | 5000 | 5000 | 0 | 5000 | 0 | 314.7698 |  | 1573849.2088 | 283292.8576 | 1857142.0664 | 1573849.2088 | 0 | 1573849.2088 | 283292.8576 | 1857142.0664 | 0 |  | Cable | A
18.2.3 | 16 CX 2.5 mm2 | MTRS | 3500 | 3500 | 0 | 3500 | 0 | 473.1509 |  | 1656028.0441 | 298085.0479 | 1954113.0921 | 1656028.0441 | 0 | 1656028.0441 | 298085.0479 | 1954113.0921 | 0 |  | Cable | A
18.2.4 | 19 CX 2.5 mm2 | MTRS | 3500 | 3500 | 0 | 3500 | 0 | 562.8005 |  | 1969801.7788 | 354564.3202 | 2324366.099 | 1969801.7788 | 0 | 1969801.7788 | 354564.3202 | 2324366.099 | 0 |  | Cable | A
18.2.5 | 4 CX 4 mm2 | MTRS | 6500 | 6500 | 0 | 6500 | 0 | 219.1436 |  | 1424433.1447 | 256397.966 | 1680831.1108 | 1424433.1447 | 0 | 1424433.1447 | 256397.966 | 1680831.1108 | 0 |  |  | A
19 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
19.1 | 24 fibre optic approach cable along with installation hardware including HDPE pipes | KM | 1 | 1 | 0 | 1 | 0 | 198995.3025 |  | 198995.3025 | 35819.1545 | 234814.457 | 198995.3025 | 0 | 198995.3025 | 35819.1545 | 234814.457 | 0 |  |  | A
19.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 2 | 2 | 0 | 2 | 0 | 340831.9878 |  | 681663.9756 | 122699.5156 | 804363.4912 | 681663.9756 | 0 | 681663.9756 | 122699.5156 | 804363.4912 | 0 |  |  | A
19.3 | Supply of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 1 | 1 | 0 | 1 | 0 | 70918.8407 |  | 70918.8407 | 12765.3913 | 83684.232 | 70918.8407 | 0 | 70918.8407 | 12765.3913 | 83684.232 | 0 |  |  | A
20 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Illumination | A
20.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj or any approved vendor of OPTCL) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | Nos | 50 | 50 | 0 | 50 | 0 | 61135.0768 |  | 3056753.84 | 550215.6912 | 3606969.5312 | 3056753.84 | 0 | 3056753.84 | 550215.6912 | 3606969.5312 | 0 |  | Illumination | A
20.2 | STREET LIGHTING, IT INCLUDES SUPPLY OF GI TUBULAR POLE, WITH LED LIGHTING FIXTURES WITH LAMPS of reputed make (Philips/CGL/Bajaj) (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos | 5 | 5 | 0 | 5 | 0 | 45037.9862 |  | 225189.9308 | 40534.1875 | 265724.1183 | 225189.9308 | 0 | 225189.9308 | 40534.1875 | 265724.1183 | 0 |  | Illumination | A
20.3 | INDOOR LIGHTING of EXTENDED CONTROL ROOM BUILDING: IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,Conduit & other required materials for succesful illumination of the area/rooms.( No. of LED Lighting fixtures are to be calculated based on the illumination design considering the required lux level indicated in the technical spec & fixing of the same rigidly on the suitable height either ceiling & wall as required.) | LOT | 1 | 1 | 0 | 1 | 0 | 2174539.6387 |  | 2174539.6387 | 391417.135 | 2565956.7737 | 2174539.6387 | 0 | 2174539.6387 | 391417.135 | 2565956.7737 | 0 |  | Illumination | A
21 | 2 TR (Two Ton) CAPACITY SPLIT 5 star AIR CONDITIONING UNITS inverter technology WITH REMOTE CONTROL FACILITY AND INCLUDING RELATED MATERIALS LIKE VOLTAGE STABILISER,CONTROL BOXES ETC FOR AIR CONDITIONING SYSTEM (AS PER SPECIFICATION ): FOR SWITCHYARD CONTROL ROOM. | NOS | 5 | 5 | 0 | 5 | 0 | 62790.6068 |  | 313953.034 | 56511.5461 | 370464.5801 | 313953.034 | 0 | 313953.034 | 56511.5461 | 370464.5801 | 0 |  | Air Conditioning | A
22 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | Fire Fighting System | A
22.1 | FOAM TYPE-9 LTRS | NOS | 1 | 1 | 0 | 1 | 0 | 4008.3349 |  | 4008.3349 | 721.5003 | 4729.8352 | 4008.3349 | 0 | 4008.3349 | 721.5003 | 4729.8352 | 0 |  | Fire Fighting System | A
22.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 17002.552 |  | 17002.552 | 3060.4594 | 20063.0113 | 17002.552 | 0 | 17002.552 | 3060.4594 | 20063.0113 | 0 |  | Fire Fighting System | A
22.3 | DRY POWDER TYPE - 5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 5580.1919 |  | 5580.1919 | 1004.4345 | 6584.6265 | 5580.1919 | 0 | 5580.1919 | 1004.4345 | 6584.6265 | 0 |  | Fire Fighting System | A
22.4 | CO2 - 4.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 6186.8212 |  | 6186.8212 | 1113.6278 | 7300.449 | 6186.8212 | 0 | 6186.8212 | 1113.6278 | 7300.449 | 0 |  | Fire Fighting System | A
22.5 | CO2 - 9 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 13028.0847 |  | 13028.0847 | 2345.0552 | 15373.1399 | 13028.0847 | 0 | 13028.0847 | 2345.0552 | 15373.1399 | 0 |  | Fire Fighting System | A
22.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 26132.8696 |  | 26132.8696 | 4703.9165 | 30836.7861 | 26132.8696 | 0 | 26132.8696 | 4703.9165 | 30836.7861 | 0 |  | Fire Fighting System | A
22.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 1 | 1 | 0 | 1 | 0 | 17642.0527 |  | 17642.0527 | 3175.5695 | 20817.6222 | 17642.0527 | 0 | 17642.0527 | 3175.5695 | 20817.6222 | 0 |  | Fire Fighting System | A
23 | COMPLETE SUB-STATION AUTOMATION SYSTEM FOR 400 KV BAY EXTENSION INCLUDING HARDWARE AND SOFTWARE FOR THE SUB-STATION AND REMOTE CONTROL SYSTEM ALONGWITH ASSOCIATED EQUIPMENT AND ACCESSORIES AS PER TECHNICAL SPECIFICATION & RELAY PROTECTION PANEL, EVENT LOGGER PANEL ,BUS BAR PROTN PAN & RELAY TOOL KITS AS PER TECH SPEC. The SAS & Bus Bar Protection scheme shall be integrated with the existing system. Allmaterials & equipment as required for successful completion shall be considered. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.1 | SUB-STATION AUTOMATION SYSTEM FOR PROPOSED 400 kv bay extension | SET | 1 | 1 | 0 | 1 | 0 | 273752.1438 |  | 273752.1438 | 49275.3859 | 323027.5297 | 273752.1438 | 0 | 273752.1438 | 49275.3859 | 323027.5297 | 0 | As per Record Notes of Meeting Dated 11-13 July 2023: OPTCL advised BHEL to follow the contract and propose technical solution so that the bays can be controlled from Main Control Room. BHEL indicated that this may require additional items such as Station level switch, HMIs etc., which will have commercial implication. OPTCL will resolve the issue | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.2 | BCU FOR CONTROLLING AND MONITORING OF THE PROPOSED (400 KV) | SET | 2 | 2 | 0 | 2 | 0 | 345770.6868 |  | 691541.3735 | 124477.4472 | 816018.8207 | 691541.3735 | 0 | 691541.3735 | 124477.4472 | 816018.8207 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.3 | 400 KV FEEDER PROTECTION RELAY PANEL(MAIN-I WITH AUTO RECLOSURE & MAIN-II WITH AUTO RECLOSURE AND BACK-UP PROTECTION ) AND TIE PROTECTION PANEL with Bus Bar Protection. | SET | 2 | 2 | 0 | 2 | 0 | 978850.5349 |  | 1957701.0698 | 352386.1926 | 2310087.2624 | 1957701.0698 | 0 | 1957701.0698 | 352386.1926 | 2310087.2624 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.4 | 400 KV LINE REACTOR AND 132 KV NGR PROTECTION RELAY PANEL | SET | 2 | 2 | 0 | 2 | 0 | 894435.4392 |  | 1788870.8784 | 321996.7581 | 2110867.6365 | 1788870.8784 | 0 | 1788870.8784 | 321996.7581 | 2110867.6365 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.5 | 400kV CB Panel for Switched reactor protection | SET | 2 | 2 | 0 | 2 | 0 | 519623.2501 |  | 1039246.5002 | 187064.37 | 1226310.8703 | 1039246.5002 | 0 | 1039246.5002 | 187064.37 | 1226310.8703 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.6 | 400kV Tie Protection Panel | Nos | 1 | 1 | 0 | 1 | 0 | 600651.5817 |  | 600651.5817 | 108117.2847 | 708768.8664 | 600651.5817 | 0 | 600651.5817 | 108117.2847 | 708768.8664 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
23.7 | Integration with existing Busbar protection & SAS system | SET | 1 | 1 | 0 | 1 | 0 | 5145191.9737 |  | 5145191.9737 | 926134.5553 | 6071326.529 | 5145191.9737 | 0 | 5145191.9737 | 926134.5553 | 6071326.529 | 0 |  | SUBSTATION AUTOMATION SYSTEM (SAS) | A
24 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO.19) | NOS | 1 | 1 | 0 | 1 | 0 | 41164.1257 |  | 41164.1257 | 7409.5426 | 48573.6683 | 41164.1257 | 0 | 41164.1257 | 7409.5426 | 48573.6683 | 0 |  | ALUMINIUM LADDER | A
25 | PEDESTAL MOUNTED WHEEL FITTED DERRICK FOR LIFTING/ LOWERING OF MATERIALS UP TO 1.5 TON CAPACITY.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 20) | SET | 1 | 1 | 0 | 1 | 0 | 58805.1823 |  | 58805.1823 | 10584.9328 | 69390.1151 | 58805.1823 | 0 | 58805.1823 | 10584.9328 | 69390.1151 | 0 |  |  | A
27 | OTHER TOOLS AND PLANTS (T&P's) : ANNEXURE - II : (REFER TS-VOL-II-E-25 TESTING INSTRUMENTS AND MAINTENANCE KITS OTHER TOOLS & PLANTS & FURNITURE) INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT) | LOT | 1 | 1 | 0 | 1 | 0 | 164678.417 |  | 164678.417 | 29642.1151 | 194320.5321 | 164678.417 | 0 | 164678.417 | 29642.1151 | 194320.5321 | 0 |  | Tools & Plants | A
28 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | NOS | 10 | 10 | 0 | 10 | 0 | 1470.2541 |  | 14702.5407 | 2646.4573 | 17348.998 | 14702.5407 | 0 | 14702.5407 | 2646.4573 | 17348.998 | 0 |  |  | A
29 | FIRE FIGHTING EQIPMENT (Main Pump,Jockey Pump,DG Set cum Pump, Control Panel,Different sizes of MS pipe(to be painted for rust proof),different type of valves,Fire sensor etc for the Fire Fighting System(HIGH PRESSURE : Hydrant and Mulsifire to take care of 2 Nos80 MVAR 400 KV Line Reactor. | LOT | 1 | 1 | 0 | 1 | 0 | 4802147.6321 |  | 4802147.6321 | 864386.5738 | 5666534.2058 | 4802147.6321 | 0 | 4802147.6321 | 864386.5738 | 5666534.2058 | 0 |  |  | A
30 | 400kV CT JB | Nos. | 4 | 4 | 0 | 4 | 0 | 30578.4956 |  | 122313.9823 | 22016.5168 | 144330.4991 | 122313.9823 | 0 | 122313.9823 | 22016.5168 | 144330.4991 | 0 |  |  | A
31 | 400kV CVT JB | Nos. | 4 | 2 | -2 | 2 | 0 | 30284.644 | 0 | 121138.5759 | 21804.9437 | 142943.5196 | 60569.288 | 0 | 60569.288 | 10902.4718 | 71471.7598 | -71471.7598 | As per approved SLD TB-3-420-510-001-D Only two Set CVts required hence 2 Nos. JB |  | B
32 | 433V ACK Distribution Board | Nos. | 1 | 1 | 0 | 1 | 0 | 39498.6346 |  | 39498.6346 | 7109.7542 | 46608.3888 | 39498.6346 | 0 | 39498.6346 | 7109.7542 | 46608.3888 | 0 |  |  | A
33 | 80 MVAR, 400 KV Line Reactor with Nitrogen Injection System for fire protection,online drying out system,Online dissolved gas(Multi gas) & moisture analyser and spares etc. as per Technical spec including all materials. |  |  |  |  | 0 | [7 empty] | 0 | [6 empty] | A
33.1 | 80 MVAR, 400 KV Line Reactor with accessories and spares as per Technical Spec. | Nos. | 2 | 2 | 0 | 2 | 0 | 58354459.3183 |  | 116708918.6366 | 21007605.3546 | 137716523.9912 | 116708918.6366 | 0 | 116708918.6366 | 21007605.3546 | 137716523.9912 | 0 |  | Reactor 80MVAr | A
33.2 | Type Test Charges for any one of the entire LOT of 80 MVAR, 400 KV Line Reactor for the following as per Technical Spec.: - Temperature Rise Test - Top oil and hot spot temperature rise test - Winding temperature rise test - Measurement of Zero Sequence Reactance -IP-55 Test | Lot | 1 | 1 | 0 | 1 | 0 | 418364.9796 |  | 418364.9796 | 75305.6963 | 493670.6759 | 418364.9796 | 0 | 418364.9796 | 75305.6963 | 493670.6759 | 0 |  | Reactor 80MVAr | A
33.3 | Other requirement of 80 MVAR, 400 KV Line Reactor as indicated belowas per Technical Spec: (i) Nitrogen Injection system for protection against fire & explosion(As per Technical Specification) (2 setsfor both the Line Reactor). (ii) Online insulating oil drying system(As per Technical Specification) (2 sets for both the Line Reactor) (iii) Online dissolved gas(Multi gas) & moisture analyser (As per Technical Specification) (2 sets for both the Line Reactor) | Lot | 1 | 1 | 0 | 1 | 0 | 10589235.9978 |  | 10589235.9978 | 1906062.4796 | 12495298.4774 | 10589235.9978 | 0 | 10589235.9978 | 1906062.4796 | 12495298.4774 | 0 |  | Reactor 80MVAr | A
34 | NGR, 132KV for above Line Reactor as per Technical spec including all materials & its accessories. | Nos. | 2 | 2 | 0 | 2 | 0 | 3909883.4423 |  | 7819766.8847 | 1407558.0392 | 9227324.9239 | 7819766.8847 | 0 | 7819766.8847 | 1407558.0392 | 9227324.9239 | 0 |  | Reactor NGR | A
[10 empty] | 1418108433.8754 | 255259518.0976 | 1673367951.9729 | 1455398801.0156 | 98190015.6268 | 1553588816.6423 | 279645986.9956 | 1833234803.6379 | 159866851.665

## ERECTION_SCHEDULE_VIIB
ODISHA POWER TRANSMISSION CORPORATION LIMITED
LOA No. - SGM-CPC-Construction-400/220kV GIS Ersama (Pkg-49/2021-22)-08/2020/828
Contractor: Bharat Heavy Electricals Limited
| ERECTION, INSTALLATION, TESTING & COMMISSIONING _SUBSTATION |  | Quantity |  |  |  |  | Unit Price |  | Amount As per Original BOQ |  |  | Amount As per Amendment-1 BOQ
Sl. No. | DESCRIPTION OF ITEMS | UNIT OF MEASUREMENT | QTY during Original Order | Total QTY as per actual | Differential Qty | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Unit Price as per BOQ | Unit Price as per least cost | Original BOQ Amount | Total GST @ 18% (Works contract), in INR | Total Amount including GST, in INR | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Total Amount | Total GST @ 18% , in INR | Total Amount inclusive GST after Amendment-1 | Differential Amount (BOQ Amount and Amended Amount) inclusive of GST | REMARKS
1 | 2 | 3 | 4 | 5 | 6=5-4 | 7 | 8 | 9 | 10 | 11=4*9 | 12 | 13=11+12 | 14=7*9 | 15=8*10 | 16=14+15 | 17 | 18=16+17 | 19=18-13
A | ELECTRICAL WORKS Ersama SUB-STATION
1 | 3150A, 63kA for 3s, one and half Circuit Breaker (Circuit breaker shall be C2 - M2 class as per IEC 62271-100) arrangement. 420KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203.
1.1 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector,grounding switches & line PT), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated circuit breaker , current transformer (6 core), line Potential transformer (3 cores), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 222992.3844 |  | 445984.7687 | 80277.2584 | 526262.0271 | 445984.7687 | 0 | 445984.7687 | 80277.2584 | 526262.0271 | 0 |  | A
1.2 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector,grounding switches etc), SF6 gas insulated (Bus Reactor) bay module with CSD (Control Switching Device) each comprising of SF6 gas insulated circuit breaker with CSD (Control Switching Device), current transformer (6 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through, different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to completeBus reactor bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 1 | 2 | 1 | 1 | 1 | 192858.865 | 192858.865 | 192858.865 | 34714.5957 | 227573.4607 | 192858.865 | 192858.865 | 385717.7299 | 69429.1914 | 455146.9213 | 227573.4607 | Revised qty as per approved SLD (Drg. No. TB-3-420-510-001) Rate Contract Rate not available | B | 15110440.4194
1.3 | 420kV, 3150A, 63KA for (3 sec for CB & 1 sec for CT,Disconnector,grounding switches etc) SF6 gas insulated ICT feeder bay module each comprising of SF6 gas insulated circuit breaker with CSD (Control Switching Device), current transformer (6 cores), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through, different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete ICT feeder bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. . | Set | 2 | 2 | 0 | 2 | 0 | 192858.865 |  | 385717.7299 | 69429.1914 | 455146.9213 | 385717.7299 | 0 | 385717.7299 | 69429.1914 | 455146.9213 | 0 |  | A
1.4 | 420kV, 3150A, 63KA (3 sec for CB & 1 sec for CT,Disconnector & grounding switches), SF6 gas insulated Tie bay module with CSD (Control Switching Device) each comprising of SF6 gas insulated circuit breaker with CSD (Control Switching Device), current transformer (6 core), Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Tie bay module & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 3 | 3 | 0 | 3 | 0 | 192858.865 |  | 578576.5949 | 104143.7871 | 682720.382 | 578576.5949 | 0 | 578576.5949 | 104143.7871 | 682720.382 | 0 |  | A
1.5 | 420kV, 3150A, 63KA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T) , 3- phase Isolated , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), dis connectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 , different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement for the GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. . | Set | 2 | 2 | 0 | 2 | 0 | 148087.7399 |  | 296175.4798 | 53311.5864 | 349487.0662 | 296175.4798 | 0 | 296175.4798 | 53311.5864 | 349487.0662 | 0 |  | A
1.6 | 420kV, 3150 A, 63kA, 3 Sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed]outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) etc. as per the technical specification. (The GIBus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 1050 | 1400 | 350 | 1312 | 88 | 1096.0693 | 1096.0693 | 1150872.7424 | 207157.0936 | 1358029.836 | 1438042.8934 | 96454.0965 | 1534496.9899 | 276209.4582 | 1810706.4481 | 452676.612 | Revised qty as per approved LUP (Drg. No. TB-420-316-000) Rate Contract Rate not available | B | -322141.3709
1.7 | 420kV, 3150 A, 63kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with support structure. | NO | 15 | 15 | 0 | 15 | 0 | 12053.8024 |  | 180807.0357 | 32545.2664 | 213352.3021 | 180807.0357 | 0 | 180807.0357 | 32545.2664 | 213352.3021 | 0 |  | A
1.8 | Online continuous Partial Discharge Monitoring System (PDM): 420 KV & 245 KV GIS equipment system shall have Online continuous Partial Discharge Monitoring System (PDM) system to provide an automatic facility for the simultaneous collection of PD data at multiple points on the GIS & its associated GIB ducts and Voltage Transformers adopting UHF technique & the data stored shall provide a historical record of the progress of PD sources and shall identify the areas of maximum activity. PDM system shall be interfacing with UHF PD couplers provided.The PD Monitoring PC Work Station alongwith all accessories shall be considered. Power supply to PDM PC shall have protection against surges, overload and short circuit. A dedicated on-line UPS system shall also be provided as a backup during supply interruption, to ensure trouble-free & reliable running of the PDM System for a minimum of 15 minutes duration. | SET | 1 | 1 | 0 | 1 | 0 | 112994.7783 |  | 112994.7783 | 20339.0601 | 133333.8384 | 112994.7783 | 0 | 112994.7783 | 20339.0601 | 133333.8384 | 0 |  | A
2 | 245KV GIS EQUIPMENT as per latest IEC standard & type tested equipment as per technical specification, with open future proof & flexible system in line with IEC 61850 & IEC 62271-203. (Circuit breaker shall be C2 - M2 class as per IEC 62271-100). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
2.1 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T ) SF6 gas insulated ICT feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete ICT feeder bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 113423.9324 |  | 226847.8648 | 40832.6157 | 267680.4804 | 226847.8648 | 0 | 226847.8648 | 40832.6157 | 267680.4804 | 0 |  | A
2.2 | 245kV, 3150A,50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T), SF6 gas insulated line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer,Line Potential Transformer (3 core), bus-bar dis connectors with common grounding switch, Motorised dis connectors with safety grounding switch(es), high speed fault making motorised grounding switch, Local control cubicle, SF6 gas monitoring system for complete bay, SF6 bus duct termination arrangement,PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete line feeder bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 4 | 4 | 0 | 4 | 0 | 131146.5143 |  | 524586.0572 | 94425.4903 | 619011.5475 | 524586.0572 | 0 | 524586.0572 | 94425.4903 | 619011.5475 | 0 |  | A
2.3 | 245kV , 3150A, 50 kA ( 3 sec for Bus bar ,1 sec for disconnector,grounding switch & bus P.T), 3- phase Isolated , SF6 gas insulated , metal enclosed bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with bus potential transformer (3 core), dis connectors , bus bar grounding switch, SF6 gas monitoring system PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete the bus & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 2 | 2 | 0 | 2 | 0 | 76206.905 |  | 152413.8099 | 27434.4858 | 179848.2957 | 152413.8099 | 0 | 152413.8099 | 27434.4858 | 179848.2957 | 0 |  | A
2.4 | 245kV, 3150A, 50 kA (3 sec for CB & 1 sec for Disconnector,Grounding switch,C.T) SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, dis connectors switches, disconnector with safety grounding switch(es). Local control cubicle, SF6 gas monitoring system, PD sensor (adequate number of UHF sensors in the offered GIS equipment for detection of Partial discharge (of 5 pC and above) as per IEC 60270 through Partial Discharge (PD) monitoring system), different gas compartment, O- ring & gaskets,Nuts, Bolts & Washers Absorbent,Limit Switch ,SF6 Gas , etc to complete Bus Coupler bay module & its earthing arrangement for GIS equipment with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification. | Set | 1 | 1 | 0 | 1 | 0 | 134691.228 |  | 134691.228 | 24244.421 | 158935.649 | 134691.228 | 0 | 134691.228 | 24244.421 | 158935.649 | 0 |  | A
2.5 | 245kV, 3150A, 50 kA, 3 sec, single phase, SF6 gas Insulated Bus Duct [The service condition shall be as per IEC-62271-203- (Special - Outdoor) to be followed] outside GIS Hall alongwith associated Support structure arrangement bends, joints,accessories, & its earthing arrangement with earthing strips of adequate size (as per IEEE-80-2000 and CIGRE44 to protect operating staff against any hazardous touch voltages and electro-magnetic interferences) as per the technical specification etc. (The GIBus duct quantity will be calculated from the end of the GIS module and shall include both the indoor and outdoor GIB) | RM | 750 | 1000 | 250 | 937 | 63 | 645.2109 | 645.2109 | 483908.1738 | 87103.4713 | 571011.6451 | 604562.6118 | 40648.2866 | 645210.8984 | 116137.9617 | 761348.8601 | 190337.215 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate Contract Rate not available | B
2.6 | 245kV, 3150A, 50 kA SF6/Air BUSHING ( Bushing shall be of Polymer / composite insulator type and shall be seamless sheath of a silicone rubber compound. The hollow silicone composite insulators shall comply as per IEC 61462 and the relevant parts of IEC 62217. The design of the composite insulators shall be tested and verified according to IEC 61462 ) FOR CONNECTING GIS TO AIS along with support structure. | NO | 18 | 18 | 0 | 18 | 0 | 7089.4274 |  | 127609.6931 | 22969.7448 | 150579.4379 | 127609.6931 | 0 | 127609.6931 | 22969.7448 | 150579.4379 | 0 |  | A
3 | 420KV 1 phase Solid core bus post insulator (AIS) as per technical specification. | NOS | 16 | 21 | 5 | 20 | 1 | 2175.367 | 2175.367 | 34805.8723 | 6265.057 | 41070.9293 | 43507.3404 | 2175.367 | 45682.7074 | 8222.8873 | 53905.5948 | 12834.6654 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) Rate Contract 2023 rate higher than BoQ rate. BoQ rate considered. | B
4 | 245KV 1 phase Solid core bus post insulator (AIS) as per technical specification. | NOS | 24 | 18 | -6 | 18 | 0 | 1740.2936 |  | 41767.0468 | 7518.0684 | 49285.1152 | 31325.2851 | 0 | 31325.2851 | 5638.5513 | 36963.8364 | -12321.2788 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | B
5 | 390KV metal oxide polymer housed surge arrrestor, 20 KA , Long duration discharge class IV ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 24 | 15 | -9 | 15 | 0 | 4233.3333 |  | 101599.9987 | 18287.9998 | 119887.9985 | 63499.9992 | 0 | 63499.9992 | 11429.9999 | 74929.9991 | -44957.9994 | Revised qty as per approved SLD (Drg. No. TB-3-420-510-001) | B
6 | 216KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 216KV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 18 | 18 | 0 | 18 | 0 | 3625.6117 |  | 65261.0106 | 11746.9819 | 77007.9925 | 65261.0106 | 0 | 65261.0106 | 11746.9819 | 77007.9925 | 0 |  | A
7 | 30KV metal oxide polymer housed surge arrrestor, 10KA Long duration discharge class III at 30kV, pressure relief Design B & thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification. | NOS | 12 | 12 | 0 | 12 | 0 | 1088.1768 |  | 13058.1215 | 2350.4619 | 15408.5834 | 13058.1215 | 0 | 13058.1215 | 2350.4619 | 15408.5834 | 0 |  | A
8 | 36 KV ,1250A, 31.5 KA for 1 sec, isolator (single isolator with earth switch) including post insulators as per technical specification | SET | 2 | 2 | 0 | 2 | 0 | 6789.5128 |  | 13579.0257 | 2444.2246 | 16023.2503 | 13579.0257 | 0 | 13579.0257 | 2444.2246 | 16023.2503 | 0 | 33kV Isolator with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | A
9 | 36 KV,1250 A,31.5 KA 3 Sec,Vacuum Circuit Breaker with supporting GI structures as per technical specification. | SET | 2 | 2 | 0 | 2 | 0 | 7251.2234 |  | 14502.4468 | 2610.4404 | 17112.8872 | 14502.4468 | 0 | 14502.4468 | 2610.4404 | 17112.8872 | 0 | 33kV SF6 Circuit Breaker with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | A
10 | 36 KV , 31.5 KA for 1 sec ,1200-600/1-1-1-1 A, Current Transformer as per technical specification | Nos | 6 | 6 | 0 | 6 | 0 | 1485.7609 |  | 8914.5653 | 1604.6217 | 10519.187 | 8914.5653 | 0 | 8914.5653 | 1604.6217 | 10519.187 | 0 | 33kV CT with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | A
11 | 36 KV , 31.5 KA for 1 sec , 50-25/1-1 A, Current Transformer as per technical specification | Nos | 6 | 6 | 0 | 6 | 0 | 1485.7609 |  | 8914.5653 | 1604.6217 | 10519.187 | 8914.5653 | 0 | 8914.5653 | 1604.6217 | 10519.187 | 0 | 33kV CT with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | A
11.1 | CT Console Box for above 36KV CTs | Nos | 4 | 4 | 0 | 4 | 0 | 3066.2316 |  | 12264.9264 | 2207.6868 | 14472.6132 | 12264.9264 | 0 | 12264.9264 | 2207.6868 | 14472.6132 | 0 |  | A
12 | 36 KV Bus Post Insulator as per technical specification | Nos | 12 | 12 | 0 | 12 | 0 | 742.8804 |  | 8914.5653 | 1604.6217 | 10519.187 | 8914.5653 | 0 | 8914.5653 | 1604.6217 | 10519.187 | 0 | 33kV Post Insulator with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) | A
13 | All type of Terminal clamp & connectors suitable for 36 KV, 1250 A for station transformers. | LOT | 1 | 1 | 0 | 1 | 0 | 6780.6338 |  | 6780.6338 | 1220.5141 | 8001.1479 | 6780.6338 | 0 | 6780.6338 | 1220.5141 | 8001.1479 | 0 |  | A
14 | BUS BAR & CIRCUIT MATERIALS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
14.1 | 160 KN LR Antifog INSULATOR STRINGS (SUSPENSION & TENSION) 420 KV side suitable for the arrangement as expalined below. Brief description regarding use: (a) Provision of suspension insulators to hold the Quad conductor arrangement from the other end of Aluminium tube to 400 KV gantry for 400 KV line feeder. | SET | 12 | 33 | 21 | 15 | 18 | 2610.4404 | 2610.4404 | 31325.2851 | 5638.5513 | 36963.8364 | 39156.6064 | 46987.9276 | 86144.534 | 15506.0161 | 101650.5501 | 64686.7137 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) BoQ rates considered as RC rates not available. | B
14.2 | 160 KN LR Antifog INSULATOR STRINGS for Single Suspension Single/ Moose cond (SUSPENSION & TENSION) 245 KV side for the arrangement as explained below. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
14.2.1 | (a) Provision of suspension insulators to hold the single conductor arrangement from the other end of the Aluminium tube to 220 KV gantry for 220 KV line feeder.=12 sets | SET | 12 | 12 | 0 | 12 | 0 | 2175.367 |  | 26104.4042 | 4698.7928 | 30803.197 | 26104.4042 | 0 | 26104.4042 | 4698.7928 | 30803.197 | 0 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | A
14.2.2 | (b) Provision of suspension insulators to hold the Quad conductor arrangement from other end of Aluminium tube to 220 KV gantry both side of the road near ICT 220 KV side for 220 KV ICT feeder.= 12 sets | SET | 12 | 0 | -12 | 0 | 0 | 2175.367 |  | 26104.4042 | 4698.7928 | 30803.197 | 0 | 0 | 0 | 0 | 0 | -30803.197 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | B
14.2.3 | (c) Provision of tension insulators for holding the Quad conductor arrangement from 220 KV gantry near the ICT to cross the road & to other end gantry for 220 KV ICT feeder.=12 sets. | SET | 12 | 0 | -12 | 0 | 0 | 2465.416 |  | 29584.9915 | 5325.2985 | 34910.2899 | 0 | 0 | 0 | 0 | 0 | -34910.2899 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) | B
14.3 | ACSR MOOSE CONDUCTOR | Mtrs | 1500 | 3600 | 2100 | 1875 | 1725 | 73.9921 | 73.9921 | 110988.1133 | 19977.8604 | 130965.9736 | 138735.1416 | 127636.3302 | 266371.4718 | 47946.8649 | 314318.3367 | 183352.3631 | Revised qty as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) BoQ Rate considered since RC rate is not available. | B
14.4 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. Brief description regarding use: (a) Upto the 400 KV Gantry from SF6 to Air Bushing for 400 KV Line. (b) Upto 400 KV SA near ICT from SF6 to Air Bushing for ICT. (c) Upto the 220 KV Gantry from SF6 to Air Bushing for 220 KV side of ICT. (d) Upto the 220 KV Gantry from SF6 to Air Bushing for 220 KV Line. | MTR | 650 | 650 | 0 | 650 | 0 | 430.1406 |  | 279591.3893 | 50326.4501 | 329917.8394 | 279591.3893 | 0 | 279591.3893 | 50326.4501 | 329917.8394 | 0 |  | A
14.5 | All types of HARDWARES & FITTINGS/SPACERS/CLAMPS & CONNECTORS FOR 400KV SIDE OF THE GIS S/S. | Lot | 1 | 1 | 0 | 1 | 0 | 192110.0652 |  | 192110.0652 | 34579.8117 | 226689.8769 | 192110.0652 | 0 | 192110.0652 | 34579.8117 | 226689.8769 | 0 |  | A
14.6 | All types of HARDWARES & FITTINGS/SPACERS/CLAMPS & CONNECTORS FOR 220 KV SIDE OF THE GIS S/S. | Lot | 1 | 1 | 0 | 1 | 0 | 128361.4526 |  | 128361.4526 | 23105.0615 | 151466.5141 | 128361.4526 | 0 | 128361.4526 | 23105.0615 | 151466.5141 | 0 |  | A
15 | SUBSTATION EARTHING SYSTEMS:Substation earth-mat: (a) Laying of earth-mat conductors of of size 40mm dia Rod, excavation of earth for laying of earth flat as per approved drawing, welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc of ground conductors & etc with back filling and good compaction.The spacing between the earth conductor not more than 5 mtrs(both way) and to be buried at depth of 700mm from the finished ground level. (b) 40 mm MS solid rod: Provision of grounding driven 40 mm MS Solid rod, (c) 50 mm,3 mtr long Heavy duty perforated GI pipes: for treated earth pits (with details of treatment as per IS). (d) Provision of water taps inside the switch yard areas and peripheral for treated earth pit for watering the treated earth pits. Note: The no. of treated and un treated earth pits are to be done as per the practice and as indicated in the drawing for different equipment. (e) The erection of risers of size 50X6 mm /75X10 mm GI flats including welding/jointing ,application of two coats of bituminous Paint,wrapping of HT Tape etc as per requirement. This is as per approved drawing and specification. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
'15.1 | EARTHING CONDUCTOR FOR BURRIAL & RAISER FROM MAT UPTO THE REQUIRED HEIGHT BELOW GROUND : 40 mm MS Rod for laying (spacing maximum 5m both way) | Mtrs | 7500 | 35000 | 27500 | 9375 | 25625 | 146.9976 | 146.9976 | 1102481.925 | 198446.7465 | 1300928.6715 | 1378102.4063 | 3766813.2438 | 5144915.6501 | 926084.817 | 6071000.4672 | 4770071.7956 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) BoQ Rate considered since RC rate is not available. | B
'15.2 | EARTHING CONDUCTOR: 75X 10 mm GI (HDG) Flat for Raiser from the burial earth mat to equipment,structure etc) | Mtrs | 1500 | 5300 | 3800 | 1875 | 3425 | 72.019 | 67.39 | 108028.4302 | 19445.1174 | 127473.5477 | 135035.5378 | 230810.75 | 365846.2878 | 65852.3318 | 431698.6196 | 304225.0719 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) RC 2023 rate Sl no. 21.2(vi.b) for Riser considered since lower than BoQ rate. | B
'15.3 | EARTHING CONDUCTOR: 50X6mm GI (HDG) Flat for Raiser for console box,LT panels,DC panels,Marshalling boxes etc) | Mtrs | 750 | 8900 | 8150 | 937 | 7963 | 67.0861 | 67.0861 | 50314.6113 | 9056.63 | 59371.2414 | 62859.7211 | 534207.0002 | 597066.7213 | 107472.0098 | 704538.7311 | 645167.4897 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) BoQ Rate considered since lower than RC rate | B
'15.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) | Nos | 150 | 380 | 230 | 187 | 193 | 8889.9012 | 8889.9012 | 1333485.1848 | 240027.3333 | 1573512.518 | 1662411.5303 | 1715750.9377 | 3378162.4681 | 608069.2442 | 3986231.7123 | 2412719.1943 | Revised qty as per Earthmat layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-008) BoQ rate considered for additional requirement of water tap arrangement. | B
'15.5 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | Nos | 100 | 0 | -100 | 0 | 0 | 638.305 | 0 | 63830.4971 | 11489.4895 | 75319.9866 | 0 | 0 | 0 | 0 | 0 | -75319.9866 |  | B
'15.6 | 100sqmm copper braid for gate earthing. | Lot | 1 | 1 | 0 | 1 | 0 | 6147.2616 |  | 6147.2616 | 1106.5071 | 7253.7687 | 6147.2616 | 0 | 6147.2616 | 1106.5071 | 7253.7687 | 0 |  | A
16 | G.I Cable Trays including support GI angle suitable for different sections along with its accessories as per TS. Details of No. of tiers are indicated in the TS-Civil Section accordingly the requirement can be ascertained. |  |  |  |  | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
16.1 | G.I Cable Trays(size: 450x75x2500mm) | MTRS | 1500 | 4875 | 3375 | 1875 | 3000 | 57.2205 | 57.2205 | 85830.8076 | 15449.5454 | 101280.353 | 107288.5095 | 171661.6152 | 278950.1247 | 50211.0224 | 329161.1471 | 227880.7941 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate not available, BoQ rate considered. | B
16.2 | G.I Cable Trays(size: 300x75x2500mm) | MTRS | 1250 | 1750 | 500 | 1562 | 188 | 57.2205 | 57.2205 | 71525.673 | 12874.6211 | 84400.2941 | 89378.481 | 10757.4612 | 100135.9422 | 18024.4696 | 118160.4118 | 33760.1177 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate not available, BoQ rate considered. | B
16.3 | G.I Cable Trays(size: 150x75x2500mm) | MTRS | 1000 | 250 | -750 | 250 | 0 | 57.2205 | 0 | 57220.5384 | 10299.6969 | 67520.2353 | 14305.1346 | 0 | 14305.1346 | 2574.9242 | 16880.0588 | -50640.1765 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate not available, BoQ rate considered. | B
16.4 | Support G. I angle 50x50x6 mm for cable tray | MT | 5 | 13.3 | 8.3 | 6 | 7.3 | 34364.8795 | 4533.3 | 171824.3977 | 30928.3916 | 202752.7893 | 206189.2773 | 33093.09 | 239282.3673 | 43070.8261 | 282353.1934 | 79600.4041 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
17 | SWITCH YARD AC CONSOLE (Al alloy box painted with enamel gray colour) FOR LIGHTING (01 nos each on 400KV side & 220 kv side and other area ) as per Technical Specification. | NOS | 3 | 3 | 0 | 3 | 0 | 5199.1765 |  | 15597.5295 | 2807.5553 | 18405.0848 | 15597.5295 | 0 | 15597.5295 | 2807.5553 | 18405.0848 | 0 |  | A
18 | SWITCH YARD RECEPTACLE BOARD (Al alloy box painted with enamel gray colour) FOR TFR OIL FILTERATION (01 no. near 400/220KV ICT) as per Technical Specification. | NOS | 1 | 1 | 0 | 1 | 0 | 8398.5939 |  | 8398.5939 | 1511.7469 | 9910.3407 | 8398.5939 | 0 | 8398.5939 | 1511.7469 | 9910.3407 | 0 |  | A
19 | SWITCH YARD RECEPTACLE BOARD (Al alloy box painted with enamel gray colour) FOR WELDING & OTHER EMERGENCY as per Technical Specification. | NOS | 1 | 1 | 0 | 1 | 0 | 5199.1765 |  | 5199.1765 | 935.8518 | 6135.0283 | 5199.1765 | 0 | 5199.1765 | 935.8518 | 6135.0283 | 0 |  | A
20 | HDG SWITCH YARD STRUCTURES (INCLUDING FOUNDATION BOLTS) FOR 400Kv & 220KV CLASS (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.1 | DIFFERENT TYPES OF LATICE TYPE COLUMNS & DIFFERENT TYPE OF BEAMS AND LIGHTING CUM LIGHTNING MAST.(Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.1.1 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 52 | 186.2 | 134.2 | 65 | 121.2 | 5441.8705 | 4533.3 | 282977.2667 | 50935.908 | 333913.1747 | 353721.5834 | 549435.96 | 903157.5434 | 162568.3578 | 1065725.9012 | 731812.7265 | No. of towers & beams as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
20.2 | DIFFERENT TYPE OF SUPPORT STRUCTURES (HDG) OF PIPE TYPE FOR ALL 400KV, 220KV & 33 KV EQUIPMENT INCLUDING HIGH LEVEL SA NEAR TRANSFORMER. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.2.1 | TOTAL WEIGHT OF PIPE TYPE SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 55 | 55 | 0 | 55 | 0 | 4595.4012 |  | 252747.0643 | 45494.4716 | 298241.5359 | 252747.0643 | 0 | 252747.0643 | 45494.4716 | 298241.5359 | 0 |  | A
20.2.2 | 40 Mtrs heigh Monopole Lighting cum Lightning Mast with control gear panel etc suitable for wind zone-VI.(Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). | Nos | 3 | 3 | 0 | 3 | 0 | 303730.564 |  | 911191.6921 | 164014.5046 | 1075206.1966 | 911191.6921 | 0 | 911191.6921 | 164014.5046 | 1075206.1966 | 0 |  | A
21 | Total weight of different type of GI Nuts and bolts for the above structures. (Galvanization thisckness shall be minimum 910gm/sqm as these are to be installed in coastal area). | MT | 5.6 | 9 | 3.4 | 7 | 2 | 5650.0349 | 4533.3 | 31640.1954 | 5695.2352 | 37335.4305 | 39550.2442 | 9066.6 | 48616.8442 | 8751.032 | 57367.8762 | 20032.4456 | No. of towers & beams as per Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A) RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
22 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
22.1 | POWER CABLES,1.1KV,XLPE & PVC FRLS ,FLAT STRIP ARMOURED, ALUMINIUM CONDUCTOR (As per Specification). Provision of Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building.(Refer the scope pof work Vol-II) including supply & fixing. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
22.1.1 | XLPE-1CX 630 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 222.9628 |  | 668888.3626 | 120399.9053 | 789288.2678 | 668888.3626 | 0 | 668888.3626 | 120399.9053 | 789288.2678 | 0 |  | A
22.1.2 | XLPE-1CX 300 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 86.8174 |  | 86817.3686 | 15627.1263 | 102444.4949 | 86817.3686 | 0 | 86817.3686 | 15627.1263 | 102444.4949 | 0 |  | A
22.1.3 | XLPE-3.5 CX185 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 54.2609 |  | 27130.4277 | 4883.477 | 32013.9047 | 27130.4277 | 0 | 27130.4277 | 4883.477 | 32013.9047 | 0 |  | A
22.1.4 | XLPE-3.5 CX120 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 38.4759 |  | 19237.9396 | 3462.8291 | 22700.7688 | 19237.9396 | 0 | 19237.9396 | 3462.8291 | 22700.7688 | 0 |  | A
22.1.5 | PVC-3.5 CX70 mm2 | Mtrs | 250 | 250 | 0 | 250 | 0 | 41.4356 |  | 10358.8906 | 1864.6003 | 12223.4909 | 10358.8906 | 0 | 10358.8906 | 1864.6003 | 12223.4909 | 0 |  | A
22.1.6 | PVC-3.5 CX35 mm2 | Mtrs | 500 | 500 | 0 | 500 | 0 | 30.5834 |  | 15291.6956 | 2752.5052 | 18044.2008 | 15291.6956 | 0 | 15291.6956 | 2752.5052 | 18044.2008 | 0 |  | A
22.1.7 | PVC-4 CX 16 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 25.6506 |  | 25650.5862 | 4617.1055 | 30267.6917 | 25650.5862 | 0 | 25650.5862 | 4617.1055 | 30267.6917 | 0 |  | A
22.1.8 | PVC-4 CX 6 mm2 | Mtrs | 1000 | 1000 | 0 | 1000 | 0 | 25.6506 |  | 25650.5862 | 4617.1055 | 30267.6917 | 25650.5862 | 0 | 25650.5862 | 4617.1055 | 30267.6917 | 0 |  | A
22.1.9 | PVC-2CX 6 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 25.6506 |  | 51301.1724 | 9234.211 | 60535.3834 | 51301.1724 | 0 | 51301.1724 | 9234.211 | 60535.3834 | 0 |  | A
22.2 | CONTROL CABLES,1.1 KV,PVC FRLS , COPPER STRANDED ARMOURED STRANDED(As per specification). Provision of Modular Multi-diameter flexible Cable sealing system consisting of frames, blocks and accessories to be installed wherever the electrical / control / communication cables over-ground enter or leave from control room building.(Refer the scope pof work Vol-II) including supply & fixing. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
22.2.1 | 2 CX 2.5 mm2 | Mtrs | 2500 | 2500 | 0 | 2500 | 0 | 23.6775 |  | 59193.6604 | 10654.8589 | 69848.5193 | 59193.6604 | 0 | 59193.6604 | 10654.8589 | 69848.5193 | 0 |  | A
22.2.2 | 4 CX 4 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 23.6775 |  | 47354.9283 | 8523.8871 | 55878.8154 | 47354.9283 | 0 | 47354.9283 | 8523.8871 | 55878.8154 | 0 |  | A
22.2.3 | 4 CX 2.5 mm2 | Mtrs | 6000 | 6000 | 0 | 6000 | 0 | 23.6775 |  | 142064.785 | 25571.6613 | 167636.4463 | 142064.785 | 0 | 142064.785 | 25571.6613 | 167636.4463 | 0 |  | A
22.2.4 | 5 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 25.6506 |  | 102602.3447 | 18468.422 | 121070.7667 | 102602.3447 | 0 | 102602.3447 | 18468.422 | 121070.7667 | 0 |  | A
22.2.5 | 7CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 25.6506 |  | 102602.3447 | 18468.422 | 121070.7667 | 102602.3447 | 0 | 102602.3447 | 18468.422 | 121070.7667 | 0 |  | A
22.2.6 | 10 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 25.6506 |  | 102602.3447 | 18468.422 | 121070.7667 | 102602.3447 | 0 | 102602.3447 | 18468.422 | 121070.7667 | 0 |  | A
22.2.7 | 12 CX 2.5 mm2 | Mtrs | 2000 | 2000 | 0 | 2000 | 0 | 28.6103 |  | 57220.5384 | 10299.6969 | 67520.2353 | 57220.5384 | 0 | 57220.5384 | 10299.6969 | 67520.2353 | 0 |  | A
22.2.8 | 16 CX 2.5 mm2 | Mtrs | 4000 | 4000 | 0 | 4000 | 0 | 30.5834 |  | 122333.5648 | 22020.0417 | 144353.6065 | 122333.5648 | 0 | 122333.5648 | 22020.0417 | 144353.6065 | 0 |  | A
22.2.9 | 19 CX 2.5 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 35.5162 |  | 106548.5887 | 19178.746 | 125727.3347 | 106548.5887 | 0 | 106548.5887 | 19178.746 | 125727.3347 | 0 |  | A
22.2.10 | 27 CX 2.5 mm2 | Mtrs | 3000 | 3000 | 0 | 3000 | 0 | 49.3281 |  | 147984.151 | 26637.1472 | 174621.2982 | 147984.151 | 0 | 147984.151 | 26637.1472 | 174621.2982 | 0 |  | A
22.2.11 | 1CX 120 mm2 BAT TO BAT CHARGER & CHARGER TO DCDB | Mtrs | 300 | 300 | 0 | 300 | 0 | 66.0996 |  | 19829.8762 | 3569.3777 | 23399.254 | 19829.8762 | 0 | 19829.8762 | 3569.3777 | 23399.254 | 0 |  | A
23 | HARD CONDUIT INCLUDING of adequate tensile strength minimum 7kg/sqmm or better & ITS ACCESSORIES LIKE ALL TYPE OF SOCKETS & BENDS FOR TAKING CABLE FROM TRENCH TO EQUIPMENT MB etc | LOT | 1 | 1 | 0 | 1 | 0 | 289872.3416 |  | 289872.3416 | 52177.0215 | 342049.363 | 289872.3416 | 0 | 289872.3416 | 52177.0215 | 342049.363 | 0 |  | A
24 | SUPPLY OF STATION TRANSFORMER & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION AS PER TECHNICAL SPECIFICATION |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
24.1 | STATION TRANSFORMER 33KV/433V,1000 KVA (AS PER SPECIFICATION) | NOS | 2 | 2 | 0 | 2 | 0 | 24531.826 |  | 49063.652 | 8831.4574 | 57895.1093 | 49063.652 | 0 | 49063.652 | 8831.4574 | 57895.1093 | 0 |  | A
24.2 | OUT DOOR KIOSK MADE OUT OF 3mm thick Al alloy box painted with enamel gray colour having gland plates OR BETTER quality WITH 3 NOS. OF CUT-OUTS(1000 AMPS) AT THE INCOMING SIDE , 1No. OF 3 PHASE SFU (500/1000 AMPS) AT THE OUTGOING SIDE AND SUITABLE BUS BAR ARRANGEMENT FOR TERMINATION of incoming cable from transformer & outgoing cable to Main ACDB. | SET | 2 | 2 | 0 | 2 | 0 | 29001.9339 |  | 58003.8678 | 10440.6962 | 68444.564 | 58003.8678 | 0 | 58003.8678 | 10440.6962 | 68444.564 | 0 |  | A
25 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area). The switchyard lights to be controlled by lux meter for variable lux output of the luminaire as per ambient light. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
25.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be achieved).(150 watt each) | SET | 40 | 40 | 0 | 40 | 0 | 1577.511 |  | 63100.442 | 11358.0796 | 74458.5215 | 63100.442 | 0 | 63100.442 | 11358.0796 | 74458.5215 | 0 |  | A
26 | STREET LIGHTING: IT INCLUDES GI TUBULAR POLE AS PER TECHNICAL SPECIFICATION, LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. (TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
26.1 | LED LIGHTING FIXTURES including LAMPS of reputed make (Philips/CGL/Bajaj).(100 watt each) for Street Light. | SET | 40 | 40 | 0 | 40 | 0 | 1577.511 |  | 63100.442 | 11358.0796 | 74458.5215 | 63100.442 | 0 | 63100.442 | 11358.0796 | 74458.5215 | 0 |  | A
26.2 | GI Tubular Pole: (410-SP-24: IS 2713-Part-II-1980 or latest) Length of pole 8.5 mtrs(minimum weight 158 Kgs). (ALL THE STREET LIGHT POLE SHALL BE OF GI TUBULAR POLE AND PROVISION OF A GI JUNCTION BOX WITH SUITABLE COVERS AT A HEIGHT OF 1 METRE FROM THE GROUND. THE JUNCTION BOX SHALL HAVE PROVISION OF FUSES, BUSES, CONNECTORS FOR CABLE IN AND OUT. | SET | 40 | 40 | 0 | 40 | 0 | 11443.1211 |  | 457724.8447 | 82390.472 | 540115.3167 | 457724.8447 | 0 | 457724.8447 | 82390.472 | 540115.3167 | 0 |  | A
26.3 | (a) OUTDOOR KIOSK of 3 mm thick Al alloy box painted with enamel gray colour FOR STREET LIGHT HAVING 2 NOS 200 AMP SWITCH FUSE UNITS AND 10 NOS. OUT LETS OF 32 AMP MCB.(1 No.) (b) OUTDOOR KIOSK of 3 mm thick Al alloy box painted with enamel gray colour for colony power supply with 200A SFU & ten out-going feeder of 32A rating fitted with MCB. (1 No.) | NO | 2 | 2 | 0 | 2 | 0 | 6102.8664 |  | 12205.7328 | 2197.0319 | 14402.7647 | 12205.7328 | 0 | 12205.7328 | 2197.0319 | 14402.7647 | 0 |  | A
27 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR CONTROL ROOM, CARRIER ROOM & CONFERENCE ROOM.,OFFICE ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. | LOT | 1 | 1 | 0 | 1 | 0 | 180979.6839 |  | 180979.6839 | 32576.3431 | 213556.027 | 180979.6839 | 0 | 180979.6839 | 32576.3431 | 213556.027 | 0 |  | A
28 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR 400KV GIS HALL LCC ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. | LOT | 1 | 1 | 0 | 1 | 0 | 90490.3352 |  | 90490.3352 | 16288.2603 | 106778.5956 | 90490.3352 | 0 | 90490.3352 | 16288.2603 | 106778.5956 | 0 |  | A
29 | 2 TR CAPACITY SPLIT AIR CONDITIONING UNITS WITH REMOTE CONTROL FACILITY: INCLUDING SUPPLY OF 5 star rated AIR CONDITIONERS, Automatic Voltage Stabiliser,CONTROL BOXES ETC FOR COMPLETING THE A.C SCHEME.(AS PER SPECIFICATION ) FOR 220KV GIS HALL LCC ROOM etc which includes all type of cables & wires and a main control switch gear kiosk having sufficient outlet for each air conditioner unit. | LOT | 1 | 1 | 0 | 1 | 0 | 48261.5779 |  | 48261.5779 | 8687.084 | 56948.6619 | 48261.5779 | 0 | 48261.5779 | 8687.084 | 56948.6619 | 0 |  | A
30 | FIRE FIGHTING SYSTEM(PORTABLE /TROLLEY/ WHEEL MOUNTEDFIRE EXTINGUSHERS SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 15-ANNEXURE - I) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
30.1 | FOAM TYPE-9 LTRS | NOS | 4 | 4 | 0 | 4 | 0 | 771.4907 |  | 3085.9628 | 555.4733 | 3641.4361 | 3085.9628 | 0 | 3085.9628 | 555.4733 | 3641.4361 | 0 |  | A
30.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 6 | 6 | 0 | 6 | 0 | 3268.4766 |  | 19610.8597 | 3529.9547 | 23140.8144 | 19610.8597 | 0 | 19610.8597 | 3529.9547 | 23140.8144 | 0 |  | A
30.3 | DRY POWDER TYPE - 5 KGS | NOS | 6 | 6 | 0 | 6 | 0 | 1072.3918 |  | 6434.3509 | 1158.1832 | 7592.534 | 6434.3509 | 0 | 6434.3509 | 1158.1832 | 7592.534 | 0 |  | A
30.4 | CO2 - 4.5 KGS | NOS | 10 | 10 | 0 | 10 | 0 | 1188.806 |  | 11888.0601 | 2139.8508 | 14027.911 | 11888.0601 | 0 | 11888.0601 | 2139.8508 | 14027.911 | 0 |  | A
30.5 | CO2 - 9 KGS | NOS | 10 | 10 | 0 | 10 | 0 | 2504.8784 |  | 25048.784 | 4508.7811 | 29557.5651 | 25048.784 | 0 | 25048.784 | 4508.7811 | 29557.5651 | 0 |  | A
30.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 4 | 4 | 0 | 4 | 0 | 5021.5955 |  | 20086.3821 | 3615.5488 | 23701.9309 | 20086.3821 | 0 | 20086.3821 | 3615.5488 | 23701.9309 | 0 |  | A
30.7 | 9 litre water type | Nos. | 4 | 4 | 0 | 4 | 0 | 2847.2151 |  | 11388.8603 | 2049.9948 | 13438.8551 | 11388.8603 | 0 | 11388.8603 | 2049.9948 | 13438.8551 | 0 |  | A
30.8 | 4.5 kg DCP type | Nos. | 4 | 4 | 0 | 4 | 0 | 965.8432 |  | 3863.3729 | 695.4071 | 4558.78 | 3863.3729 | 0 | 3863.3729 | 695.4071 | 4558.78 | 0 |  | A
30.9 | 50 Litres Mechanical Foam type | Nos. | 2 | 2 | 0 | 2 | 0 | 7711.9474 |  | 15423.8948 | 2776.3011 | 18200.1958 | 15423.8948 | 0 | 15423.8948 | 2776.3011 | 18200.1958 | 0 |  | A
30.1 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 5 | 5 | 0 | 5 | 0 | 3390.8102 |  | 16954.0509 | 3051.7292 | 20005.7801 | 16954.0509 | 0 | 16954.0509 | 3051.7292 | 20005.7801 | 0 |  | A
31 | SUBSTATION AUTOMATION SYSTEM FOR 400/220 KV SUBSTATION ON PRP MODE: Design , engineering , drawing, supervision, installation , testing & commissioning of Substation Automation system alongwith Supply of the following 220, 132 and 33 kV level of protection panels consisting of Bay control Units & numerical protection relays and other auxiliary relays suitable for SAS as per technical specification. NOTE: All protective relays & BCU shall be numerical type. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
31.1 | Gate way panel for Sub-Station Automation (in PRP as per the specification & indicative drg ) system (for All 400 , 220 & 33 KV side bays including the future bays),other accessories (comprising servers, engg. Station, works station (Main & standby), Remote station control, Colour Laser jet Printers & dot matrix printer for local station as per requirement and also for remote station, Ethernet Switches , LIU, Red Box, Multimode glass fibre Doublle jacket armoured optical cables, special cables like F.O patch cord & armoured FO cables of adequate length etc required for the system in all respect as per latest IEC 61850 standard, Inverters of required capacity & rating (Input shall be both A.C & D.C and output shall be A.C) etc as per TS. A large vedio screen of 67 inches or more for display including all type of accessories & as per technical specification. | SET | 1 | 1 | 0 | 1 | 0 | 181463.0988 |  | 181463.0988 | 32663.3578 | 214126.4566 | 181463.0988 | 0 | 181463.0988 | 32663.3578 | 214126.4566 | 0 |  | A
31.2 | BCU for Substation Auxilliary System (Station,AC, Station DC, Lighting, Fire fighting, Diesel generator etc.) | SET | 1 | 1 | 0 | 1 | 0 | 7251.2234 |  | 7251.2234 | 1305.2202 | 8556.4436 | 7251.2234 | 0 | 7251.2234 | 1305.2202 | 8556.4436 | 0 |  | A
31.3 | 400 KV SIDE PROTECTION & OTHER PANELS as per Technical specification. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
31.3.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) for substation automation system. | NOS | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
31.3.2 | TRANSFORMER PROTECTION PANEL (DIFFERENTIAL I &II , REF I & II & BACK-UP PROTECTION for HV & IV side CONSIDERING HV ,IV & LV side for 500 MVA 400/220/33 KV ICT) with Bay control units (BCU) for substation automation system. | SET | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
31.3.3 | TIE BREAKER PROTECTION PANEL with Bay control unit (BCU) for substation automation system. | NOS | 3 | 3 | 0 | 3 | 0 | 14501.4602 |  | 43504.3807 | 7830.7885 | 51335.1692 | 43504.3807 | 0 | 43504.3807 | 7830.7885 | 51335.1692 | 0 |  | A
31.3.4 | BUS-BAR PROTECTION PANEL ( Provision of bus bar modules for the future bays and to be integrated with the Automation system) | NOS | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
31.03.5 | REACTOR PROTECTION PANEL for 125MVAR Bus Reactor with Bay Control Unit (BCU) for Substation Automation System as per Technical Specification | NOS | 1 | 2 | 1 | 1 | 1 | 14501.4602 | 14501.4602 | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 14501.4602 | 29002.9205 | 5220.5257 | 34223.4462 | 17111.7231 | Additional panel for one no. equipped GIS Bay for future Reactor added as per the approved SLD (Drg. No. TB-3-420-510-001) BoQ rate is considered as RC rate not available. | B
31.4 | 220 KV SIDE PROTECTION & OTHER PANELS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
31.4.1 | FEEDER PROTECTION PANEL (MAIN-I , MAIN-II & BACK-UP PROTECTION WITH AUTO RECLOSURE DISTANCE PROTECTION with Bay control unit (BCU) for substation automation system. | NOS | 4 | 4 | 0 | 4 | 0 | 14501.4602 |  | 58005.841 | 10441.0514 | 68446.8923 | 58005.841 | 0 | 58005.841 | 10441.0514 | 68446.8923 | 0 |  | A
31.4.2 | BUS COUPLER PROTECTION PANEL with Bay control unit (BCU) for substation automation system. | NOS | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
31.4.3 | BUS-BAR PROTECTION PANEL ( Provision of bus bar modules for the future bays and to be integrated with the Automation system) | NOS | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
31.5 | 33 KV SIDE PROTECTION PANELS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
31.5.1 | STATION TRANSFORMER PROTECTION PANEL ( BACK-UP ,PROTECTION CONSIDERING 1000 KVA 33/0.43 KV ) with Bay control units (BCU) for substation automation system. | Nos | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
32 | AC & DC SYSTEM (Suitable for Sub- station Automation System) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
32.1 | AC SYSTEM (Suitable for Sub- station Automation System) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
32.1.1 | MAIN AC DB,(HAVING A 1600 A,50KA,DRAWOUT TYPE ACB WITH 3 O/C,E/F,U/V RELAYING FACILITY and MECH& ELECT INTERLOCK FACILITY CONSIDERING Main-1,2 & DG INDOOR TYPE AS PER SPECIFICATION.(MAIN DB-1,MAIN DB-2 WITH B/C & PROVISION FOR D.G INCOMING) | SET | 1 | 1 | 0 | 1 | 0 | 29001.9339 |  | 29001.9339 | 5220.3481 | 34222.282 | 29001.9339 | 0 | 29001.9339 | 5220.3481 | 34222.282 | 0 |  | A
32.1.2 | ACDB (HAVING 800A MCCB) AS PER SPECIFICATION (AC DB-1,AC DB-2 WITH B/C) | SET | 1 | 1 | 0 | 1 | 0 | 43502.4076 |  | 43502.4076 | 7830.4334 | 51332.841 | 43502.4076 | 0 | 43502.4076 | 7830.4334 | 51332.841 | 0 |  | A
32.1.3 | MAIN LIGHTING DISTRIBUTION BOARD (HAVING 250A MCCB AS INCOMER)AS PER SPECIFICATION (WITH DB-1,DB-2 & B/C) | SET | 1 | 1 | 0 | 1 | 0 | 50752.6444 |  | 50752.6444 | 9135.476 | 59888.1204 | 50752.6444 | 0 | 50752.6444 | 9135.476 | 59888.1204 | 0 |  | A
32.1.4 | INDOOR LIGHTING DISTRIBUTION BOARD AS PER SPECIFICATION. (WITH DB-1,DB-2 & B/C) | SET | 1 | 1 | 0 | 1 | 0 | 43502.4076 |  | 43502.4076 | 7830.4334 | 51332.841 | 43502.4076 | 0 | 43502.4076 | 7830.4334 | 51332.841 | 0 |  | A
32.1.5 | EMERGENCY LIGHTING DISTRIBUTION BOARD | SET | 1 | 1 | 0 | 1 | 0 | 29001.9339 |  | 29001.9339 | 5220.3481 | 34222.282 | 29001.9339 | 0 | 29001.9339 | 5220.3481 | 34222.282 | 0 |  | A
32.1.6 | INDOOR RECEPTACLE BOARD | SET | 2 | 2 | 0 | 2 | 0 | 6102.8664 |  | 12205.7328 | 2197.0319 | 14402.7647 | 12205.7328 | 0 | 12205.7328 | 2197.0319 | 14402.7647 | 0 |  | A
32.2 | DC SYSTEM (Suitable for Sub- station Automation System) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
32.2.1 | 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). Consider separate source(DC1 & DC 2) to each panels & accordingly sufficient nos. of DC output from DB-1 & 2 to be considered. | SET | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
32.2.2 | 220 V DC EMERGENCY DISTRIBUTION BOARD | SET | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
32.2.3 | BATTERY (645 AH PLANTE TYPE) for 220 V DC | SET | 2 | 2 | 0 | 2 | 0 | 50752.6444 |  | 101505.2889 | 18270.952 | 119776.2409 | 101505.2889 | 0 | 101505.2889 | 18270.952 | 119776.2409 | 0 |  | A
32.2.4 | BATTERY CHARGER FOR 645 AH, 220 V DC (FLOAT & FLOAT CUM BOOST) (including provision of series dropper diodes with heat sinks & other protection facility at the DC Load terminal end in order to feed 220 V to the load). | SET | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
33 | DE MINERALISED PLANT of 30 L/Hr FOR MAKING DISTLED WATER FOR BATTERY BANKS | SET | 1 | 1 | 0 | 1 | 0 | 16950.1047 |  | 16950.1047 | 3051.0188 | 20001.1235 | 16950.1047 | 0 | 16950.1047 | 3051.0188 | 20001.1235 | 0 |  | A
34 | PORTABLE ALUMINIUM LADDER EXTENDABLE TYPE OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT INSIDE SWITCH YARD.(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 19) | NOS | 2 | 2 | 0 | 2 | 0 | 1130.5989 |  | 2261.1978 | 407.0156 | 2668.2134 | 2261.1978 | 0 | 2261.1978 | 407.0156 | 2668.2134 | 0 |  | A
35 | CARTWHEEL MOUNTED ALUMINIUM LADDER OF ADEQUATE HEIGHT TO BE USED FOR MAINTENANCE OF EQUIPMENT . | NOS | 1 | 1 | 0 | 1 | 0 | 1130.5989 |  | 1130.5989 | 203.5078 | 1334.1067 | 1130.5989 | 0 | 1130.5989 | 203.5078 | 1334.1067 | 0 |  | A
36 | WATER COOLER WITH WATER PURIFIER (with R.O & ultra violet purification system of ISI mark) SYSTEM | NOS | 1 | 1 | 0 | 1 | 0 | 4520.4225 |  | 4520.4225 | 813.6761 | 5334.0986 | 4520.4225 | 0 | 4520.4225 | 813.6761 | 5334.0986 | 0 |  | A
37 | MAINTENANCE & TESTING EQUIPMENT (REFER TS-VOL-IIA-16. Maintenance & Testing Equipment (ANNEXURE-II & ANNEXURE-III) INDICATED IN -SCHEDULE OF REQUIREMENTS OF MAINTENANCE EQUIPMENT). | LOT | 1 | 1 | 0 | 1 | 0 | 1129947.7835 |  | 1129947.7835 | 203390.601 | 1333338.3845 | 1129947.7835 | 0 | 1129947.7835 | 203390.601 | 1333338.3845 | 0 |  | A
38 | Essential Tools & Plants as per Technical Specification |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
38.1 | SF6 gas analyzer: Portable type instruments (A). In-built calibration facility. (B). Sensitivity of the equipment shall not be affected by any atmospheric conditions like dust, humidity, heat, wind etc. (C). Equipment shall work on zero gas loss principle i.e. gas should be pumped back to the compartment after measurement without any exposure to the atmosphere.(D). Equipment shall be supplied with suitable regulator which can be used to connect SF6 cylinder if required. (E). Following acidic/impurities products should be detected as per IEC 60480 and IEC 60376 (i) SF6 purity – Range: 0-100 % & Accuracy: +/- 0.5 %, (ii) Dew point - Range : -60 to +20 deg C & Accuracy: +/- 0.5 deg C, (iii) SO2 - Range : 0-150 ppm & Accuracy : +/- 2 %,(iv) CF4 – Range : 0-60% vol & Accuracy : +/- 1 % , (v) HF - Range : 0-200ppm & Accuracy : +/- 5 %, (F). Instrument should work on AC source as well as on rechargeable battery, (G). Input pressure: upto 10 bar h. It should be housed in a robust IP67 case with wheels. | SET | 1 | 1 | 0 | 1 | 0 | 5650.0349 |  | 5650.0349 | 1017.0063 | 6667.0412 | 5650.0349 | 0 | 5650.0349 | 1017.0063 | 6667.0412 | 0 |  | A
38.2 | SF6 gas leak detector: The detector shall be portable, battery operated with built in battery charger, hand held type and having a minimum SF6 gas leakage sensitivity of 5gm/year. The sensor shall be connected through a flexible wand for easy accessibility to joints, seals and couplings in GIS equipment and provided with a protection filter. The equipment shall have on/off switch & suitable indicating lamps/LEDs, variable pitch audible signal for leakage indication, and a head phone jack. The equipment shall have automatic zeroing of background signals suitable for detecting SF6 gas leakage in charged switchyard AIS/GIS. The test kit shall be compatible for EMI/EMC environment as per IEC 1000. | SET | 1 | 1 | 0 | 1 | 0 | 5650.0349 |  | 5650.0349 | 1017.0063 | 6667.0412 | 5650.0349 | 0 | 5650.0349 | 1017.0063 | 6667.0412 | 0 |  | A
38.3 | SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant with spares for 5 years Operation. The plant necessary for filling and evacuating the SF6 gas in the switchgear shall be supplied to enable any maintenance work to be carried out. This shall include all the necessary gas cylinders for temporarily storing the evacuated SF6 gas. The capacity of the temporary storage facilities shall at least be sufficient for storing the maximum quantity of gas that could be removed from at least one phase of one complete bay. The minimum capacity of evacuation plant shall be: Vacuum Pump: 60 M3/Hour (Nominal suction pressure) Compressor : 15 M3/Hour(Delivery). The evacuation equipment shall be provided with all the necessary pipes, couplings, flexible tubes and valves for coupling up to the switchgear for filling or evacuating all the gases. The gases compartments shall be fitted with permanent non-return valves through which the gas is pumped into or evacuated form the compartments. | SET | 1 | 1 | 0 | 1 | 0 | 227297.7366 |  | 227297.7366 | 40913.5926 | 268211.3292 | 227297.7366 | 0 | 227297.7366 | 40913.5926 | 268211.3292 | 0 |  | A
39 | OFFICE FURNITURE (REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 18 ANNEXURE - IV ,INDICATED IN SCHEDULE OF REQUIREMENTS OFFICE FURNITURE) & PLACING IN CONTROL ROOM,CONFERENCE ROOM,OFFICE ROOMS,LIBRARY,TESTING LAB, SAS Room etc. | LOT | 1 | 1 | 0 | 1 | 0 | 56497.3892 |  | 56497.3892 | 10169.5301 | 66666.9192 | 56497.3892 | 0 | 56497.3892 | 10169.5301 | 66666.9192 | 0 |  | A
40 | EOT Crane for GIS building for 400 kV GIS station (7T Capacity safe working load & minimum height of crane have shall be 9.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. | SET | 1 | 1 | 0 | 1 | 0 | 338984.335 |  | 338984.335 | 61017.1803 | 400001.5153 | 386442.1419 | 0 | 386442.1419 | 69559.5855 | 456001.7275 | 56000.2121 | As per the revised size of GIS Hall, due to extra DSL and cables, Unit Rate to be increased by 14%. | B
41 | EOT Crane for GIS building for 220 kV GIS station (5T Capacity safe working load & minimum height of crane have shall be 8.0 meters or as per actual requirement whichever is higher. The crane shall have minimum speeds under full load of: Speed (a) Hoisting 2 meters/minute (b) Cross Travel 10 meters/minute (c) Long Travel 20 meters/minute (d) Creep speed shall be of 25% of operating speed.The crane shall be possible to be operated through the cable, through the pendant control and which shall be easily accessible from the floor of GIS building and through remote control device. ) including all accessories with control panel. | SET | 1 | 1 | 0 | 1 | 0 | 248588.7097 |  | 248588.7097 | 44745.9677 | 293334.6774 | 278419.3548 | 0 | 278419.3548 | 50115.4839 | 328534.8387 | 35200.1613 | As per the revised size of GIS Hall, due to extra DSL and cables, Unit Rate to be increased by 12%. | B
42 | FIRE FIGHTING EQIPMENT: (Main Pump, Jockey Pump, DG Set cum Pump, Control Panel for Fire Fighting System (HIGH PRESSURE : Hydrant and Mulsifire system) to take care of 2 Nos 500 MVA ICT,125 MVAr Reactor, switcyard equipment and buildings. HVW system & hydrant sytsem, complete with all overhead piping, valves, fittings etc inside pump house for Fire protection sytem of substation) as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 932256.7427 |  | 932256.7427 | 167806.2137 | 1100062.9564 | 932256.7427 | 0 | 932256.7427 | 167806.2137 | 1100062.9564 | 0 |  | A
43 | Hydrant sytsem, complete overhead piping of different sizes,vaves and accessories etc outside the Pump House for Fire protection sytem of of 2 Nos 500 MVA ICT,125 MVAr Reactor, switcyard equipment and buildings as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 645091.5245 |  | 645091.5245 | 116116.4744 | 761207.9989 | 645091.5245 | 0 | 645091.5245 | 116116.4744 | 761207.9989 | 0 |  | A
44 | HVW Spray sytsem, Hydrant System and complete overhead piping,different type of valves,Fire sensor etc and accessories etc near the Transformer for Fire protection of 500 MVA, 400/220/33 KV ICT,125 MVAr Reactor, as per the technical spec. | LOT | 1 | 1 | 0 | 1 | 0 | 429090.898 |  | 429090.898 | 77236.3616 | 506327.2597 | 429090.898 | 0 | 429090.898 | 77236.3616 | 506327.2597 | 0 |  | A
45 | BEST QUALITY &APPROVED MAKE INSULATING MAT (Confirming to IS:15652:2006) TO BE KEPT INFRONT OF ALL PANELS,BOARDS ETC.(2000X1000X3)mm Size | Nos | 45 | 45 | 0 | 45 | 0 | 565.2995 |  | 25438.4756 | 4578.9256 | 30017.4012 | 25438.4756 | 0 | 25438.4756 | 4578.9256 | 30017.4012 | 0 |  | A
46 | 250 KVA outdoor type silent Generator with contro panel having adequate mechanical & electrical protection as per latest IS with Automatic Mains Failure feature as per Technical spec. The DG should be covered with canopy and suitable barricade. | NOS | 1 | 1 | 0 | 1 | 0 | 252843.7473 |  | 252843.7473 | 45511.8745 | 298355.6218 | 252843.7473 | 0 | 252843.7473 | 45511.8745 | 298355.6218 | 0 |  | A
47 | RECEIVING & DRAGGING AND INSTALLING ON THE PLINTH AND PLACING IN POSITION, ERECTION OF ACCESSORIES & OTHERE QUIPMENT OF THE TRANSFORMERS, EART-HING AS PER STANDARD(INCLUDING SUPPLY OF MATERIALS),VACUUM TREATMENT OF THE TANK AND WINDING,OIL FILTRATION(INCLUDING SUPPLY OF VACUUM CUM OIL FILTER MACHINE),SUPPLY & LAYING OF ALL TYPES OF CONTROL & POWER CABLES PERTAINING TO TRANSFORMERS ,TESTING AND COMMISSIONING INCLUDING ALL TESTS OF THE OILS AS PER STIPULATION IN THE STANDARD APPROVED TESTING LABORATORY AND AS PER THE INSTRUCTION OF THE ENGINEER IN CHARGE.THIS INCLUDE ALL RELATED WORKS FOR ERECTION,TESTING AND COMMISSIONING OF THE POWER TRANSFORMERS.(CONTRACTOR TO ARRANGE POWER SUPPLY FOR FILTRATION AND VACUUM TREATMENT WORKS).IT ALSO INCLUDES SUPPLY OF ALL MATERIALS FOR ERECTION INCLUDING T&P's. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
47.1 | 400/220KV,500 MVA ICT in complete shape as per Technical spec | Nos | 2 | 2 | 0 | 2 | 0 | 2883268.9374 |  | 5766537.8749 | 1037976.8175 | 6804514.6923 | 5766537.8749 | 0 | 5766537.8749 | 1037976.8175 | 6804514.6923 | 0 |  | A
48 | RECEIVING & DRAGGING AND INSTALLING ON THE PLINTH AND PLACING IN POSITION, ERECTION OF ACCESSORIES & OTHERE QUIPMENT OF THE REACTOR, EART-HING AS PER STANDARD(INCLUDING SUPPLY OF MATERIALS),VACUUM TREATMENT OF THE TANK AND WINDING,OIL FILTRATION(INCLUDING SUPPLY OF VACUUM CUM OIL FILTER MACHINE),SUPPLY & LAYING OF ALL TYPES OF CONTROL & POWER CABLES PERTAINING TO REACTOR ,TESTING AND COMMISSIONING INCLUDING ALL TESTS OF THE OILS AS PER STIPULATION IN THE STANDARD APPROVED TESTING LABORATORY AND AS PER THE INSTRUCTION OF THE ENGINEER IN CHARGE.THIS INCLUDE ALL RELATED WORKS FOR ERECTION(Transformer and its accessories,RTCC Panel etc),TESTING AND COMMISSIONING OF THE REACTORS.(CONTRACTOR TO ARRANGE POWER SUPPLY FOR FILTRATION AND VACUUM TREATMENT WORKS).IT ALSO INCLUDES SUPPLY OF ALL MATERIALS FOR ERECTTION INCLUDING T&P's. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
48.1 | 400 KV, 125 MVAR REACTOR in complete shape as per Technical spec: | Nos | 1 | 1 | 0 | 1 | 0 | 1638738.0124 |  | 1638738.0124 | 294972.8422 | 1933710.8546 | 1638738.0124 | 0 | 1638738.0124 | 294972.8422 | 1933710.8546 | 0 |  | A
49 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
49.1 | Erection of 24 fibre(DWSM) optic approach cable along with hardware | KM | 1 | 1 | 0 | 1 | 0 | 19389.87 |  | 19389.87 | 3490.1766 | 22880.0466 | 19389.87 | 0 | 19389.87 | 3490.1766 | 22880.0466 | 0 |  | A
49.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 6 | 6 | 0 | 6 | 0 | 8303.884 |  | 49823.304 | 8968.1947 | 58791.4987 | 49823.304 | 0 | 49823.304 | 8968.1947 | 58791.4987 | 0 |  | A
49.3 | 48V , 800AH, maintenance free VRLA battery set | NO | 1 | 2 | 1 | 1 | 1 | 36252.1708 | 4582.81 | 36252.1708 | 6525.3907 | 42777.5615 | 36252.1708 | 4582.81 | 40834.9808 | 7350.2965 | 48185.2773 | 5407.7158 | Quantity revised as per OPTCL comment on Single Line Diagram for Auxiliary Power System for 400/220kV GIS Sub Station at Ersama (Drg. No. TB-0-420-510-003). RC 2023 rate sl no. 20 (ii) is considered as it is lower than the BoQ rate. | B
49.4 | SMPS based battery charger of 125A suitable for 48V VRLA battery | NO | 1 | 2 | 1 | 1 | 1 | 14501.4602 | 4582.81 | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 4582.81 | 19084.2702 | 3435.1686 | 22519.4389 | 5407.7158 | Quantity revised as per OPTCL comment on Single Line Diagram for Auxiliary Power System for 400/220kV GIS Sub Station at Ersama (Drg. No. TB-0-420-510-003). RC rate sl no. 20(ii) is considered as it is lower than the BoQ rate. | B
49.5 | 48 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C). | SET | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
49.6 | Installation & commissioning of Optical Line Terminal Equipent(OLTE), STM4 type SDH equipment with integrated MUX and tributary cards for speech and data ports, SFP module L 4.2(2 nos) for interfacing of speech and data which should be compatible with existing OPTCL system. | NO | 1 | 1 | 0 | 1 | 0 | 8589.9867 |  | 8589.9867 | 1546.1976 | 10136.1843 | 8589.9867 | 0 | 8589.9867 | 1546.1976 | 10136.1843 | 0 |  | A
49.7 | Installation & commissioning of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 2 | 2 | 0 | 2 | 0 | 4755.2241 |  | 9510.4481 | 1711.8807 | 11222.3288 | 9510.4481 | 0 | 9510.4481 | 1711.8807 | 11222.3288 | 0 |  | A
50 | CCTV Surveilance system with Latest Version PC Monitor, DBR with 1TB Hard Disk, (Night Hawk) cameras including all materials for areas in Control room building & Entire Switchyard areas,GIS Buildings, Other areas etc suitable for 180 & 360 deg movement with all necessary hardware fittings for monitoring with SCADA compatibility. No. of such cameras (different type) are to be calculated as per standard practice & its installations at the strategic locations. Additional Information: 1. Fixed type cameras for monitoring of main gate , Main Entrance door of Control Room Building, Main Entrance door of Fire-fighting Pump House,Main Entrance door of GIS Hall, Main Entrance door of store shed and indoor areas. 2. The areas (Staretgic Location) to be monitored through CCTV system are : a) 220 and 400 kV GIS hall indoor area b) All the Transformer and Reactors under present scope c) Main Entrance door of Control Room Building, Fire-fighting Pump House, GIS Hall, store shed. d) Main entrance gate of switchyard and all gates of switchyard. e) 400 and 220 kV bays Line side equipment (Surge Arrester) of present scope Note: Any other requirement besides above to be explored & can be finalised during detail Engg. | Lot | 1 | 1 | 0 | 1 | 0 | 191654.274 |  | 191654.274 | 34497.7693 | 226152.0433 | 191654.274 | 0 | 191654.274 | 34497.7693 | 226152.0433 | 0 |  | A
A1 | ADDITIONAL ELECTRICAL WORKS FOR SUBSTATION |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
51 | 420 KV, 3150 A, 63 KA, ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
51.1 | WITH ONE EARTH SWITCH | Nos | 0 | 2 | 2 | 0 | 2 |  | 39313.4696 | 0 | 0 | 0 | 0 | 78626.9391 | 78626.9391 | 14152.849 | 92779.7882 | 92779.7882 | Additional line side Isolators qty as per as per approved SLD (Drg. No. TB-3-420-510-001) Rate Considered from New Duburi portion Sl. No. B.2.1. | B
52 | 245 KV, 2000 A, 50 KA, ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
52.1 | WITH ONE EARTH SWITCH | Nos | 0 | 4 | 4 | 0 | 4 |  | 25786.48 | 0 | 0 | 0 | 0 | 103145.92 | 103145.92 | 18566.2656 | 121712.1856 | 121712.1856 | Additional line side Isolators qty as per as per approved SLD (Drg. No. TB-3-420-510-001) RC rate sl no. 10.1 (d) (i) is considered as it is lower than the BoQ rate. | B
53 | 38/66kV XLPE CABLE & ACCESSORIES |  |  |  |  | 0 |  |  |  | 0 |  |  | 0 | 0 | [5 empty] | A
53.1 | 38/66kV, 1C x 240 sq. mm XLPE CABLE | Mtrs | 0 | 1500 | 1500 | 0 | 1500 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | rate from BHEL | A
53.2 | 66kV XLPE CABLE Termination Kit suitable for ICT tertiary | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
53.3 | 66kV XLPE CABLE Termination Kit suitable for ST | Nos | 0 | 6 | 6 | 0 | 6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
53.4 | 66kV CABLE Link Box (with SVL) with bonding cable | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
53.5 | 66kV CABLE Link Box (without SVL) with bonding cable | Nos | 0 | 2 | 2 | 0 | 2 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
54 | 36 kV, 31.5 kA for 1 sec Voltage Tranformer (with higher BIL) | Nos | 0 | 6 | 6 | 0 | 6 |  | 1827.9 | 0 | 0 | 0 | 0 | 10967.4 | 10967.4 | 1974.132 | 12941.532 | 12941.532 | 33kV PT with higher BIL (52.5kV) as per approved SLD (Drg. No. TB-3-420-510-001) RC rate sl no. 10.4 (h) (i) is considered as it is lower than the BoQ rate. | B
55 | Controlled Switching Device (CSD) for 400kV Line Bays in GIS | Nos. | 0 | 2 | 2 | 0 | 2 |  | 6250 | 0 | 0 | 0 | 0 | 12500 | 12500 | 2250 | 14750 | 14750 | Additional qty as per approved SLD (Drg. No. TB-3-420-510-001) Rate from BHEL | B
[6 empty] | 0 | [7 empty] | 0 | [5 empty] | A
B | ELECTRICAL WORKS - New Duburi SS Extn. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
1 | 420 KV,2000-1000-500A,63 KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 12 | 12 | 0 | 12 | 0 | 12936.7745 |  | 155241.2938 | 27943.4329 | 183184.7267 | 155241.2938 | 0 | 155241.2938 | 27943.4329 | 183184.7267 | 0 |  | A
2 | 420 KV,3150A,63 KA,ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
2.1 | WITH ONE EARTH SWITCH | NOS | 8 | 8 | 0 | 8 | 0 | 39313.4696 |  | 314507.7565 | 56611.3962 | 371119.1526 | 314507.7565 | 0 | 314507.7565 | 56611.3962 | 371119.1526 | 0 |  | A
2.2 | WITH TWO EARTH SWITCH | NOS | 2 | 2 | 0 | 2 | 0 | 47136.8983 |  | 94273.7967 | 16969.2834 | 111243.0801 | 94273.7967 | 0 | 94273.7967 | 16969.2834 | 111243.0801 | 0 |  | A
3 | 420 KV,4400pF,63 KA,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
3.1 | SINGLE PHASE LINE CAPACITOR VOLTAGE TRANSFORMER | NOS | 6 | 6 | 0 | 6 | 0 | 12936.7745 |  | 77620.6469 | 13971.7164 | 91592.3633 | 77620.6469 | 0 | 77620.6469 | 13971.7164 | 91592.3633 | 0 |  | A
4 | 420KV,3150A,63KA,SF6,CIRCUIT BREAKER WITH Terminal Connector, SUPPORT STRUCTURE etc. WITH CSD (For Tie & reactor switching) | NOS | 3 | 3 | 0 | 3 | 0 | 82050.3058 |  | 246150.9174 | 44307.1651 | 290458.0826 | 246150.9174 | 0 | 246150.9174 | 44307.1651 | 290458.0826 | 0 |  | A
5 | 420KV,3150A,63KA,SF6,CIRCUIT BREAKER WITH Terminal Connector SUPPORT STRUCTURE etc WITH OUT CSD | NOS | 2 | 2 | 0 | 2 | 0 | 64577.3238 |  | 129154.6476 | 23247.8366 | 152402.4842 | 129154.6476 | 0 | 129154.6476 | 23247.8366 | 152402.4842 | 0 |  | A
6 | 390KV metal oxide polymer housed surge arrrestor, 20 KA , Long duration discharge class IV ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 12 | 12 | 0 | 12 | 0 | 3836.7358 |  | 46040.8291 | 8287.3492 | 54328.1783 | 46040.8291 | 0 | 46040.8291 | 8287.3492 | 54328.1783 | 0 |  | A
7 | 120KV metal oxide polymer housed surge arrrestor, 10 KA , Long duration discharge class III ,pressure relief Design A, thermal energy (Wth) & Repetitive charge transfer(Qrs) as per latest IEC, as per technical specification COMPLETE WITH INSULATING BASE & SURGE MONITOR | NOS | 2 | 2 | 0 | 2 | 0 | 2900.4894 |  | 5800.9787 | 1044.1762 | 6845.1549 | 5800.9787 | 0 | 5800.9787 | 1044.1762 | 6845.1549 | 0 |  | A
8 | 400 KV Bus Post Insulators | NOS | 48 | 59 | 11 | 59 | 0 | 1972.1355 |  | 94662.5017 | 17039.2503 | 111701.752 | 116355.9917 | 0 | 116355.9917 | 20944.0785 | 137300.0702 | 25598.3182 | As per approved EKD TB-2-420-316-007-D Rev 00 | B
9 | 145 KV ISOLATORS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
9.1 | 132kV, 2000A, 40kA,ISOLATORS WITHOUT EARTH SWITCH (1-Pole) | NOS | 2 | 2 | 0 | 2 | 0 | 12080.4395 |  | 24160.8791 | 4348.9582 | 28509.8373 | 24160.8791 | 0 | 24160.8791 | 4348.9582 | 28509.8373 | 0 |  | A
10 | 145 KV CT (800-400-200/1-1-1) FOR NGR | NOS | 2 | 2 | 0 | 2 | 0 | 4821.3236 |  | 9642.6473 | 1735.6765 | 11378.3238 | 9642.6473 | 0 | 9642.6473 | 1735.6765 | 11378.3238 | 0 |  | A
11 | BUS BAR & CIRCUIT MATERIALS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
11.1 | 160 kN INSULATOR(AANTI FOG) Porcelain LRI for twin Moose cond (Double TENSION)-400 KV | SET | 72 | 54 | -18 | 54 | 0 | 2610.4404 |  | 187951.7105 | 33831.3079 | 221783.0184 | 140963.7829 | 0 | 140963.7829 | 25373.4809 | 166337.2638 | -55445.7546 | As per approved EKD TB-2-420-316-007-D Rev 00 | B
11.2 | 120 kN INSULATOR(ANTI FOG) Porcelain LRI for Twin Moose cond (SUSPENSION)-400 KV | SET | 30 | 24 | -6 | 24 | 0 | 2610.4404 |  | 78313.2127 | 14096.3783 | 92409.591 | 62650.5702 | 0 | 62650.5702 | 11277.1026 | 73927.6728 | -18481.9182 | As per approved EKD TB-2-420-316-007-D Rev 00 | B
12 | ACSR MOOSE CONDUCTOR | MTR | 3300 | 4200 | 900 | 4125 | 75 | 430.1406 | 430.1406 | 1419463.9765 | 255503.5158 | 1674967.4923 | 1774329.9706 | 32260.5449 | 1806590.5155 | 325186.2928 | 2131776.8083 | 456809.3161 | As per approved EKD TB-2-420-316-007-D Rev 00. RC rate not available, BoQ rate considered. | B
13 | IPS 4.5” Aluminium Tube (OD: 120 mm,Thickness: 12 mm)(for 400 KV Bus and connection from equipment to equipment in 400 KV side) including welding sleeves,corona bell etc. | MTR | 450 | 750 | 300 | 562 | 188 | 430.1406 | 430.1406 | 193563.2695 | 34841.3885 | 228404.658 | 241739.0166 | 80866.4326 | 322605.4492 | 58068.9809 | 380674.4301 | 152269.772 | As per approved EKD TB-2-420-316-007-D Rev 00 RC 2023 rate not avialable, BoQ rate considered. | B
14 | SUBSTATION EARTHING SYSTEMS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
14.1 | EARTHING CONDUCTOR FOR BURRIAL & RAISER FROM THE MAT BELOW GROUND :40 mm for laying as main eartth mat (spacing maximum 5m both way ) | MTR | 3960 | 14500 | 10540 | 4950 | 9550 | 146.9976 | 146.9976 | 582110.4564 | 104779.8822 | 686890.3386 | 727638.0705 | 1403826.9845 | 2131465.0551 | 383663.7099 | 2515128.765 | 1828238.4264 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 RC 2023 rate not avialable, BoQ rate considered. | B
14.2 | EARTHING CONDUCTOR: 75X10 mm GI Flat for Raiser from the burial earth mat to equipment,structure etc) | MTR | 2377 | 2850 | 473 | 2850 | 0 | 72.019 |  | 171189.0525 | 30814.0294 | 202003.0819 | 205254.0175 | 0 | 205254.0175 | 36945.7231 | 242199.7406 | 40196.6587 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 | B
14.3 | EARTHING CONDUCTOR: 50X6 mm GI Flat for fencing,cable tray and auxiliary Boards earthing. | MTR | 847 | 2850 | 2003 | 1058 | 1792 | 67.0861 | 67.0861 | 56821.9677 | 10227.9542 | 67049.9219 | 70977.1451 | 120218.378 | 191195.5231 | 34415.1942 | 225610.7173 | 158560.7953 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 RC 2023 rate higher than BoQ, BoQ rate considered. | B
14.4 | EARTHING DEVICE & ASSOCIATED ACCESSORIES (50 mm heavy duty GI PERFORATED PIPE 3 mtrs long for treated earth pit) (Provision to be made for water taps for all treated earth pit individually) | NOS | 60 | 180 | 120 | 75 | 105 | 8889.9012 | 8889.9012 | 533394.0739 | 96010.9333 | 629405.0072 | 666742.5924 | 933439.6293 | 1600182.2217 | 288032.7999 | 1888215.0216 | 1258810.0144 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 BoQ rate considered for additional requirement of water tap arrangement. | B
14.5 | EARTHING DEVICE & ASSOCIATED ACCESSORIES 40mm MS rod 3 mtrs long for non treated earth pit) | NOS | 50 | 0 | -50 | 0 | 0 | 638.305 |  | 31915.2486 | 5744.7447 | 37659.9933 | 0 | 0 | 0 | 0 | 0 | -37659.9933 | As per submitted earthmat layout TB-1-420-316-008-D Rev 00 | B
14.6 | G.I Cable Trays including support GI angle suitable for different sections i.e. Section:1-1,2-2,3-3 & 4-4 along with its accessories as per TS. Sizes of Cable Tray: Section:1-1:G.I Cable Trays(size: 450x75x2500mm) Section:2-2:G.I Cable Trays(size: 300x75x2500mm) Section:3-3 & 4-4:G.I Cable Trays(size: 150x75x2500mm) GI Support Angle:50X50X6 mm | LOT | 1 | 1 | 0 | 1 | 0 | 1454478.9997 |  | 1454478.9997 | 261806.22 | 1716285.2197 | 1454478.9997 | 0 | 1454478.9997 | 261806.22 | 1716285.2197 | 0 |  | A
15 | BAY MARSHALLING KIOSK | NOS | 2 | 2 | 0 | 2 | 0 | 5199.1765 |  | 10398.353 | 1871.7035 | 12270.0566 | 10398.353 | 0 | 10398.353 | 1871.7035 | 12270.0566 | 0 |  | A
16 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 1 | 1 | 0 | 1 | 0 | 5199.1765 |  | 5199.1765 | 935.8518 | 6135.0283 | 5199.1765 | 0 | 5199.1765 | 935.8518 | 6135.0283 | 0 |  | A
17 | SWITCH YARD RECEPTACLE BOARD FOR Reactor OIL FILTERATION | NOS | 1 | 1 | 0 | 1 | 0 | 8398.5939 |  | 8398.5939 | 1511.7469 | 9910.3407 | 8398.5939 | 0 | 8398.5939 | 1511.7469 | 9910.3407 | 0 |  | A
18 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY | NOS | 1 | 1 | 0 | 1 | 0 | 5199.1765 |  | 5199.1765 | 935.8518 | 6135.0283 | 5199.1765 | 0 | 5199.1765 | 935.8518 | 6135.0283 | 0 |  | A
19 | SWITCH YARD STRUCTURES( including Foundation Bolts and Nuts) GALVANISED (LATTICE) FOR ALL 400 KV |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
19.1 | DIFFERENT TYPES OF COLUMNS (LATTICE TYPE) WITH DETAILS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
19.1.1 | 400 KV COLUMN with peak (4TP) | NOS | 9 | 20 | 11 | 11 | 9 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | A
19.1.2 | 400 KV COLUMN without peak (4T) | NOS | 5 | 0 | -5 | 0 | 0 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | A
19.2 | DIFFERENT TYPE OF BEAMS (LATTICE TYPE) WITH DETAILS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
19.2.1 | 400 KV BEAM( Nominal Weight 3.5 MT appox) | NOS | 9 | 12 | 3 | 11 | 1 | [6 empty] | 0 |  |  |  |  | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 | A
19.3 | TOTAL WEIGHT OF COLUMN & BEAM | MT | 146 | 205 | 59 | 182.5 | 22.5 | 5441.8705 | 4533.3 | 794513.0949 | 143012.3571 | 937525.452 | 993141.3687 | 101999.25 | 1095140.6187 | 197125.3114 | 1292265.93 | 354740.478 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
19.4 | Total weight of different size of GI Nuts and bolts for structures. | MT | 13 | 18.5 | 5.5 | 16.25 | 2.25 | 5650.0349 | 4533.3 | 73450.4535 | 13221.0816 | 86671.5351 | 91813.0669 | 10199.925 | 102012.9919 | 18362.3385 | 120375.3304 | 33703.7953 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
19.5 | SUPPORT STRUCTURES (Including foundation Bolts and Nuts) GALVANISED (PIPE TYPE) FOR ALL 400 KV & 220 kV EQUIPMENTS |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
19.5.1 | ISOLATORS-400KV | SET | 10 | 10 | 0 | 10 | 0 | [6 empty] | 0 | [5 empty] | A
19.5.2 | CTS-400 KV | SET | 12 | 12 | 0 | 12 | 0 | [6 empty] | 0 | [5 empty] | A
19.5.3 | CVTS-400 KV | SET | 6 | 6 | 0 | 6 | 0 | [6 empty] | 0 | [5 empty] | A
19.5.4 | Surge Arrester-400 Kv | SET | 12 | 12 | 0 | 12 | 0 | [6 empty] | 0 | [5 empty] | A
19.5.5 | BPI-400 KV | SET | 48 | 59 | 11 | 59 | 0 | [6 empty] | 0 |  |  |  |  | As per approved EKD TB-2-420-316-007-D Rev 00 | A
19.5.6 | ISOLATOR-132 KV | SET | 2 | 2 | 0 | 2 | 0 | [6 empty] | 0 | [5 empty] | A
19.5.7 | CTS-132 KV | SET | 2 | 2 | 0 | 2 | 0 | [6 empty] | 0 | [5 empty] | A
19.6 | TOTAL WEIGHT OF SUPPORT STRUCTURE FOR ABOVE EQUIPMENT | MT | 55 | 75 | 20 | 68.75 | 6.25 | 4595.4012 | 4533.3 | 252747.0643 | 45494.4716 | 298241.5359 | 315933.8304 | 28333.125 | 344266.9554 | 61968.052 | 406235.0074 | 107993.4715 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
19.7 | Total weight of different size of GI Nuts and bolts for structures. | MT | 1.5 | 2 | 0.5 | 1.875 | 0.125 | 5650.0349 | 4533.3 | 8475.0523 | 1525.5094 | 10000.5617 | 10593.8154 | 566.6625 | 11160.4779 | 2008.886 | 13169.3639 | 3168.8022 | Quantity of Towers and Equipment As Per: Approved structure loading diagram TB-2-316-006-D Rev 00 & Land Usage Plan TB-2-420-316-000-D Rev 00 RC rate sl no. 16.1 considerd, as it is lower than the BoQ rate. | B
20 | GENERAL EQUIPMENT & SUBSTATION ACCESSORIES |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.1 | POWER CABLES,1.1KV,XLPE & PVC,ARMOURED, ALUMINIUM CONDUCTOR (As per Specification) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.1.1 | PVC 3.5 CX70 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 41.4356 |  | 41435.5623 | 7458.4012 | 48893.9635 | 41435.5623 | 0 | 41435.5623 | 7458.4012 | 48893.9635 | 0 |  | A
20.1.2 | PVC 3.5 CX35 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 30.5834 |  | 30583.3912 | 5505.0104 | 36088.4016 | 30583.3912 | 0 | 30583.3912 | 5505.0104 | 36088.4016 | 0 |  | A
20.1.3 | PVC 4 CX 16 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 25.6506 |  | 25650.5862 | 4617.1055 | 30267.6917 | 25650.5862 | 0 | 25650.5862 | 4617.1055 | 30267.6917 | 0 |  | A
20.1.4 | PVC 4 CX 6 mm2 | MTRS | 1000 | 1000 | 0 | 1000 | 0 | 25.6506 |  | 25650.5862 | 4617.1055 | 30267.6917 | 25650.5862 | 0 | 25650.5862 | 4617.1055 | 30267.6917 | 0 |  | A
20.1.5 | PVC 2CX 6 mm2 | MTRS | 3000 | 3000 | 0 | 3000 | 0 | 25.6506 |  | 76951.7585 | 13851.3165 | 90803.0751 | 76951.7585 | 0 | 76951.7585 | 13851.3165 | 90803.0751 | 0 |  | A
20.2 | COPPER FLEXIBLE CONTROL CABLES,1.1 KV, PVC,FRLS, ARMOURED STRANDED (As per specification) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
20.2.1 | 5 CX 2.5 mm2 | MTRS | 7000 | 7000 | 0 | 7000 | 0 | 25.6506 |  | 179554.1032 | 32319.7386 | 211873.8418 | 179554.1032 | 0 | 179554.1032 | 32319.7386 | 211873.8418 | 0 |  | A
20.2.2 | 10 CX 2.5 mm2 | MTRS | 5000 | 5000 | 0 | 5000 | 0 | 25.6506 |  | 128252.9309 | 23085.5276 | 151338.4584 | 128252.9309 | 0 | 128252.9309 | 23085.5276 | 151338.4584 | 0 |  | A
20.2.3 | 16 CX 2.5 mm2 | MTRS | 3500 | 3500 | 0 | 3500 | 0 | 30.5834 |  | 107041.8692 | 19267.5365 | 126309.4057 | 107041.8692 | 0 | 107041.8692 | 19267.5365 | 126309.4057 | 0 |  | A
20.2.4 | 19 CX 2.5 mm2 | MTRS | 3500 | 3500 | 0 | 3500 | 0 | 35.5162 |  | 124306.6868 | 22375.2036 | 146681.8905 | 124306.6868 | 0 | 124306.6868 | 22375.2036 | 146681.8905 | 0 |  | A
20.2.5 | 4 CX 4 mm2 | MTRS | 6500 | 6500 | 0 | 6500 | 0 | 23.6775 |  | 153903.5171 | 27702.6331 | 181606.1501 | 153903.5171 | 0 | 153903.5171 | 27702.6331 | 181606.1501 | 0 |  | A
21 | ACCESSORIES FOR OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
21.1 | Erection of 24 fibre(DWSM) optic approach cable along with hardware | KM | 1 | 1 | 0 | 1 | 0 | 19389.87 |  | 19389.87 | 3490.1766 | 22880.0466 | 19389.87 | 0 | 19389.87 | 3490.1766 | 22880.0466 | 0 |  | A
21.2 | Digital tele-protection coupler compatible for interfacing with SDHMUX installed at 400KV Easama grid S/S and Duburi New grid S/s | NO | 2 | 2 | 0 | 2 | 0 | 8303.884 |  | 16607.768 | 2989.3982 | 19597.1662 | 16607.768 | 0 | 16607.768 | 2989.3982 | 19597.1662 | 0 |  | A
21.3 | Installation & commissioning of FODP(Fibre Optic Distribution panel) 48F: Indoor type, rack mounted with FCPC coupling and pig tails(DWSM Fibre) | NO | 1 | 1 | 0 | 1 | 0 | 4755.2241 |  | 4755.2241 | 855.9403 | 5611.1644 | 4755.2241 | 0 | 4755.2241 | 855.9403 | 5611.1644 | 0 |  | A
22 | SUB STATION LIGHTING (AS PER SPECIFICATION AND APPROVED DRAWINGS )(Switch yard and other street area) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
22.1 | SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES ERECTION OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | Nos | 50 | 50 | 0 | 50 | 0 | 1577.511 |  | 78875.5525 | 14197.5994 | 93073.1519 | 78875.5525 | 0 | 78875.5525 | 14197.5994 | 93073.1519 | 0 |  | A
22.2 | STREET LIGHTING, IT INCLUDES ERECTION OF GI TUBULAR POLE, WITH LED LIGHTING FIXTURES WITH LAMPS of reputed make (Philips/CGL/Bajaj)(TO BE PROVIDED IN THE SWITCH YARD, ALONG THE ROADS (APPROACH INSIDE YARD AND OTHER ROADS). | Nos | 5 | 5 | 0 | 5 | 0 | 11443.1211 |  | 57215.6056 | 10298.809 | 67514.4146 | 57215.6056 | 0 | 57215.6056 | 10298.809 | 67514.4146 | 0 |  | A
23 | 2 TR (Two Ton) CAPACITY SPLIT AIR CONDITIONING(5 star Inverter) UNITS WITH REMOTE CONTROL FACILITY AND INCLUDING RELATED MATERIALS LIKE VOLTAGE STABILISER,CONTROL BOXES ETC FOR AIR CONDITIONING SYSTEM (AS PER SPECIFICATION ): FOR SWITCHYARD CONTROL ROOM. | NOS | 5 | 5 | 0 | 5 | 0 | 6032.8206 |  | 30164.1028 | 5429.5385 | 35593.6413 | 30164.1028 | 0 | 30164.1028 | 5429.5385 | 35593.6413 | 0 |  | A
24 | FIRE FIGHTING SYSTEM(PORTABLE AND WHEEL MOUNTED SETS FOR CONTROL ROOM,EQUIPMENT LIKE TRANSFORMER AND OTHER AREAS AS PER TECH SPEC(REFER TS-VOL-IIA-SCOPE OF WORKAT SL NO. 16-ANNEXURE - I) |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
24.1 | FOAM TYPE-9 LTRS | NOS | 1 | 1 | 0 | 1 | 0 | 771.4907 |  | 771.4907 | 138.8683 | 910.359 | 771.4907 | 0 | 771.4907 | 138.8683 | 910.359 | 0 |  | A
24.2 | DRY CHEMICAL POWDER(TROLLEY MOUNTED)- 22.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 3268.4766 |  | 3268.4766 | 588.3258 | 3856.8024 | 3268.4766 | 0 | 3268.4766 | 588.3258 | 3856.8024 | 0 |  | A
24.3 | DRY POWDER TYPE - 5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 1072.3918 |  | 1072.3918 | 193.0305 | 1265.4223 | 1072.3918 | 0 | 1072.3918 | 193.0305 | 1265.4223 | 0 |  | A
24.4 | CO2 - 4.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 1188.806 |  | 1188.806 | 213.9851 | 1402.7911 | 1188.806 | 0 | 1188.806 | 213.9851 | 1402.7911 | 0 |  | A
24.5 | CO2 - 9 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 2504.8784 |  | 2504.8784 | 450.8781 | 2955.7565 | 2504.8784 | 0 | 2504.8784 | 450.8781 | 2955.7565 | 0 |  | A
24.6 | CO2 (TROLLY MOUNTED)- 22.5 KGS | NOS | 1 | 1 | 0 | 1 | 0 | 5021.5955 |  | 5021.5955 | 903.8872 | 5925.4827 | 5021.5955 | 0 | 5021.5955 | 903.8872 | 5925.4827 | 0 |  | A
24.7 | FIRE BUCKET (6 NOS IN EACH STAND) WITH STAND AND CANOPY | SET | 1 | 1 | 0 | 1 | 0 | 3390.8102 |  | 3390.8102 | 610.3458 | 4001.156 | 3390.8102 | 0 | 3390.8102 | 610.3458 | 4001.156 | 0 |  | A
25 | COMPLETE SUB-STATION AUTOMATION SYSTEM FOR 400 KV BAY EXTENSION INCLUDING HARDWARE AND SOFTWARE FOR THE SUB-STATION AND REMOTE CONTROL SYSTEM ALONGWITH ASSOCIATED EQUIPMENT AND ACCESSORIES AS PER TECHNICAL SPECIFICATION & RELAY PROTECTION PANEL, EVENT LOGGER PANEL ,BUS BAR PROTN PAN & RELAY TOOL KITS AS PER TECH SPEC. The SAS & Bus Bar Protection scheme shall be integrated with the existing system. Allmaterials & equipment as required for successful completion shall be considered. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
25.1 | SUB-STATION AUTOMATION SYSTEM FOR PROPOSED 400 kv bay extension | SET | 1 | 1 | 0 | 1 | 0 | 181463.0988 |  | 181463.0988 | 32663.3578 | 214126.4566 | 181463.0988 | 0 | 181463.0988 | 32663.3578 | 214126.4566 | 0 | As per Record Notes of Meeting Dated 11-13 July 2023: OPTCL advised BHEL to follow the contract and propose technical solution so that the bays can be controlled from Main Control Room. BHEL indicated that this may require additional items such as Station level switch, HMIs etc., which will have commercial implication. OPTCL will resolve the issue | A
25.2 | BCU FOR CONTROLLING AND MONITORING OF THE PROPOSED (400 KV) | SET | 2 | 2 | 0 | 2 | 0 | 7251.2234 |  | 14502.4468 | 2610.4404 | 17112.8872 | 14502.4468 | 0 | 14502.4468 | 2610.4404 | 17112.8872 | 0 |  | A
25.3 | 400 KV FEEDER PROTECTION RELAY PANEL(MAIN-I WITH AUTO RECLOSURE & MAIN-II WITH AUTO RECLOSURE & BACK-UP PROTECTION ) AND TIE PROTECTION PANEL with Bus Bar Protection. | SET | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
25.4 | 400 KV, 80MVAR LINE REACTOR with NGR PROTECTION RELAY PANEL | SET | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
25.5 | 400kV CB Panel for Switched reactor protection | SET | 2 | 2 | 0 | 2 | 0 | 14501.4602 |  | 29002.9205 | 5220.5257 | 34223.4462 | 29002.9205 | 0 | 29002.9205 | 5220.5257 | 34223.4462 | 0 |  | A
25.6 | 400kV Tie Protection Panel | Nos | 1 | 1 | 0 | 1 | 0 | 14501.4602 |  | 14501.4602 | 2610.2628 | 17111.7231 | 14501.4602 | 0 | 14501.4602 | 2610.2628 | 17111.7231 | 0 |  | A
25.7 | Integration with existing Busbar protection & SAS system | SET | 1 | 1 | 0 | 1 | 0 | 225989.5567 |  | 225989.5567 | 40678.1202 | 266667.6769 | 225989.5567 | 0 | 225989.5567 | 40678.1202 | 266667.6769 | 0 |  | A
26 | FIRE FIGHTING EQIPMENT (Main Pump,Jockey Pump,DG Set cum Pump, Control Panel,Different sizes of MS pipe(to be painted for rust proof),different type of valves,Fire sensor etc for the Fire Fighting System(HIGH PRESSURE : Hydrant and Mulsifire to take care of 2 Nos 80 MVAR 400 KV Reactor and switcyard equipment and control room building. | LOT | 1 | 1 | 0 | 1 | 0 | 922746.2946 |  | 922746.2946 | 166094.333 | 1088840.6276 | 922746.2946 | 0 | 922746.2946 | 166094.333 | 1088840.6276 | 0 |  | A
27 | RECEIVING THE REACTOR AND DRAGGING AND INSTALLING ON THE PLINTH AND PLACING IN POSITION, ERECTION OF ACCESSORIES & OTHERE QUIPMENT OF THE REACTOR, EART-HING AS PER STANDARD(INCLUDING SUPPLY OF MATERIALS),VACUUM TREATMENT OF THE TANK AND WINDING,OIL FILTRATION(INCLUDING SUPPLY OF VACUUM CUM OIL FILTER MACHINE),SUPPLY & LAYING OF ALL TYPES OF CONTROL & POWER CABLES PERTAINING TO REACTOR ,TESTING AND COMMISSIONING INCLUDING ALL TESTS OF THE OILS AS PER STIPULATION IN THE STANDARD APPROVED TESTING LABORATORY AND AS PER THE INSTRUCTION OF THE ENGINEER IN CHARGE.THIS INCLUDE ALL RELATED WORKS FOR ERECTION(Transformer and its accessories,RTCC Panel etc),TESTING AND COMMISSIONING OF THE REACTORS.(CONTRACTOR TO ARRANGE POWER SUPPLY FOR FILTRATION AND VACUUM TREATMENT WORKS).IT ALSO INCLUDES SUPPLY OF ALL MATERIALS FOR ERECTTION INCLUDING T&P's. |  |  |  |  | 0 | [7 empty] | 0 | [5 empty] | A
27.1 | 400 KV, 80 MVAR LINE REACTOR in complete shape as per Technical spec: | NOS | 2 | 2 | 0 | 2 | 0 | 1638738.0124 |  | 3277476.0248 | 589945.6845 | 3867421.7093 | 3277476.0248 | 0 | 3277476.0248 | 589945.6845 | 3867421.7093 | 0 |  | A
28 | Erection of 132kV NGR & its accessories in complete shape as per Technical spec: | NOS | 2 | 2 | 0 | 2 | 0 | 71177.417 |  | 142354.8339 | 25623.8701 | 167978.704 | 142354.8339 | 0 | 142354.8339 | 25623.8701 | 167978.704 | 0 |  | A
29 | 400kV CT JB | Nos. | 4 | 4 | 0 | 4 | 0 | 2779.1424 |  | 11116.5694 | 2000.9825 | 13117.5519 | 11116.5694 | 0 | 11116.5694 | 2000.9825 | 13117.5519 | 0 |  | A
30 | 400kV CVT JB | Nos. | 4 | 2 | -2 | 2 | 0 | 2779.1424 |  | 11116.5694 | 2000.9825 | 13117.5519 | 5558.2847 | 0 | 5558.2847 | 1000.4912 | 6558.776 | -6558.776 | As per approved SLD TB-3-420-510-001-D Only two Set CVts required hence 2 Nos. JB | B
31 | 433V ACK Distribution Board | Nos. | 1 | 1 | 0 | 1 | 0 | 6102.8664 |  | 6102.8664 | 1098.5159 | 7201.3823 | 6102.8664 | 0 | 6102.8664 | 1098.5159 | 7201.3823 | 0 |  | A
[10 empty] | 40045462.0123 | 7208183.1622 | 47253645.1745 | 42094310.4312 | 10468975.8024 | 52563286.2335 | 9461391.522 | 62024677.7556 | 14771032.581
Sr. Manager/BHEL

## CIVIL WORKS_SCHEDULE VIIC
ODISHA POWER TRANSMISSION CORPORATION LIMITED
LOA No. - SGM-CPC-Construction-400/220kV GIS Ersama (Pkg-49/2021-22)-08/2020/828
Contractor: Bharat Heavy Electricals Limited
| CIVIL WORKS _SUBSTATION |  | Quantity |  |  |  |  | Unit Price |  | Amount As per Original BOQ |  |  | Amount As per Amendment-1 BOQ | [5 empty] | Remarks
Sl. No. | DESCRIPTION OF ITEMS | UNIT OF MEASUREMENT | QTY during Original Order | Total QTY as per actual | Differential Qty | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Unit Price as per BOQ | Unit Price as per least cost | Original BOQ Amount | Total GST @ 18% (Works contract), in INR | Total Amount including GST, in INR | upto 25% of BOQ Qty | Above 25% of BOQ Qty | Total Amount | Total GST @ 18% , in INR | Total Amount inclusive GST after Amendment-1 | Differential Amount (BOQ Amount and Amended Amount) inclusive of GST
1 | 2 | 3 | 4 | 5 | 6=5-4 | 7 | 8 | 9 | 10 | 11=4*9 | 12 | 13=11+12 | 14=7*9 | 15=8*10 | 16=14+15 | 17 | 18=16+17 | 19=18-13
A | CIVIL WORKS for Ersama S/s
1 | Foundations: Design, engineering, supply of all labour, material (Cement-OPC-43 Grade, MS Rod (FE-500 as per BIS-1786), coarse and fine aggregates (Sand and Metal Chips) etc) for construction of RCC (1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation, concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings. (RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks, back filling, and disposal of excess earth as per the direction of Engineer In charge.
1.1 | EXCAVATION FOR PREPARATION OF FOUNDATION WORK FOR THE SWITCHYARD COLUMN, EQUIPMENT etc.:This also includes excavation in all types of soil or rocks, back filling, and disposal of excess earth as per the direction of Engineer In charge. |  | 3700 | [15 empty] | For Input Qty of Tower & Equipment as per approved layout Dwg No. TB-420-316-001 Rev-00 and for higher wind speed. For inclusiuon of RCC retaining wall (approx. 950m) and RCC retaining wall cum boundary wall (approx. 1450m).
1.1.1 | Soft/Loose soil | Cum | 1200 | 8680 | 7480 | 1500 | 7180 | 294.733 | 195.85 | 353679.5874 | 63662.3257 | 417341.9131 | 442099.4842 | 1406203 | 1848302.4842 | 332694.4472 | 2180996.9314 | 1763655.0183 | RC 2023 rate Sl no. 2.2(i) | B | 398002018.055
1.1.2 | Hard/Dense Soil | Cum | 500 | 3620 | 3120 | 625 | 2995 | 323.4151 | 293.78 | 161707.5295 | 29107.3553 | 190814.8848 | 202134.4118 | 879871.1 | 1082005.5118 | 194760.9921 | 1276766.504 | 1085951.6192 | RC 2023 rate Sl no. 2.2(ii) | B
1.1.3 | Muddy Soil | Cum | 1400 | 10120 | 8720 | 1750 | 8370 | 368.9108 | 319.88 | 516475.0574 | 92965.5103 | 609440.5677 | 645593.8217 | 2677395.6 | 3322989.4217 | 598138.0959 | 3921127.5177 | 3311686.9499 | RC 2023 rate Sl no. 2.2(iii) | B | -29183180.6261
1.1.4 | Soft/Disintegrated Rock (not requiring blasting) | Cum | 400 | 50 | -350 | 50 | 0 | 396.6038 | 0 | 158641.5151 | 28555.4727 | 187196.9879 | 19830.1894 | 0 | 19830.1894 | 3569.4341 | 23399.6235 | -163797.3644 |  | B
1.1.5 | Hard rock (requiring blasting/using breaker machinery) | Cum | 200 | 50 | -150 | 50 | 0 | 651.7753 | 0 | 130355.0604 | 23463.9109 | 153818.9713 | 32588.7651 | 0 | 32588.7651 | 5865.9777 | 38454.7428 | -115364.2285 |  | B
1.2 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 130 | 1150 | 1020 | 162.5 | 987.5 | 5381.3497 | 5237.8 | 699575.4545 | 125923.5818 | 825499.0363 | 874469.3181 | 5172327.5 | 6046796.8181 | 1088423.4273 | 7135220.2454 | 6309721.2091 | For Input Qty of Tower & Equipment as per approved layout Dwg No. TB-420-316-001 Rev-00 and for higher wind speed. For inclusiuon of RCC retaining wall (approx. 950m) and RCC retaining wall cum boundary wall (approx. 1450m). RC 2023 rate Sl no. 3.2 (i) lower than BoQ, hence, RC rate considered. | B
1.3 | Open cast / Pile foundation for the above column/equipment/ marshalling box foundations with RCC: 1:1.5:3 (Grade M-20), excluding MS Rod and including supply of Labour all materials like Cement, coarse and fine aggregates, shuttering, proper curing of the foundations/ concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | Cum | 450 | 7450 | 7000 | 562.5 | 6887.5 | 8212.9622 | 7565.71 | 3695833.0036 | 665249.9406 | 4361082.9442 | 4619791.2545 | 52108827.625 | 56728618.8795 | 10211151.3983 | 66939770.2778 | 62578687.3336 | For Input Qty of Tower & Equipment as per approved layout Dwg No. TB-420-316-001 Rev-00 and for higher wind speed. For inclusiuon of RCC retaining wall (approx. 950m) and RCC retaining wall cum boundary wall (approx. 1450m). RC 2023 rate Sl no. 3.4 (i) lower than BoQ, hence, RC rate considered. | B
1.4 | Supply of Steel (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786) of different size (as per design) with cutting, bending, binding in position of M.S. Rod for reinfocement of foundation concrete of Piles (Under reem Pile) including supply of binding wire with supply of steel rod (FE-500 as per BIS-1786 ) | MT | 80 | 1130 | 1050 | 100 | 1030 | 73631.8175 | 68623.36 | 5890545.3961 | 1060298.1713 | 6950843.5674 | 7363181.7451 | 70682060.8 | 78045242.5451 | 14048143.6581 | 92093386.2032 | 85142542.6358 | For Input Qty of Tower & Equipment as per approved layout Dwg No. TB-420-316-001 Rev-00 and for higher wind speed. For inclusiuon of RCC retaining wall (approx. 950m) and RCC retaining wall cum boundary wall (approx. 1450m). RC 2023 rate Sl no. 3.5(i) lower than BoQ, hence, RC rate considered. | B
1.5 | Boring for under ream cast-in-Situ piling, with Manual Auger method or by using Motor driven Machinery, including supply of Bentonite required for stabilization bore of required diameter bore holes & approximate length of the bore is 10 Mtrs. with under reemed piles. |  | 1100 |  |  | 0 | [12 empty] | Pile quantity calculated for Input Qty of Tower & Equipment as per approved layout Dwg No. TB-420-316-001 Rev-00 and as per design for higher wind speed and considering each pile of 10m.
1.5.1 | 250MM DIA | Mtrs | 100 | 100 | 0 | 100 | 0 | 2051.2625 |  | 205126.2484 | 36922.7247 | 242048.9731 | 205126.2484 | 0 | 205126.2484 | 36922.7247 | 242048.9731 | 0 |  | A
1.5.2 | 300MM DIA | Mtrs | 150 | 690 | 540 | 187.5 | 502.5 | 2084.8897 | 759.63 | 312733.4606 | 56292.0229 | 369025.4836 | 390916.8258 | 381714.075 | 772630.9008 | 139073.5621 | 911704.463 | 542678.9794 | RC 2023 rate Sl no. 4.1(ii) | B
1.5.3 | 375MM DIA | Mtrs | 250 | 0 | -250 | 0 | 0 | 2153.1333 |  | 538283.3205 | 96890.9977 | 635174.3182 | 0 | 0 | 0 | 0 | 0 | -635174.3182 |  | B
1.5.4 | 400MM DIA | Mtrs | 100 | 0 | -100 | 0 | 0 | 2197.6399 |  | 219763.9942 | 39557.5189 | 259321.5131 | 0 | 0 | 0 | 0 | 0 | -259321.5131 |  | B
1.5.5 | 450MM DIA | Mtrs | 100 | 3014 | 2914 | 125 | 2889 | 2243.1356 | 1225.22 | 224313.5638 | 40376.4415 | 264690.0053 | 280391.9548 | 3539660.58 | 3820052.5348 | 687609.4563 | 4507661.991 | 4242971.9857 | RC 2023 rate Sl no. 4.1(v) | B
1.5.6 | 500MM DIA | Mtrs | 400 | 0 | -400 | 0 | 0 | 2311.3792 |  | 924551.673 | 166419.3011 | 1090970.9742 | 0 | 0 | 0 | 0 | 0 | -1090970.9742 |  | B
2 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for indooor (inside buildings) and outdoor (switchyard) cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm), fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing), including supply of Labour all materials like MS Rod, Cement, coarse and fine aggregates, shuttering, cutting, bending, binding of M.S.Rod FE-500 as per BIS-1786 including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Brickwork with KB brick ,plastering (!:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5) Supply, fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. The cable trench cover slabs shall be provided with GI Angle of suitable size as per the thickness of the slabs on the outer portions (four side) as a frame. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}. The chequered plate with MS angle stiffeners of minimum 50X50X6 mm thick (four sides and corners to corners) at the bottom for proper mechanical strength. All the MS shall be provided with anti-rusting paints of minimum two coats after the primer coat. |  |  |  |  | 0
2.1 | Cable trench with covers |  |  |  |  | 0
2.1.1 | Section 1-1 | Mtrs | 350 | 480 | 130 | 437 | 43 | 29668.1392 | 29668.1392 | 10383848.7243 | 1869092.7704 | 12252941.4947 | 12964976.8358 | 1275729.9861 | 14240706.8219 | 2563327.2279 | 16804034.0499 | 4551092.5552 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate not avialable, BoQ rate considered. | B
2.1.2 | Section 2- 2 | Mtrs | 300 | 260 | -40 | 260 | 0 | 22304.7597 |  | 6691427.898 | 1204457.0216 | 7895884.9196 | 5799237.5116 | 0 | 5799237.5116 | 1043862.7521 | 6843100.2637 | -1052784.6559 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) | B
2.1.3 | Section 3-3 | Mtrs | 250 | 330 | 80 | 312 | 18 | 19733.2638 | 19733.2638 | 4933315.9446 | 887996.87 | 5821312.8147 | 6156778.2989 | 355198.748 | 6511977.0469 | 1172155.8684 | 7684132.9154 | 1862820.1007 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) RC rate not avialable, BoQ rate considered. | B
2.1.4 | Section 4-4 | Mtrs | 300 | 165 | -135 | 165 | 0 | 11554.9178 |  | 3466475.3517 | 623965.5633 | 4090440.915 | 1906561.4434 | 0 | 1906561.4434 | 343181.0598 | 2249742.5033 | -1840698.4118 | Revised qty as per Outdoor Cable Trench layout of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-010) | B
2.2 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | LOT | 1 | 1 | 0 | 1 | 0 | 453113.3989 |  | 453113.3989 | 81560.4118 | 534673.8107 | 453113.3989 | 0 | 453113.3989 | 81560.4118 | 534673.8107 | 0 |  | A
2.3 | Cable trench crossing: Design, engineering, construction including supply of labour, materials, cement, reinforcement steel, formwork etc, and all associated works for construction of trench crossing as per technical specification and approved drawing. |  |  |  |  | 0 | [7 empty] | 0
2.3.1 | Road crossing for |  |  |  |  | 0 | [7 empty] | 0
2.3.1.1 | Section 1-1 | Lot | 1 | 1 | 0 | 1 | 0 | 1359340.1966 |  | 1359340.1966 | 244681.2354 | 1604021.432 | 1359340.1966 | 0 | 1359340.1966 | 244681.2354 | 1604021.432 | 0 |  | A
2.3.1.2 | Section 2- 2 | Lot | 1 | 1 | 0 | 1 | 0 | 906226.7978 |  | 906226.7978 | 163120.8236 | 1069347.6214 | 906226.7978 | 0 | 906226.7978 | 163120.8236 | 1069347.6214 | 0 |  | A
2.3.1.3 | Section 3-3 | Lot | 1 | 1 | 0 | 1 | 0 | 736309.2732 |  | 736309.2732 | 132535.6692 | 868844.9424 | 736309.2732 | 0 | 736309.2732 | 132535.6692 | 868844.9424 | 0 |  | A
3 | 400KV GIS buildings : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification (The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification. The area for GIS hall(s) is 55 mtrs X 15.5 mtrs appox. (The room like GIS, Relay panel & AHU hall also to be considered). The Shutter door of GIS building shall be motor operated. The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. |  |  |  |  | 0 | [7 empty] | 0 |  |  |  |  | Size of 400kV GIS Building increased by 40% as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A). Building dimensions changed from 55m x 15.5m to 77m x 15.5m. Unit Rate to be increased by 40% on pro rata basis against the change in LOT quantity.
3.1 | Boring and concreting for under ream cast-in-situ piling, with Manual Auger method or by using Motor driven Machinery,including supply of Bentonite required for stabilization of bore of required diameter bore holes applicable for under ream piles. The work includes design, engineering, supply of all materials like cement, steel (FE-500 and above as per BIS-1786 ), all coarse aggregates, fine aggregates and making RCC (1:1.5:3) grade under-reamed pile foundations (pile boring as per required depth, basing on design) as per requirement. |  |  |  |  | 0 | [7 empty] | 0
3.1.1 | 300MM DIA | Mtrs | 150 | 0 | -150 | 0 | 0 | 3229.2054 |  | 484380.8107 | 87188.5459 | 571569.3567 | 0 | 0 | 0 | 0 | 0 | -571569.3567 | Increase in pile quantity due toincrease in building length adoptation of 450mm dia pile only as proposed by BHEL. RC not available for boring with concreting. | B
3.1.2 | 375MM DIA | Mtrs | 120 | 0 | -120 | 0 | 0 | 4010.5445 |  | 481265.3446 | 86627.762 | 567893.1066 | 0 | 0 | 0 | 0 | 0 | -567893.1066 |  | B
3.1.3 | 450MM DIA | Mtrs | 500 | 1450 | 950 | 625 | 825 | 4984.7459 | 4984.7459 | 2492372.9311 | 448627.1276 | 2941000.0587 | 3115466.1639 | 4112415.3364 | 7227881.5003 | 1301018.6701 | 8528900.1703 | 5587900.1116 |  | B
3.1.4 | 500MM DIA | Mtrs | 60 | 0 | -60 | 0 | 0 | 5720.5893 |  | 343235.3579 | 61782.3644 | 405017.7224 | 0 | 0 | 0 | 0 | 0 | -405017.7224 |  | B
3.2 | RCC volume (excluding Piling concreting) including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 (including, column, Beams and roofs etc) as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 31502709.6505 |  | 31502709.6505 | 5670487.7371 | 37173197.3876 | 44103793.5108 | 0 | 44103793.5108 | 7938682.8319 | 52042476.3427 | 14869278.9551 | Unir Rate increased by 40% in against change in LOT quantity | B
3.3 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 2594074.6042 |  | 2594074.6042 | 466933.4288 | 3061008.033 | 3403425.8807 | 0 | 3403425.8807 | 612616.6585 | 4016042.5392 | 955034.5063 | Unir Rate increased by 31.2% in against change in LOT quantity | B
3.4 | Flooring of GIS room shall be epoxy paint of adequate thickness & Flooring adjacent panel rooms shall be with vitrified digital tiles with dado as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 1332153.551 |  | 1332153.551 | 239787.6392 | 1571941.1901 | 1865014.9713 | 0 | 1865014.9713 | 335702.6948 | 2200717.6662 | 628776.476 | Unir Rate increased by 40% in against change in LOT quantity | B
3.5 | External and internal wall (External (18mm thk) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 1164501.9099 |  | 1164501.9099 | 209610.3438 | 1374112.2536 | 1579064.5898 | 0 | 1579064.5898 | 284231.6262 | 1863296.2159 | 489183.9623 | Unir Rate increased by 35.6% in against change in LOT quantity | B
3.6 | Provision of ceiling in the adjacent panel room area as per specification mentioned in the civil section & approved drawings. Provision of window blinders in the Panel room. | Lot | 1 | 1 | 0 | 1 | 0 | 1140713.5949 |  | 1140713.5949 | 205328.4471 | 1346042.042 | 1596999.0328 | 0 | 1596999.0328 | 287459.8259 | 1884458.8587 | 538416.8168 | Unir Rate increased by 40% in against change in LOT quantity | B
3.7 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC with double layer glaze(taughned)of 6mm & windows shall have aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 1 | 0 | 1 | 0 | 804276.8764 |  | 804276.8764 | 144769.8378 | 949046.7142 | 1055211.2619 | 0 | 1055211.2619 | 189938.0271 | 1245149.289 | 296102.5748 | Unir Rate increased by 31.2% in against change in LOT quantity | B
3.8 | Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc. (of Legrand make),fixing of lighting fixtures & switchgear , Erection of all Lighting FIXTURES & LAMPS (LED), D.C emergency lighting (including supply). Concealed internal wiring for Cable connection for Internet LAN, socket for using Telephone including supply of all materials,board,connectors etc as required should also be considered. Cabling for EOT crane including supply and installation of Switch Board panel required for EOT crane. This is as per approved drawing and direction of Engineer In charge. | Lot | 1 | 1 | 0 | 1 | 0 | 389868.4467 |  | 389868.4467 | 70176.3204 | 460044.7671 | 545815.8254 | 0 | 545815.8254 | 98246.8486 | 644062.674 | 184017.9068 | Unir Rate increased by 40% in against change in LOT quantity | B
3.9 | Provision of smoke and fire detection & Alarmsystem of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 80426.5008 |  | 80426.5008 | 14476.7701 | 94903.2709 | 112597.1011 | 0 | 112597.1011 | 20267.4782 | 132864.5793 | 37961.3084 | Unir Rate increased by 40% in against change in LOT quantity | B
3.10 | Provision of rails & other arrangement including all type of Civil works for EOT crane. This is as per the standard practice adopted in GIS sub-station and as directed by the Engineer in Charge. | Lot | 1 | 1 | 0 | 1 | 0 | 1619881.1922 |  | 1619881.1922 | 291578.6146 | 1911459.8068 | 2267833.6691 | 0 | 2267833.6691 | 408210.0604 | 2676043.7296 | 764583.9227 | Unir Rate increased by 40% in against change in LOT quantity | B
3.11 | Provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. It includes supply of all types of materials of reputed make, labour etc to complete the work. | Lot | 1 | 1 | 0 | 1 | 0 | 2473999.5931 |  | 2473999.5931 | 445319.9268 | 2919319.5198 | 3463599.4303 | 0 | 3463599.4303 | 623447.8975 | 4087047.3277 | 1167727.8079 | Unir Rate increased by 40% in against change in LOT quantity | B
3.12 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint (plastic emulsion). Refer the specification. | Lot | 1 | 1 | 0 | 1 | 0 | 2622394.6862 |  | 2622394.6862 | 472031.0435 | 3094425.7297 | 3555967.1944 | 0 | 3555967.1944 | 640074.095 | 4196041.2894 | 1101615.5598 | Unir Rate increased by 35.6% in against change in LOT quantity | B
3.13 | Installation of Ventilation system of all equipment and materials as per technical specification (design calculation to be submitted) | Lot | 1 | 1 | 0 | 1 | 0 | 1445895.759 |  | 1445895.759 | 260261.2366 | 1706156.9956 | 2024254.0626 | 0 | 2024254.0626 | 364365.7313 | 2388619.7938 | 682462.7982 | Unir Rate increased by 40% in against change in LOT quantity | B
3.14 | Provision of Building earthing: Design,Engg,supply & erection with civil works for: (a) Protection from Lightning & (b) other conventional earthing | Lot | 1 | 1 | 0 | 1 | 0 | 846793.5937 |  | 846793.5937 | 152422.8469 | 999216.4406 | 1185511.0312 | 0 | 1185511.0312 | 213391.9856 | 1398903.0168 | 399686.5762 | Unir Rate increased by 40% in against change in LOT quantity | B
3.15 | The main entrance door of GIS buildings shall shave access control system which is sensor operated with key card for entry. Log of all the persons accessing the buildings with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 56639.1749 |  | 56639.1749 | 10195.0515 | 66834.2263 | 56639.1749 | 0 | 56639.1749 | 10195.0515 | 66834.2263 | 0 |  | A
4 | 220KV GIS buildings : Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification. The area for GIS hall(s) is 23.5 mtrsX12 mtrs appox. (The room like GIS, Relay panel & AHU hall also to be considered) Shutter door of GIS building shall be motor operated. The area given is for reference only and may vary according to requirement of the equipment to be installed inside. The contractor shall finalize the dimensions according to the equipment offered by them providing enough space & access for erection, operation and maintenance & future expansion. |  |  |  |  | 0 |  |  |  |  | 0 | 0 |  | 0 |  |  |  |  | Size of 220kV GIS Building increased by 83% as per the Layout Plan of 400/220kV GIS, Ersama (Drg. No. TB-0-420-316-001A). Building dimensions changed from 23.5m x 12m to 43m x 12m. Unit Rate to be increased by 83% on pro rata basis against the change in LOT quantity.
4.1 | Boring and concreting for under ream cast-in-situ piling, with Manual Auger method or by using Motor driven Machinery, including supply of Bentonite required for stabilization of bore of required diameter bore holes applicable for under ream piles. The work includes design, engineering, supply of all materials like cement, steel (FE-500 and above as per BIS-1786 ), all coarse aggregates, fine aggregates and making RCC (1:1.5:3) grade under-reamed pile foundations (pile boring as per required depth, basing on design) as per requirement. |  |  |  |  | 0 | [7 empty] | 0
4.1.1 | 300MM DIA | Mtrs | 140 | 0 | -140 | 0 | 0 | 3229.2054 |  | 452088.7567 | 81375.9762 | 533464.7329 | 0 | 0 | 0 | 0 | 0 | -533464.7329 | Increase in pile quantity due to increase in building length adoptation of 450mm dia pile only as proposed by BHEL. RC not available for boring with concreting. | B
4.1.2 | 375MM DIA | Mtrs | 90 | 0 | -90 | 0 | 0 | 4010.5445 |  | 360949.0084 | 64970.8215 | 425919.8299 | 0 | 0 | 0 | 0 | 0 | -425919.8299 |  | B
4.1.3 | 450MM DIA | Mtrs | 400 | 1000 | 600 | 500 | 500 | 4984.7459 | 4984.7459 | 1993898.3449 | 358901.7021 | 2352800.047 | 2492372.9311 | 2492372.9311 | 4984745.8623 | 897254.2552 | 5882000.1175 | 3529200.0705 |  | B
4.1.4 | 500MM DIA | Mtrs | 60 | 0 | -60 | 0 | 0 | 5720.5893 |  | 343235.3579 | 61782.3644 | 405017.7224 | 0 | 0 | 0 | 0 | 0 | -405017.7224 |  | B
4.2 | RCC volume (excluding Piling concreting) including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 (including, column, Beams and roofs etc) as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 11463769.1895 |  | 11463769.1895 | 2063478.4541 | 13527247.6436 | 20978697.6167 | 0 | 20978697.6167 | 3776165.571 | 24754863.1877 | 11227615.5442 | Unir Rate increased by 83% in against change in LOT quantity | B
4.3 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 1251726.0611 |  | 1251726.0611 | 225310.691 | 1477036.7521 | 1940175.3947 | 0 | 1940175.3947 | 349231.5711 | 2289406.9658 | 812370.2137 | Unir Rate increased by 55% in against change in LOT quantity | B
4.4 | Flooring of GIS room shall be epoxy paint of adequate thickness & Flooring adjacent panel rooms shall be with vitrified digital double charged tiles with dado as per technical spec & approved drawings. Provision of window blinders in the Panel room. | Lot | 1 | 1 | 0 | 1 | 0 | 529010.1108 |  | 529010.1108 | 95221.8199 | 624231.9307 | 968088.5027 | 0 | 968088.5027 | 174255.9305 | 1142344.4332 | 518112.5025 | Unir Rate increased by 83% in against change in LOT quantity | B
4.5 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 538072.6557 |  | 538072.6557 | 96853.078 | 634925.7337 | 909342.7881 | 0 | 909342.7881 | 163681.7019 | 1073024.49 | 438098.7563 | Unir Rate increased by 69% in against change in LOT quantity | B
4.6 | Provision of ceiling in the adjacent panel room area as per specification mentioned in the civil section & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 436121.7453 |  | 436121.7453 | 78501.9142 | 514623.6595 | 798102.7939 | 0 | 798102.7939 | 143658.5029 | 941761.2969 | 427137.6374 | Unir Rate increased by 83% in against change in LOT quantity | B
4.7 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC with double layer glaze(taughned) of 6mm & windows shall have aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 1 | 0 | 1 | 0 | 478035.1501 |  | 478035.1501 | 86046.327 | 564081.4771 | 740954.4827 | 0 | 740954.4827 | 133371.8069 | 874326.2896 | 310244.8124 | Unir Rate increased by 55% in against change in LOT quantity | B
4.8 | Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make),fixing of lighting fixtures & switchgear , Erection of all Lighting FIXTURES & LAMPS (LED), D.C emergency lighting (including supply). Concealed internal wiring for Cable connection for Internet LAN, socket for using Telephone including supply of all materials,board,connectors etc as required should also be considered. Cabling for EOT crane including supply and installation of Switch Board panel required for EOT crane. This is as per approved drawing and direction of Engineer In charge. | Lot | 1 | 1 | 0 | 1 | 0 | 346541.7082 |  | 346541.7082 | 62377.5075 | 408919.2157 | 634171.3261 | 0 | 634171.3261 | 114150.8387 | 748322.1647 | 339402.949 | Unir Rate increased by 83% in against change in LOT quantity | B
4.9 | Provision of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 47678.5008 |  | 47678.5008 | 8582.1301 | 56260.6309 | 87251.6564 | 0 | 87251.6564 | 15705.2981 | 102956.9545 | 46696.3236 | Unir Rate increased by 83% in against change in LOT quantity | B
4.10 | Provision of rails & other arrangement including all type of Civil works for EOT crane. This is as per the standard practice adopted in GIS sub-station and as directed by the Engineer in Charge. | Lot | 1 | 1 | 0 | 1 | 0 | 703459.4023 |  | 703459.4023 | 126622.6924 | 830082.0948 | 1287330.7063 | 0 | 1287330.7063 | 231719.5271 | 1519050.2334 | 688968.1386 | Unir Rate increased by 83% in against change in LOT quantity | B
4.11 | Provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. It includes supply of all types of materials of reputed make, labour etc to complete the work. | Lot | 1 | 1 | 0 | 1 | 0 | 2096782.9061 |  | 2096782.9061 | 377420.9231 | 2474203.8292 | 3837112.7181 | 0 | 3837112.7181 | 690680.2893 | 4527793.0074 | 2053589.1782 | Unir Rate increased by 83% in against change in LOT quantity | B
4.12 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint(plastic emulsion). Refer the specification. | Lot | 1 | 1 | 0 | 1 | 0 | 1072745.9916 |  | 1072745.9916 | 193094.2785 | 1265840.2701 | 1812940.7259 | 0 | 1812940.7259 | 326329.3307 | 2139270.0565 | 873429.7864 | Unir Rate increased by 69% in against change in LOT quantity | B
4.13 | Installation of Ventilation system of all equipment and materials as per technical specification (design calculation to be submitted) | Lot | 1 | 1 | 0 | 1 | 0 | 981398.5456 |  | 981398.5456 | 176651.7382 | 1158050.2838 | 1795959.3385 | 0 | 1795959.3385 | 323272.6809 | 2119232.0194 | 961181.7356 | Unir Rate increased by 83% in against change in LOT quantity | B
4.14 | Provision of Building earthing: Design,Engg,supply & erection with civil works for: (a) Protection from Lightning & (b) other conventional earthing | Lot | 1 | 1 | 0 | 1 | 0 | 409547.3135 |  | 409547.3135 | 73718.5164 | 483265.8299 | 749471.5836 | 0 | 749471.5836 | 134904.8851 | 884376.4687 | 401110.6388 | Unir Rate increased by 83% in against change in LOT quantity | B
4.15 | The main entrance door GIS buildings shall shave access control system which is sensor operated with key card for entry. Log of all the persons accessing the buildings with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 56639.1749 |  | 56639.1749 | 10195.0515 | 66834.2263 | 56639.1749 | 0 | 56639.1749 | 10195.0515 | 66834.2263 | 0 | Unir Rate increased by 83% in against change in LOT quantity | A
5 | CONTROL ROOM BUILDING: Design, engineering and construction of switch yard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawings and specification. (one Double storied building having the GF: Store room,Bat room, Maint room, ACDB & DCDB Room, Toilets & stair case & etc, FF : SAS room, conference room, Office room,Transit rest room, toilets, pantry etc). Control Room Building Size: 27 mtrs X 15.5 Mtrs appox The indicative plan drawing of the building is provided and details of the building shall be as per the drawing (indicative) &Tech spec. |  |  |  |  | 0 | [7 empty] | 0
5.1 | Boring and concreting for under ream cast-in-situ piling, with Manual Auger method or by using Motor driven Machinery, including supply of Bentonite required for stabilization of bore of required diameter bore holes applicable for under ream piles. The work includes design, engineering, supply of all materials like cement, steel (FE-500 and above as per BIS-1786 ), all coarse aggregates, fine aggregates and making RCC (1:1.5:3) grade under-reamed pile foundations (pile boring as per required depth, basing on design) as per requirement. |  |  |  |  | 0 | [7 empty] | 0
5.1.1 | 300MM DIA | Mtrs | 150 | 150 | 0 | 150 | 0 | 3501.1905 |  | 525178.5819 | 94532.1447 | 619710.7267 | 525178.5819 | 0 | 525178.5819 | 94532.1447 | 619710.7267 | 0 |  | A
5.1.2 | 375MM DIA | Mtrs | 90 | 90 | 0 | 90 | 0 | 4338.9048 |  | 390501.4303 | 70290.2575 | 460791.6878 | 390501.4303 | 0 | 390501.4303 | 70290.2575 | 460791.6878 | 0 |  | A
5.1.3 | 450MM DIA | Mtrs | 400 | 400 | 0 | 400 | 0 | 5369.4812 |  | 2147792.483 | 386602.6469 | 2534395.13 | 2147792.483 | 0 | 2147792.483 | 386602.6469 | 2534395.13 | 0 |  | A
5.1.4 | 500MM DIA | Mtrs | 40 | 40 | 0 | 40 | 0 | 6151.8094 |  | 246072.3751 | 44293.0275 | 290365.4026 | 246072.3751 | 0 | 246072.3751 | 44293.0275 | 290365.4026 | 0 |  | A
5.2 | RCC volume (excluding Piling concreting) including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 (including, column ,Beams and roofs etc) as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 9447414.7623 |  | 9447414.7623 | 1700534.6572 | 11147949.4195 | 9447414.7623 | 0 | 9447414.7623 | 1700534.6572 | 11147949.4195 | 0 |  | A
5.3 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 1079543.6421 |  | 1079543.6421 | 194317.8556 | 1273861.4977 | 1079543.6421 | 0 | 1079543.6421 | 194317.8556 | 1273861.4977 | 0 |  | A
5.4 | Flooring with double charged vitrified digital tiles with dado in all the rooms,Bath and toilets shall be provided with anti skid ceramic digital tiles(wall of the same also to be provided with ceramic digital tiles),Acid proof industrial tiles to be provided on the floor and full wall of the battery room as per technical spec & approved drawings. Stair case & its landing platforms are to be provided with Granite flooring. | Lot | 1 | 1 | 0 | 1 | 0 | 817870.1993 |  | 817870.1993 | 147216.6359 | 965086.8351 | 817870.1993 | 0 | 817870.1993 | 147216.6359 | 965086.8351 | 0 |  | A
5.5 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section). | Lot | 1 | 1 | 0 | 1 | 0 | 374951.7925 |  | 374951.7925 | 67491.3227 | 442443.1152 | 374951.7925 | 0 | 374951.7925 | 67491.3227 | 442443.1152 | 0 |  | A
5.6 | Provision of ceiling in the control room area as per specification mentioned in the civil section & approved drawings including, office room, SAS room, panel room, LT room, communication room, conference room, transit room, corridor etc as per direction of the engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 882438.4828 |  | 882438.4828 | 158838.9269 | 1041277.4097 | 882438.4828 | 0 | 882438.4828 | 158838.9269 | 1041277.4097 | 0 |  | A
5.7 | Doors and windows shall be of clear openable (door) and sliding (window) type with adequate locking facility. The door window frame shall be of UPVC of reputed make heavy sections with double layer toughened glaze of 6mm & windows shall have anodised aluminium grills(only GF external window). Windows shall be provided with vertical window blinder to protect from the sun ray. In the Air Conditioned area the glaze shall be double toughned. The main entrance door of the control room building shall be Transparent Automatic Sensor Glass Door(Features 1. Open and close single or both the door.2. Sequence of adjustment 3. Can be integrated with most of access control system (RFID, Biometric etc) 4. Can be paired with upto 100 remote 5. Safely 12volts DC motors eliminating the dangers of electric shock hazard.6. Overload sensor provide instant stop upon contact with obstacle.7. Starting opening force adjustment 8. Open speed adjustment 9. Soft start and stop.10. Open buffer distance adjustment when open). The bath/toilet door & its frame shall be of uPVC of reputed make. As per technical spec & approved drawing. | Lot | 1 | 1 | 0 | 1 | 0 | 1522461.0598 |  | 1522461.0598 | 274042.9908 | 1796504.0506 | 1522461.0598 | 0 | 1522461.0598 | 274042.9908 | 1796504.0506 | 0 |  | A
5.8 | Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches having ISI mark & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc. of Legrand make),fixing of lighting fixtures & switchgear, ceiling fans of 1400 sweep and regulators (including supply),exhaust fan (including supply), Erection of all Lighting FIXTURES & LAMPS (LED), D.C emergency lighting (including supply). Concealed internal wiring for Cable connection for TV,Internet LAN, socket for using Telephone including supply of all materials,board,connectors etc as required should also be considered There shall be audio visual system in the conference room for video and tele conferencing. The battery room shall have minimum of 2 Nos exhaust fan (to be calculated as per the standard design & nos. may vary accordingly) (1 main + 1 backup). One exhaust fan should be able to discharge the corrosive fumes to outside with the other one acting as backup. The exhaust fans should be electrically interlocked besides manual operation. This is as per approved drawing and direction of Engineer In charge. | Lot | 1 | 1 | 0 | 1 | 0 | 1314570.4533 |  | 1314570.4533 | 236622.6816 | 1551193.1349 | 1314570.4533 | 0 | 1314570.4533 | 236622.6816 | 1551193.1349 | 0 |  | A
5.9 | Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging. At the entrance of the cable trench to the control room building to prevent fire, sand barrier of effective size to be provided as per relevant safety codes and direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 102061.6825 |  | 102061.6825 | 18371.1028 | 120432.7853 | 102061.6825 | 0 | 102061.6825 | 18371.1028 | 120432.7853 | 0 |  | A
5.10 | Supply, fitting and fixing of stainless steel pf 304 grade in hand railing using 50mm dia of 2mm thick circular pipe with balustrade of size 32mmx32mmx32mm @0.90mtr C/C and stainless square pipe bracing of size 32mmx32mmx32mm in three rows in staircase as per approved design and specification, buffing,polishing etc with cost, conveyance, taxes of all materials, labour, T&P etc required for the complete in all respect | Lot | 1 | 1 | 0 | 1 | 0 | 380616.0067 |  | 380616.0067 | 68510.8812 | 449126.8879 | 380616.0067 | 0 | 380616.0067 | 68510.8812 | 449126.8879 | 0 |  | A
5.11 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint(plastic emulsion).Refer the specification. The ceiling of Battery room shall be acid proof paints as per specification & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 967397.7396 |  | 967397.7396 | 174131.5931 | 1141529.3327 | 967397.7396 | 0 | 967397.7396 | 174131.5931 | 1141529.3327 | 0 |  | A
5.12 | Provision of PHD and other fittings of reputed make (JAQUAR) for the control room building (in Toilets, wash room, overhead water tank of adequate capacity etc) of reputed make, provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. There shall be septic tank and soak pit of required capacity including complete sewage system as per approved drawing & technical specification & as per instruction of Engg- in-Charge. It includes supply of all types of materials of reputed make for UPVC pipe,fittings etc, labour etc to complete the work. Toilets (Provision of comboard & granite platform base standalone type wash basin) for Gents & Ladies to be provided including all good quality fittings of Jaguar make as per specification. The toilets & wash room shall have antiskid floor tiles & wall tiles of ceramic up to height of 8 feet. Provision of rain water discharge pipes at different locations and two nos of overhead water tank of 2000 ltrs capacity etc as per requirement and approved drawing. All bath room & toilet shall have water & termite proof doors ( Doors of the toilets & wash rooms shall be of solid heavy duty PVC type.) and provision of sliding louvers with exhaust fan. The urinal in the toilets shall be sensor based for automatic flushing with translucent glass partition between different urinals in the gents’ toilet. There shall be minimum 2 Nos urinals in each gents toilet. The wash basin of the toilets shall have push type water taps which will switch off automatically to reduce wastage of water. All the washbasins in the control room buildings including the ones in the toilet shall be placed on a countertop. The conference room of the CRB shall have provision of wash room with urinal, washbasin and other sanitary provisions . | Lot | 1 | 1 | 0 | 1 | 0 | 1566640.3481 |  | 1566640.3481 | 281995.2627 | 1848635.6107 | 1566640.3481 | 0 | 1566640.3481 | 281995.2627 | 1848635.6107 | 0 |  | A
5.13 | Provision of Building earthing: Design,Engg,supply & erection with civil works for: (a) Protection from Lightning & (b) other conventional earthing | Lot | 1 | 1 | 0 | 1 | 0 | 450233.3235 |  | 450233.3235 | 81041.9982 | 531275.3217 | 450233.3235 | 0 | 450233.3235 | 81041.9982 | 531275.3217 | 0 |  | A
5.14 | The main entrance door and the entry door of the HMI room of the Control room building shall shave access control system which is sensor operated with key card for entry. Log of all the persons accessing the buildings with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. | Lot | 1 | 1 | 0 | 1 | 0 | 56639.1749 |  | 56639.1749 | 10195.0515 | 66834.2263 | 56639.1749 | 0 | 56639.1749 | 10195.0515 | 66834.2263 | 0 |  | A
5.15 | Provision of Public Address System : Supply & Installation of PA as per the direction of Engineer In caharge : Latest model Combo Dual hand Wireless microphone package includes Amplifier DPA-770(75watts), Horn - SUH-45XT(40 watts with line matching), AWM-490V2 wireless mic(2 hand mic) and 15 meters speaker cable (Ahuja make). | Lot | 1 | 1 | 0 | 1 | 0 | 72615.0875 |  | 72615.0875 | 13070.7158 | 85685.8033 | 72615.0875 | 0 | 72615.0875 | 13070.7158 | 85685.8033 | 0 |  | A
6 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,colony area,approach road,control room building area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of RCC (M-20) drains on both the side of the roads for easy discharge of rain water. |  |  |  |  | 0 | [7 empty] | 0
6.1 | 7 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section(from the switch yard main gate to power transformer, approach road & infront of GIS cum control room building & Shall have drain on both side of the road. | Mtrs | 200 | 1010 | 810 | 250 | 760 | 24695.2618 | 24695.2618 | 4939052.3585 | 889029.4245 | 5828081.7831 | 6173815.4482 | 18768398.9624 | 24942214.4106 | 4489598.5939 | 29431813.0045 | 23603731.2214 | As per revised Layout Dwg No. TB-420-316-001A Rev-00. RC rate not available, BoQ rate considered. | B
6.2 | 3.75 mtrs concrete road with shoulder at both the side & shall have drain on both side of the road as per technical specification indicated in the civil section( Periphery roads outside switch yard fencing and colony roads) | Mtrs | 250 | 580 | 330 | 312 | 268 | 14953.2485 | 14953.2485 | 3738312.1375 | 672896.1847 | 4411208.3222 | 4665413.5476 | 4007470.6114 | 8672884.159 | 1561119.1486 | 10234003.3076 | 5822794.9853 | As per our Electrical Input and Approved Layout Dwg No. TB-420-316-001 Rev-00 RC rate not available, BoQ rate considered. | B
7 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme (RCC type), road-culverts, Shall have drain on both side of the road and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. All the switch yard bays , roads water drainage shall be connected to the main surface drain. As per approved drawing and specification. The MS Rod FE-500 as per BIS-1786 to be used in the RCC drain. |  |  |  |  | 0
7.1 | Storm water drain | Lots | 1 | 1 | 0 | 1 | 0 | 5354441.9128 |  | 5354441.9128 | 963799.5443 | 6318241.4571 | 5354441.9128 |  | 5354441.9128 | 963799.5443 | 6318241.4571 | 0 |  | A
7.2 | Road-culverts, drain crossings | Lots | 1 | 1 | 0 | 1 | 0 | 803166.188 |  | 803166.188 | 144569.9138 | 947736.1019 | 803166.188 |  | 803166.188 | 144569.9138 | 947736.1019 | 0 |  | A
7.3 | Cable trench crossing | Lots | 1 | 1 | 0 | 1 | 0 | 267722.3924 |  | 267722.3924 | 48190.0306 | 315912.423 | 267722.3924 |  | 267722.3924 | 48190.0306 | 315912.423 | 0 |  | A
8 | Foundations for transformers: Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road as per item under 4.2). This also includes excavation in all types of soil or rocks, back filling, and disposal of excess earth as per the direction of Engineer In charge. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL/ or any approved vendor of OPTCL) as per BIS-1786 to be used in the Transformer foundation & other works. |  |  |  |  | 0
8.1 | 500 MVA, 400/220KV ICT Total weight with oil and tank: 450 MT (appox) | Nos | 2 | 2 | 0 | 2 | 0 | 7750505.3999 |  | 15501010.7999 | 2790181.944 | 18291192.7439 | 15501010.7999 | 0 | 15501010.7999 | 2790181.944 | 18291192.7439 | 0 |  | A
8.2 | 125 MVAr, 400 KV Reactor Total weight with oil and tank: 250 MT Approximately | Nos | 1 | 1 | 0 | 1 | 0 | 3723459.7707 |  | 3723459.7707 | 670222.7587 | 4393682.5294 | 3723459.7707 | 0 | 3723459.7707 | 670222.7587 | 4393682.5294 | 0 |  | A
8.3 | OIL SUMP PIT(RCC) :Oil collection (from transformers)sump pit with provision of pump(5 HP, with auto level control , including cabling, fixing of control gear )as per CIGRE. As per spec and approved drawing. The pump shall be housed suitably on top of the Oil sump pit in a RCC roof with brick walls as per the instruction of Engineer-In-Charge. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used. >Oil capacity of each ICT in ltrs appox. a) 500 MVA, 400/220 KV: 110000 ltrs. | Nos | 1 | 1 | 0 | 1 | 0 | 3586393.106 |  | 3586393.106 | 645550.7591 | 4231943.8651 | 3586393.106 | 0 | 3586393.106 | 645550.7591 | 4231943.8651 | 0 |  | A
9 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M7.5) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | CUM | 570 | 1800 | 1230 | 712.5 | 1087.5 | 5154.8602 | 5145.91 | 2938270.317 | 528888.6571 | 3467158.974 | 3672837.8962 | 5596177.125 | 9269015.0212 | 1668422.7038 | 10937437.725 | 7470278.751 | PCC Laying for site surfacing is considered in 40% area of fenced boundary (210m x 285m size = 59850 sqm) as per Layout Dwg No. TB-420-316-001 Rev-00. RC 2023 Sl .no. 3.3(i) rate lower than BoQ rate. | B
10 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:4:8). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | CUM | 600 | 2400 | 1800 | 750 | 1650 | 1642.7903 | 1642.7903 | 985674.1521 | 177421.3474 | 1163095.4994 | 1232092.6901 | 2710603.9181 | 3942696.6082 | 709685.3895 | 4652381.9977 | 3489286.4983 | Metal Spreading for site surfacing is considered in 40% area of fenced boundary (210m x 285m size = 59850 sqm) as per Layout Dwg No. TB-420-316-001 Rev-00. RC 2023 rate higher than BoQ. Hence, BoQ rate considered. | B
11 | CONTOUR SURVEY,AND LEVELING, BACK FILLING |  |  |  |  | 0 | [7 empty] | 0
11.1 | Contour survey of the entire sub-station area including Supply of all labour & T&P by contractor. | SQM | 38400 | 250500 | 212100 | 48000 | 202500 | 4.9452 | 4.57 | 189895.0805 | 34181.1145 | 224076.195 | 237368.8506 | 925425 | 1162793.8506 | 209302.8931 | 1372096.7437 | 1148020.5487 | As per Contour & Survey Drawing. Work executed in 61.9 acres land as per OPTCL Requirement. RC 2023 Sl .no. 1.1 rate lower than BoQ rate. | B
11.2 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. | PER POINT | 5 | 14 | 9 | 6 | 8 | 113278.3497 | 30029.82 | 566391.7486 | 101950.5147 | 668342.2633 | 679670.0983 | 240238.56 | 919908.6583 | 165583.5585 | 1085492.2168 | 417149.9535 | Borehole (BH) - 05 Nos, Dynamic Cone Penetration Test (DCPT) - 06 Nos and Plate Load test (PLT) - 03 Nos were added to complete the Soil Investigation as per Actual & TS Requirement. RC 2023 Sl .no. 1.5(b) rate lower than BoQ rate. | B
12 | Cutting, Filling and Leveling of Sub-station area including supply of labour and T&P:Providing, neatly dressing up and leveling of substation area including switch yard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification. |  |  |  |  | 0
12.1 | Cutting of earth & filling of the said earth as per the direction of Engineer in Charge. | Cum | 1000 | 1000 | 0 | 1000 | 0 | 487.5952 |  | 487595.1806 | 87767.1325 | 575362.3131 | 487595.1806 | 0 | 487595.1806 | 87767.1325 | 575362.3131 | 0 |  | A
12.2 | Filling with borrowed earth beyond 30 mtrs & up to 100mtrs lead as per the direction of Engineer in Charge. | Cum | 6000 | 6000 | 0 | 6000 | 0 | 362.9765 |  | 2177859.2041 | 392014.6567 | 2569873.8608 | 2177859.2041 | 0 | 2177859.2041 | 392014.6567 | 2569873.8608 | 0 |  | A
12.3 | Filling with borrowed earth beyond 100 mtrs lead as per the direction of Engineer in Charge. | Cum | 18000 | 150000 | 132000 | 22500 | 127500 | 396.6038 | 396.6038 | 7138868.1813 | 1284996.2726 | 8423864.454 | 8923585.2266 | 50566982.951 | 59490568.1776 | 10708302.272 | 70198870.4496 | 61775005.9956 | Land development of 80270sqm area confined by retaining wall & National Highway as per Layout Dwg No. TB-0-420-607-601 & TB-0-420-316-001A and Land Usage Plan layout Dwg No. TB-420-316-001 Rev-00 based on the Contour & Survey Report. BoQ rate lower hence, BoQ rate considered. | B
13 | Land scaping & provision for platform for hoisting of National Flags and Provision of Garden: Provision of gardens in front of the control room building & other areas where can be provided as per the site Engineer's instruction, with lawn area with motorised fountain including supply of decorative plants,garden grass, adequate nos of flowering plants, 100 nos fruit bearing plants , etc with soil treatment and its plantation including materials,labour and T&P. As per the instruction of Engineer in Charge . Provision of water tap with water sprinkler arrangement and drip irrigation system including water pipe laying with control at different location including supply of all materials. Both side of the RCC roads shall also be provided with decorative plants as per the instruction of the Site Engineer. Construction of platform & suitable GI pipe & other attachment for hoisting of National Flags As per the direction of Engineer incharge. | LOT | 1 | 1 | 0 | 1 | 0 | 305851.7421 |  | 305851.7421 | 55053.3136 | 360905.0556 | 305851.7421 | 0 | 305851.7421 | 55053.3136 | 360905.0556 | 0 |  | A
14 | STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification. |  |  |  |  | 0
14.1 | Excavation in Soft & Loose Soil | Cum | 200 | 200 | 0 | 200 | 0 | 294.733 |  | 58946.5979 | 10610.3876 | 69556.9855 | 58946.5979 | 0 | 58946.5979 | 10610.3876 | 69556.9855 | 0 | Initially, RR masonry retaining wall was planned but RR masonry got replaced by RCC as per OPTCL requirement. | A
14.2 | P.C.C (1:3:6): Lean Concrete Grade M-10 | Cum | 22 | 22 | 0 | 22 | 0 | 5426.8453 |  | 119390.5976 | 21490.3076 | 140880.9052 | 119390.5976 | 0 | 119390.5976 | 21490.3076 | 140880.9052 | 0 |  | A
14.3 | RR Masonry (1:5) | Cum | 225 | 225 | 0 | 225 | 0 | 5437.7248 |  | 1223488.0692 | 220227.8525 | 1443715.9217 | 1223488.0692 | 0 | 1223488.0692 | 220227.8525 | 1443715.9217 | 0 |  | A
14.4 | P.C.C (1:2:4): Lean Concrete Grade M-15 | Cum | 2 | 2 | 0 | 2 | 0 | 6004.4429 |  | 12008.8858 | 2161.5994 | 14170.4852 | 12008.8858 | 0 | 12008.8858 | 2161.5994 | 14170.4852 | 0 |  | A
15 | SWITCH YARD FENCING: Providing and fixing of G.I Goat mesh (2.5 mm dia)( in a GI angle 50X50X6 mm frame having 50X6 mm GI flat bracing corner to corner) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, state and central government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Fly ash Brick masonry work with ratio 1:5 and cement pointing of the joints, for the fencing up to a height from the finished ground level) .This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | Mtr | 500 | 1000 | 500 | 625 | 375 | 5664.2142 | 5664.2142 | 2832107.0985 | 509779.2777 | 3341886.3763 | 3540133.8732 | 2124080.3239 | 5664214.1971 | 1019558.5555 | 6683772.7525 | 3341886.3763 | As per our Electrical Input and Approved Layout Dwg No. TB-420-316-001 Rev-00 RC rate not available, BoQ rate considered. | B
16 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant Fly ash Bricks).This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. As per approved drawing and specification. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used. Painting of the walls as per direction of the Engineer in charge. | Nos | 1 | 2 | 1 | 1 | 1 | 1548515.2583 | 1548515.2583 | 1548515.2583 | 278732.7465 | 1827248.0047 | 1548515.2583 | 1548515.2583 | 3097030.5165 | 557465.493 | 3654496.0095 | 1827248.0047 | As per our Electrical Input and Approved Layout Dwg No. TB-420-316-001 Rev-00 RC rate not available, BoQ rate considered. | B
17 | Any other civil work to be included in the schedule by the Bidder if required essential for successful completion of project, including supply of labour, material, cement reinforcement steel, form work etc. Bidder shall also quote the unit rate for the following items of works.(Rate shall be inclusive of supply of labour, material, cement, reinforcement steel, form work etc. ) |  |  |  |  | 0
17.1 | Excavation:This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. | Cu.m. | 1 | 1 | 0 | 1 | 0 | 396.6038 |  | 396.6038 | 71.3887 | 467.9925 | 396.6038 | 0 | 396.6038 | 71.3887 | 467.9925 | 0 |  | A
17.2 | Fly ash Brick masonry work using fly ash Fly ash Brick in cement sand mortar 1: 5 with Fly ash Bricks of class designation 75. | Cu.m. | 1 | 1 | 0 | 1 | 0 | 7363.3796 |  | 7363.3796 | 1325.4083 | 8688.7879 | 7363.3796 | 0 | 7363.3796 | 1325.4083 | 8688.7879 | 0 |  | A
17.3 | 12 mm thick plaster in cement sand mortar ( 1: 5 ). | Sq.m. | 1 | 1 | 0 | 1 | 0 | 170.1143 |  | 170.1143 | 30.6206 | 200.7349 | 170.1143 | 0 | 170.1143 | 30.6206 | 200.7349 | 0 |  | A
18 | STATION TRANSFORMER:Design, engineering, procurement of labour, material including all associated works for construction of foundation and DP structure for station transformers 33/0.415 KV,1000 KVA STN TRANSFORMER as per approved drawing and specification.{other accessories & materials as required need to be supplied for complete installation of transformer as per standard) and instruction of Engineer In charge. As per the specification and approved drawing. | Nos | 2 | 2 | 0 | 2 | 0 | 283195.8743 |  | 566391.7486 | 101950.5147 | 668342.2633 | 566391.7486 | 0 | 566391.7486 | 101950.5147 | 668342.2633 | 0 |  | A
19 | MAIN GATE & SWITCH YARD GATES:Design, engineering, procurement of labour, material including all associated works for construction and fixing of of a main gate and one no. switch yard gates with men gates as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of gate lights (Post top lantern type) on each pillar of the gate. It includes supply & fixing of light fixtures including LED Gate lamp, LV XLPE cables, switchgear etc required to complete works as per specification and approved drawings.(* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)} |  |  |  |  | 0 | [7 empty] | 0
19.1 | MAIN GATE (Special type gate design having RCC pillars of height 7.5 Mtr on both sides and RCC arc across the pillars, with black granite finish. Gate shall have steel lettering on the arc). | NOS | 1 | 1 | 0 | 1 | 0 | 849587.6229 |  | 849587.6229 | 152925.7721 | 1002513.395 | 849587.6229 | 0 | 849587.6229 | 152925.7721 | 1002513.395 | 0 |  | A
19.2 | WICKET GATE NEAR MAIN GATE | NOS | 1 | 1 | 0 | 1 | 0 | 283195.8743 |  | 283195.8743 | 50975.2574 | 334171.1317 | 283195.8743 | 0 | 283195.8743 | 50975.2574 | 334171.1317 | 0 |  | A
19.3 | SWITCH YARD GATE(ON BOTH SIDES OF 7MTRS. CONCRETE ROAD OF SWITCHYARD) | NOS | 2 | 3 | 1 | 2 | 1 | 396474.224 | 396474.224 | 792948.448 | 142730.7206 | 935679.1687 | 792948.448 | 396474.224 | 1189422.6721 | 214096.081 | 1403518.753 | 467839.5843 | As per our Electrical Input and Approved Layout Dwg No. TB-420-316-001 Rev-00 RC rate not available, BoQ rate considered. | B
19.4 | WICKET GATE NEAR SWITCHYARD (The wicket gate shall have biometric authentication system) | NOS | 1 | 3 | 2 | 1 | 2 | 169917.5246 | 169917.5246 | 169917.5246 | 30585.1544 | 200502.679 | 169917.5246 | 339835.0492 | 509752.5737 | 91755.4633 | 601508.037 | 401005.358 | As per our Electrical Input and Approved Layout Dwg No. TB-420-316-001 Rev-00 RC rate not available, BoQ rate considered. | B
20 | FIRE FIGHTING & DG BUILDING:(one building).Design, engineering and construction of switchyard buildings including the piling where required, the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge.As per approved drawings and specification. Area of the Fire Fighting & DG Room with portico at front side, stair case to the top of the building ,.The details of of building construction shall be as per the Tech spec. A) Area of the D.G Room Building: 10mtrsX7 mtrs (70sq mtrs), B) Area of the fire fighting Room Building: 10mtrX10 Mtrs(100 sq mtr). |  |  |  |  | 0
20.1 | RCC volume including MS rods (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 (for Pile foundation with cost of boring, Column, Beams and roofs etc.) as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 1200751.1005 |  | 1200751.1005 | 216135.1981 | 1416886.2985 | 1200751.1005 | 0 | 1200751.1005 | 216135.1981 | 1416886.2985 | 0 |  | A
20.2 | Brick masonry work in cement sand mortar 1: 6 with bricks of class designation 75kg/mm2 as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 227690.1357 |  | 227690.1357 | 40984.2244 | 268674.3601 | 227690.1357 | 0 | 227690.1357 | 40984.2244 | 268674.3601 | 0 |  | A
20.3 | Concrete Flooring to be provided on the floor l of the DG cum Fire Fighting room as per technical spec & approved drawings. | Lot | 1 | 1 | 0 | 1 | 0 | 139332.5482 |  | 139332.5482 | 25079.8587 | 164412.4069 | 139332.5482 | 0 | 139332.5482 | 25079.8587 | 164412.4069 | 0 |  | A
20.4 | External and internal wall painting with primer coat as per technical spec mentioned in the civil section. External: One coat weather coat primer + two coats of weather coat colour paint (texture paint). Internal: Two coats wall putty+solvent thinable white primer of one coat+two coats colour paint. Refer the specification. | Lot | 1 | 1 | 0 | 1 | 0 | 113278.3497 |  | 113278.3497 | 20390.1029 | 133668.4527 | 113278.3497 | 0 | 113278.3497 | 20390.1029 | 133668.4527 | 0 |  | A
20.5 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC with double layer glaze of 6mm & windows shall have aluminium grills. As per technical spec & approved drawing. | Lot | 1 | 1 | 0 | 1 | 0 | 302453.4113 |  | 302453.4113 | 54441.614 | 356895.0254 | 302453.4113 | 0 | 302453.4113 | 54441.614 | 356895.0254 | 0 |  | A
20.6 | Provision of PHD and other fittings of reputed (Jaquar make) having ISI mark ,provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing & technical specification & as per instruction of Engg- in-Charge. It includes supply of all types of materials of reputed make, labour etc to complete the work. Doors shall be of solid heavy duty PVC type. | Lot | 1 | 1 | 0 | 1 | 0 | 339835.0492 |  | 339835.0492 | 61170.3088 | 401005.358 | 339835.0492 | 0 | 339835.0492 | 61170.3088 | 401005.358 | 0 |  | A
20.7 | Internal concealed wiring,fixing of lighting fixtures(LED), fans and regulators(Electronic regulator),exhaust fan, D.C emergency lighting INCLUDING SUPPLY OF ALL ITEMS as per spec & approved drawing. | Lot | 1 | 1 | 0 | 1 | 0 | 202894.9812 |  | 202894.9812 | 36521.0966 | 239416.0778 | 202894.9812 | 0 | 202894.9812 | 36521.0966 | 239416.0778 | 0 |  | A
20.8 | Provision of smoke and fire detection system of the building. | Lot | 1 | 1 | 0 | 1 | 0 | 101391.1155 |  | 101391.1155 | 18250.4008 | 119641.5163 | 101391.1155 | 0 | 101391.1155 | 18250.4008 | 119641.5163 | 0 |  | A
20.9 | Provision of Water Tank for fire fighting below ground. | Lot | 1 | 1 | 0 | 1 | 0 | 4429184.0675 |  | 4429184.0675 | 797253.1321 | 5226437.1996 | 4429184.0675 | 0 | 4429184.0675 | 797253.1321 | 5226437.1996 | 0 |  | A
21 | SECURITY SHED & CUM VISITOR ROOM: Design, engineering, procurement of labour, material including all associated works for construction of Security shed near main gate,watch tower shed at the corners of switch yard as per the approved drawing and instruction of Engineer in charge. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Internal electrification including supply of lighting fixtures,fan with regulators and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Also includes painting of the building (in side and out side) as per recommended for colony building in the specification. |  |  |  |  | 0 | [7 empty] | 0
21.1 | SECURITY SHED:The size of the security shed shall be 3.5 mtrsX5mtrs and height of 3.5mtrs RCC roof,Fly ash Brick masonary works,plastering and painting and fixing of TATA Pravesh steel doors with frame and windows. Flooring shall be of vitrified tiles with Dado. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.The security shed shall be provided with LAN and intercom connection with security and community management system (such as My Gate or equivalent app). PCs shall be installed in the security shed for operating visitor management system. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. | Nos | 1 | 1 | 0 | 1 | 0 | 1755814.4207 |  | 1755814.4207 | 316046.5957 | 2071861.0164 | 1755814.4207 | 0 | 1755814.4207 | 316046.5957 | 2071861.0164 | 0 |  | A
22 | BORE WELL & PUMP HOUSE:Design, engineering, procurement of labour, material including all associated works for construction of two nos. bore wells for control room building including switch yard and colony quarters as per specification and approved drawing and instruction of Engineer in charge. This includes supply and fixing and commissioning of two nos submersible water pump of suitable capacity with starter and other protection. Construction of two nos pump house at ideal location for fixing of the electrical starter units. The pump house be of RCC roof and having walls of Fly ash Brick masonry and plastering and painting of external & internal walls with MS door having locking arrangement & window. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board. The size of the room shall be 2.5mtrsX2.5 mtrs having height of 3 mtrs. as per approved drawing and specification. There shall be approach road to the pump house connecting to the main/sub road of the S/S. This includes supply of materials,labours and T&P & excavation of all type of soils including rock and disposal of excess materials as per instruction of Engineer In charge Supply & laying of LV XLPE 3.5CX 35 sq mm cable from ACDB to pump house, control gear & earthing of the system etc to complete the scheme as per approved drawing & instruction of Engineer-in charge. There shall be pipe link between 2 borewells with butterfly type control valve so that in case of failure of one borewell the other one can be accessed. There shall be Fully Automatic Water Level Controller with Indicator & Up and Down Tank Sensor with dry run protection for filling up the water tanks automatically. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. | LOT | 1 | 1 | 0 | 1 | 0 | 1755814.4207 |  | 1755814.4207 | 316046.5957 | 2071861.0164 | 1755814.4207 | 0 | 1755814.4207 | 316046.5957 | 2071861.0164 | 0 |  | A
23 | COLOUR CODING, BAY MARKING Etc: Design, engineering, procurement of labour, material including all associated works for the followings. This should be as per direction of site In charge. a)Color coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof sticker (fluorescent type) may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed. Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 1 | 0 | 1 | 0 | 1132783.4972 |  | 1132783.4972 | 203901.0295 | 1336684.5267 | 1132783.4972 | 0 | 1132783.4972 | 203901.0295 | 1336684.5267 | 0 |  | A
24 | STORE SHED:Design, engineering, procurement of labour, material including all associated works for construction of store shed as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no store shed of floor size 10X10 mtr having Fly ash Brick walls and plastering with RCC roof. The flooring shall be of 75 mm thickness PCC (mix ratio1:2:4) over RR masonry works (as per standard practice of flooring). Provision of adequate nos of MS racks (proper paintings also to be done as per the direction of site in charge) for keeping the spare materials. The height of the shed shall be 4mtrs above the plinth. Internal concealed wiring (including supply of flexible copper FRP 1.1 KV PVC wire,conduits & its accessories,modular type switches & switch board,Junction boxes with required MCB & Earth leakage detector switcghear etc),fixing of lighting fixtures & switchgear ,ceiling fans of 1400 sweep and regulators( including supply) and provision of incoming AC supply from the main ACDB/outdoor kiosks installed for street light or colony quarters. Also includes painting of the building (in side and out side) as per recommended for colony building in the specification.Store shed door shall have access control system which is sensor operated with key card for entry. Log of all the persons accessing the store shed with date and time stamp shall be kept in the system. There shall be provision for manual override of the system for exigencies as per direction of engineer in charge. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment (including supply of FFE) at strategic location suitable for wall hanging as per direction of engineer in charge. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. (* REMARKS : FOR SUPPLY OF ALL THE CABLES AS INDICATED ARE COVERED IN THE supply)} | Lot | 1 | 1 | 0 | 1 | 0 | 2265566.9944 |  | 2265566.9944 | 407802.059 | 2673369.0534 | 2265566.9944 | 0 | 2265566.9944 | 407802.059 | 2673369.0534 | 0 |  | A
25 | Anti-Weed Treatment |  |  |  |  | 0 | [7 empty] | 0
25.1 | Supply of labour,T&P,Chemicals and other necessary arrangements for anti-weed treat of the switch-yard areas,controlroom etc. as per the instruction of Engineer-in-Charge.The chemical to be sprayed as per the standard practice adopted for antiweed treatment of sub-station area & as per the technical specification. | Sq Mtrs | 17500 | 23940 | 6440 | 21875 | 2065 | 28.6821 | 28.6821 | 501936.2153 | 90348.5188 | 592284.7341 | 627420.2691 | 59228.4734 | 686648.7425 | 123596.7737 | 810245.5162 | 217960.7821 | RC rate not available, BoQ rate considered. | B
26 | VEHICLE PARKING SHED: The size of the parking area shall be 15mtrs X 15 mtrs, out of the entire area there shall be provision of shed for 5 mtrs X 15 mtrs and rest of the area shall be without shed. 100 mm thick PCC(1:2:4) flooring after the preparing the foundation base & Roof of the parking place shall be RCC & Parking shed shall be as per TS-E6-Civil & as per the direction of Engineer in Charge. The MS Rod FE-500 as per BIS-1786 to be used in the building. | Lot | 1 | 1 | 0 | 1 | 0 | 2265566.9944 |  | 2265566.9944 | 407802.059 | 2673369.0534 | 2265566.9944 | 0 | 2265566.9944 | 407802.059 | 2673369.0534 | 0 |  | A
27 | Construction of township/colony (residential quarters) for staff and employees of the employer. Layout, design, survey, leveling, site dressing and clearing of the area, soil investigation, excavation,piling, PCC, RCC, brick work, plastering ,flooring(flooring shall be with vitrified tiles of reputed make with a dado of minimum 6 inches),fixing of doors (TATA pravesh make), windows and window grills, including all labour material like cement ,sand aggregate, bricks, reinforcements etc with all bought items required for completion of the quarters as per approved construction drawings with all facilities for supply of drinking water. The outer paint shall be applied with weather coat synthetic enamel paint as per the standard practice of application and the inner paint shall be applied with distemper of approved quality as per the instruction and approval of the same by OPTCL. This also includes excavation in all types of soil or rocks,including pile foundation & capping upto plinth level, back filling,and disposal of excess earth as per the direction of Engineer In charge. Internal electrical wiring with fixing of light fixtures and fans with electronic regulators and exhaust fans as per technical specification and approved drawing. Construction of over head RCC tank(1000 ltrs capacity one for each quarters), sewerage disposal and connection with main sewerage/ septic tank and soak pit, storm water and surface drainage, culverts, roads, with suitable radius on the curves and its connection with main road the substation, street lighting, internal lighting, internal plumbing and sanitation including internal/external finishing of quarters etc. required for completion of the town ship.The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. Installation of smoke and fire detection & Alarm system of the building. Provision of conventional fire fighting equipment(including supply of FFE) at strategic locatiosn suitable for wall hanging as per direction of engineer in charge. |  |  |  |  | 0 | [7 empty] | 0
27.1 | "D" type Quarter As per technical specification: 1 no quarter on ground floor & the size of quarter plinth area shall be 120 Sq Mtrs(appox) (includes supply of all materials, labour & T&P required for completion of work in full shape). Ceiling to be provided in bed rooms and living room. Premium curtains with pelmet to be provided for all doors & windows. D-Type quarter need to be used as furnished guest house having following items & facilities: | SQ Mtr | 120 | 140 | 20 | 140 | 0 | 22776.5303 |  | 2733183.63 | 491973.0534 | 3225156.6835 | 3188714.2351 | 0 | 3188714.2351 | 573968.5623 | 3762682.7974 | 537526.1139 | 16.67% increased. Rate Contract rate not available | B
27.1.1 | 1.5 ton, 5 star Inverter (split) type Air Conditioners of Hitachi/Mitsubishi/Voltas/Carrier/BlueStar make | Nos | 4 | 4 | 0 | 4 | 0 | 56639.1749 |  | 226556.6994 | 40780.2059 | 267336.9053 | 226556.6994 | 0 | 226556.6994 | 40780.2059 | 267336.9053 | 0 |  | A
27.1.2 | Durian make King size cot with mattress & all other amenities like bed side table, Coffee Table with sitting arrangement(two chairs & one single sofa) in all the bed rooms, bed sheets, pillow etc of reputed make.Developing Waredrobe,hangers for hanging cloths in each room for storage of Baggages and Cloths etc.Bathing requirements like Bath Towels, Hand Towels etc. (02 sets for all the bed rooms). Decoratives Such as wall ceinic Hangers, Doors and Windows Curtains (02 Sets for all doors and Windows) | Set | 3 | 3 | 0 | 3 | 0 | 283195.8743 |  | 849587.6229 | 152925.7721 | 1002513.395 | 849587.6229 | 0 | 849587.6229 | 152925.7721 | 1002513.395 | 0 |  | A
27.1.3 | Geyser-10 Ltr capacity of Bajaj/V-Guard/Phillips/Crompton make | Nos | 3 | 3 | 0 | 3 | 0 | 11328.4284 |  | 33985.2852 | 6117.3513 | 40102.6365 | 33985.2852 | 0 | 33985.2852 | 6117.3513 | 40102.6365 | 0 |  | A
27.1.4 | Dining table with 8 chairs of Durian/Godrej make | Set | 1 | 1 | 0 | 1 | 0 | 283195.8743 |  | 283195.8743 | 50975.2574 | 334171.1317 | 283195.8743 | 0 | 283195.8743 | 50975.2574 | 334171.1317 | 0 |  | A
27.1.5 | Modular kitchen with exhaust chimney system, gas stove, and required utensils(1. 02 Cook Ware and Dinner Sets for 08 persons 2. Induction cooking heaters for cooking capacity of 10 persons load at a stretch). | Lot | 1 | 1 | 0 | 1 | 0 | 444339.6527 |  | 444339.6527 | 79981.1375 | 524320.7902 | 444339.6527 | 0 | 444339.6527 | 79981.1375 | 524320.7902 | 0 |  | A
27.1.6 | Durian make Sofa set (3+1+1) with center table for drawing room | Set | 1 | 1 | 0 | 1 | 0 | 169917.5246 |  | 169917.5246 | 30585.1544 | 200502.679 | 169917.5246 | 0 | 169917.5246 | 30585.1544 | 200502.679 | 0 |  | A
27.1.7 | RO & UV Water purifier with cooling water system of Aquaguard/Bluestar/Kent make | Set | 1 | 1 | 0 | 1 | 0 | 28320.0819 |  | 28320.0819 | 5097.6148 | 33417.6967 | 28320.0819 | 0 | 28320.0819 | 5097.6148 | 33417.6967 | 0 |  | A
27.1.8 | 5 start inverter compressor frost free Refrigerator of 600 Ltr capacity, side-by-side door with ice and water dispenser of LG/Samsung/Whirlpool make | Nos | 1 | 1 | 0 | 1 | 0 | 215229.2601 |  | 215229.2601 | 38741.2668 | 253970.5269 | 215229.2601 | 0 | 215229.2601 | 38741.2668 | 253970.5269 | 0 |  | A
27.1.9 | 55 inch OLED TV set of Sony/LG make with supply of Set up Box facility forl the television unit with recharge of the set up box for two years) Any other requirement as per discretion of Eingeer Incharge is to be supplied. | Nos | 1 | 1 | 0 | 1 | 0 | 198237.6065 |  | 198237.6065 | 35682.7692 | 233920.3757 | 198237.6065 | 0 | 198237.6065 | 35682.7692 | 233920.3757 | 0 |  | A
27.2 | "E" type Quarter As per technical specification (one no. two storied flat. Each flat shall be with 2 nos quarters on ground floor & 2 Nos quarters on 1st floor). (There shall be 4 Nos quarters to be accommodated in one flat as E1,E2,E3 & E4) | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
27.2.1 | "E" type Quarter As per technical specification: 2 nos quarters on ground floor & the quarters to be accommodated in ground floor E1 & E2 (Each quarter size plinth area shall be 73 Sq Mtrs(appox) (includes supply of all materials, labour & T&P required for completion of work in full shape for construction above footing/pile cap level) | SQ Mtr | 146 | 146 | 0 | 146 | 0 | 22754.7714 |  | 3322196.6301 | 597995.3934 | 3920192.0235 | 3322196.6301 | 0 | 3322196.6301 | 597995.3934 | 3920192.0235 | 0 |  | A
27.2.2 | "E" type Quarter As per technical specification: 2 nos quarters on first floor & the quarters to be accommodated in ground floor, E3 & E4 (Each quarter size plinth area shall be 73 Sq Mtrs(appox) (includes supply of all materials, labour & T&P required for completion of work in full shape for construction above footing/pile cap level) | SQ Mtr | 146 | 146 | 0 | 146 | 0 | 21622.3242 |  | 3156859.3353 | 568234.6804 | 3725094.0157 | 3156859.3353 | 0 | 3156859.3353 | 568234.6804 | 3725094.0157 | 0 |  | A
28 | Boundary wall: (FOR NORMAL DESIGN) Soil investigation, Design, engineering, for construction of boundary wall including the piling where required & procurement of material like cement, steel, bricks', suitable GI '' post to be provided at the top of the B/W, single concertina wire runs in loops on fence GI post with blade tape with BT-10 to BT-60 concertina wire CBT-65 with OD:450-960 mm, hot dipped galvanised razor wire with bright & beautiful blade for fixing to the GI post and other materials labour including all associated works for construction of boundary-wall along the property line of the sub-station as per technical specification and instruction of the Engineer in Charge.(the size of the bricks shall be 250mm having 1st class Fly-ash brick having compressive strength with 75kg/cm2). The B/W shall be of RCC column & beam type frame OR Pre fabricated RCC structures as per tech spec.This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth, painting of B/W including supply of paints as per the direction of Engineer In charge and approved drawing. There shall be concrete road of 6 feet width all along the periphery of the boundary wall for supervision of the substation perimeter by security personnel. Provision of CCTV and electric pole around the boundary wall coving the whole length of the boundary wall with no blind spots.The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used . | RM | 1100 | 3000 | 1900 | 1375 | 1625 | 16992.6426 | 16992.6426 | 18691906.8503 | 3364543.2331 | 22056450.0834 | 23364883.5629 | 27613044.2107 | 50977927.7736 | 9176026.9992 | 60153954.7728 | 38097504.6894 | As per revised Layout Dwg No. TB-0-420-316-001A & Land Usage Plan Layout Dwg No. TB-420-316-001 Rev-00. RC rate not available, BoQ rate considered. | B
29 | PLATFORM FOR STORING EQUIMENTS:Design, engineering, procurement of labour, material including all associated works for construction of a platform for storing of bushings,Instrument transformers etc, as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the specification,approved drawing and direction of Engineer In charge. One no platform outside the store shed RR masonry (compacted) with PCC (1:2:4) at the top for storing the transformer bushings, Instrument transformers, transformer oil drums etc. Platform shall have provision of sand bed for storing insulators. The floor size of the platform shall be 15mtrX10 mtr with Galvanised Corrugated Sheet (Tata Make) top cover and associated MS supporting structure duly painted. | Lot | 1 | 1 | 0 | 1 | 0 | 1132783.4972 |  | 1132783.4972 | 203901.0295 | 1336684.5267 | 1132783.4972 | 0 | 1132783.4972 | 203901.0295 | 1336684.5267 | 0 |  | A
30 | PROVISION OF RAMP:Design, engineering, procurement of labour, material including all associated works for construction and fixing of Ramp as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of a ramp of adequate size and capable of for loading and unloading of the materials of 5 Ton capacity from the lorry or to the lorry near the store shed. Adequate size of MS frames and RCC (1:1.5:3) based ramps to be used for the said purpose. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL as per BIS-1786 ) to be used . | Lot | 1 | 1 | 0 | 1 | 0 | 1132783.4972 |  | 1132783.4972 | 203901.0295 | 1336684.5267 | 1132783.4972 | 0 | 1132783.4972 | 203901.0295 | 1336684.5267 | 0 |  | A
Extra Item No. 1 | Supplying and filling good quality local sand under floors/foundations including watering, ramming, consolidating and dressing complete. | Cum | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | As per recommendations of OPTCL Civil Consultant for RCC retaining wall (approx. 950m) and RCC retaining wall cum boundary wall (approx. 1450m). | A
Against item no. 1.5, 3, 4 & 5 | Installation of initial piles and their testings in accordance with IS 2911 (Part IV) - vertical load testing | Each | 0 | 0 | 0 | 0 | 0 | 141507.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Not required as per OPTCL | A
Against item no. 1.5, 3, 4 & 5 | Installation of initial piles and their testings in accordance with IS 2911 (Part IV) - horizontal load testing | Each | 0 | 0 | 0 | 0 | 0 | 110860 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
Against item no. 1.5, 3, 4 & 5 | Installation of initial piles and their testings in accordance with IS 2911 (Part IV) - cyclic vertical load testing | Each | 0 | 0 | 0 | 0 | 0 | 110400 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
Against item no. 1.5, 3, 4 & 5 | Routine pile testings in accordance with IS 2911 (Part IV) - vertical load testing | Each | 0 | 0 | 0 | 0 | 0 | 35132.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
Against item no. 1.5, 3, 4 & 5 | Routine pile testings in accordance with IS 2911 (Part IV) - horizontal load testing | Each | 0 | 0 | 0 | 0 | 0 | 35592.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
Against item no. 1.5, 3, 4 & 5 | Routine pile testings in accordance with IS 2911 (Part IV) - cyclic vertical load testing | Each | 0 | 0 | 0 | 0 | 0 | 35132.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
Against item no. 1.5, 3, 4 & 5 | Integrity testing of Pile using Low Strain/ Sonic Integrity Test/ Sonic Echo Test method in accordance with IS 14893 | Each | 0 | 0 | 0 | 0 | 0 | 1132.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Not required as per OPTCL. | A
Against item no. 11.2 | Soil investigation: Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge for other than bore-holes. | Lot | 0 | 0 | 0 | 0 | 0 | 319700 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | A
[6 empty] | 0 | [7 empty] | 0
B | CIVIL WORKS for New Duburi S/s Extn. |  |  |  |  | 0 | [7 empty] | 0
1 | Foundations : Design, engineering, supply of all labour, material (Cement-OPC-43 Grade,MS Rod FE-500 as per BIS-1786 , coarse and fine aggregates(Sand and Metal Chips) etc) for construction of RCC ( 1:1.5:3) & PCC (1:3:6), RCC footings of any depth, pedestal and piling as per requirement including soil investigation, excavation,concreting, shuttering, grouting, underpinning and back filling of foundations etc complete for the following switch yard gantry/ portal structures and equipment support & others as per the technical specification and approved drawings.(RCC RATIO 1:1.5:3). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. |  |  |  |  | 0 | [7 empty] | 0
1.1 | SWITCHYARD GANTRY/ PORTAL STRUCTURE FOUNDATIONS. |  |  |  |  | 0 | [7 empty] | 0
1.1.1 | 400 KV COLUMN with peak (4TP) | Nos | 9 |  |  | 0 | [7 empty] | 0
1.1.2 | 400 KV COLUMN without peak (4T) | Nos | 5 |  |  | 0 | [7 empty] | 0
1.2 | Equipment foundations : |  |  |  |  | 0 | [7 empty] | 0
1.2.1 | 420 KV,2000-1000-500A,63 KA,5CORE SINGLE PHASE CURRENT TRANSFORMER | NOS | 12 |  |  | 0 | [7 empty] | 0
1.2.2 | 420 KV,2000A,63 KA,ISOLATORS |  |  |  |  | 0 | [7 empty] | 0
1.2.2.a | WITH ONE EARTH SWITCH | NOS | 7 |  |  | 0 | [7 empty] | 0
1.2.2.b | WITH TWO EARTH SWITCH | NOS | 2 |  |  | 0 | [7 empty] | 0
1.2.3 | 420 KV,4400pF,3CORE,SINGLE PHASE CAPACITOR VOLTAGE TRANSFORMER | NOS | 6 |  |  | 0 | [7 empty] | 0
1.2.4 | 420KV,4000A,63KA,SF6,CIRCUIT BREAKER WITH SUPPORT STRUCTURE | NOS | 4 |  |  | 0 | [7 empty] | 0
1.2.5 | 390 KV, METAL OXIDE SURGE ARRESTOR, 10KA , Class-III | NOS | 9 |  |  | 0 | [7 empty] | 0
1.2.6 | 400 KV Bus Post Insulators | NOS | 48 |  |  | 0 | [7 empty] | 0
1.2.7 | 145 KV CT (800-400-200/1-1-1) FOR NGR | NOS | 2 |  |  | 0 | [7 empty] | 0
1.2.8 | BAY MARSHALLING KIOSK | NOS | 1 |  |  | 0 | [7 empty] | 0
1.2.9 | SWITCH YARD AC CONSOLE FOR LIGHTING | NOS | 1 |  |  | 0 | [7 empty] | 0
1.2.10 | SWITCH YARD RECEPTACLE BOARD FOR TFR OIL FILTERATION (01 no. near 400 KV Reactor) | NOS | 1 |  |  | 0 | [7 empty] | 0
1.2.11 | SWITCH YARD RECEPTACLE BOARD FOR WELDING & OTHER EMERGENCY (01 nos on 220 kV bay & 03 Nos in 400 KV Bay) | NOS | 1 |  |  | 0 | [7 empty] | 0
1.3 | EXCAVATION.:This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge (for foundations of 1.1 to 1.2.11). |  |  |  |  | 0 | [7 empty] | 0
1.3.1 | Soft/Loose Soil | Cum | 1000 | 1775 | 775 | 1250 | 525 | 294.733 | 195.85 | 294732.9895 | 53051.9381 | 347784.9276 | 368416.2368 | 102821.25 | 471237.4868 | 84822.7476 | 556060.2345 | 208275.3069 | RC 2023 rate Sl no. 2.2(i) | B
1.3.2 | Hard/Dense Soil | Cum | 600 | 950 | 350 | 750 | 200 | 323.4151 | 293.78 | 194049.0354 | 34928.8264 | 228977.8617 | 242561.2942 | 58756 | 301317.2942 | 54237.113 | 355554.4071 | 126576.5454 | RC 2023 rate Sl no. 2.2(ii) | B
1.3.3 | Muddy Soil | Cum | 100 | 160 | 60 | 125 | 35 | 368.9108 | 319.88 | 36891.0755 | 6640.3936 | 43531.4691 | 46113.8444 | 11195.8 | 57309.6444 | 10315.736 | 67625.3804 | 24093.9113 | RC 2023 rate Sl no. 2.2(iii) | B
1.3.4 | Soft / Disintegrated rock (Not required blasting) | Cum | 1000 | 1565 | 565 | 1250 | 315 | 396.6038 | 396.6038 | 396603.7879 | 71388.6818 | 467992.4697 | 495754.7348 | 124930.1932 | 620684.928 | 111723.287 | 732408.215 | 264415.7454 | BoQ rate lower than RC rate | B
1.3.5 | Hard rock (requiring blasting/using breaker machinery) | Cum | 500 | 780 | 280 | 625 | 155 | 651.7753 | 651.7753 | 325887.6511 | 58659.7772 | 384547.4283 | 407359.5639 | 101025.1718 | 508384.7357 | 91509.2524 | 599893.9882 | 215346.5599 | BoQ rate lower than RC rate | B
1.4 | Open cast foundation for the above equipment & Tower Column foundations { Sl No. 1.1 & 1.2} with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used, Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. | Cum | 887 | 1370 | 483 | 1108 | 262 | 8212.9622 | 8212.9622 | 7284897.4982 | 1311281.5497 | 8596179.0479 | 9099962.1511 | 2151796.1043 | 11251758.2554 | 2025316.486 | 13277074.7414 | 4680895.6935 | BoQ rate lower than RC rate | B
1.5 | Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labour, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. | Cum | 180 | 170 | -10 | 170 | 0 | 5381.3497 |  | 968642.937 | 174355.7287 | 1142998.6657 | 914829.4405 | 0 | 914829.4405 | 164669.2993 | 1079498.7398 | -63499.9259 |  | B
2 | Cable Trenches: Design, engineering, and construction of RCC cable trenches and all associated works for cable trench and cable trench crossings as per technical specifications and approved drawings and as per direction of the Engineer in Charge. (1) This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. (2) Design, Engineering, Providing and laying of plain cement concrete (PCC 1:3:6) of grade M10 with approved quality coarse aggregates (Nominal size 12mm to 20mm) , fine aggregates, cement in column and equipment foundation as blind layer inclusive of labour charges for concrete mixing & curing. This includes supply of all labourers, T&P and dewatering wherever required as per Technical specification and instruction of Engineer In charge. (3) Open cast foundation for the cable trench with RCC: 1:1.5:3 (Grade M-20 Nominal mixing),including supply of Labour all materials like MS Rod,Cement, coarse and fine aggregates,shuttering,cutting,bending,binding of M.S.Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used including supply of binding wire proper curing of the foundations/concrete and T&P in line with the Specification and as per direction of Engineer in Charge. (4) Brickwork with KB brick ,plastering (1:6 Ratio) & curing, wherever required including the supply of labour,material, cement, etc. (5)Supply,fabrication & Fixing of MS Angle(G.I) for cable tray support (as per specification). The cable tray support frame shall be pre fabricated GI angle as per requirement and to be welded with the plate fixed on the trench wall for better rigidity. The plate (6mm) fixed on the wall are also to be welded with the MS rods provided for the trench wall before concreting. (6) Precast of RCC covers (1:1.5:3) and its fixing on the cable trench as per spec and instruction of Engg. In Charge. The cable trench cover slabs shall be provided with GI Angle of suitable size as per the thickness of the slabs on the outer portion (four side) as a frame. (7) CABLE TRENCHES INSIDE THE CONTROL ROOM SHALL BE COVERED WITH M.S CHEQUERED PLATE(Duly painted as per instruction of Engg in charge) INCLUDING STANDARD SUPPORT STAND {HD Galvanised (M.S JOIST ,CHANNEL,ANGLE)}. The chequered plate with MS angle stiffeners of minimum 50X50X6 mm thick (four sides and corners to corners) at the bottom for proper mechanical strength. All the MS shall be provided with anti-rusting paints of minimum two coats after the primer coat. |  |  |  |  | 0 | [7 empty] | 0
2.1 | Cable trench with covers (minimum thickness of cable trench wall to be 150 mm) |  |  |  |  | 0 | [7 empty] | 0
2.1.1 | Section 1-1 | Mtrs | 80 | 200 | 120 | 100 | 100 | 29668.1392 | 29668.1392 | 2373451.137 | 427221.2047 | 2800672.3416 | 2966813.9212 | 2966813.9212 | 5933627.8425 | 1068053.0116 | 7001680.8541 | 4201008.5125 | RC rate not available, BoQ rate considered. | B
2.1.2 | Section 2- 2 | Mtrs | 120 | 80 | -40 | 80 | 0 | 22304.7597 |  | 2676571.1592 | 481782.8087 | 3158353.9678 | 1784380.7728 | 0 | 1784380.7728 | 321188.5391 | 2105569.3119 | -1052784.6559 |  | B
2.1.3 | Section 4-4 | Mtrs | 150 | 550 | 400 | 187 | 363 | 11554.9178 | 11554.9178 | 1733237.6759 | 311982.7817 | 2045220.4575 | 2160769.6359 | 4194435.1756 | 6355204.8115 | 1143936.8661 | 7499141.6775 | 5453921.22 | RC rate not available, BoQ rate considered. | B
2.2 | Rain water harvesting system as per Technical specification and approval of drawing and as per the direction of the Engineer in charge. | NOS | 1 | 1 | 0 | 1 | 0 | 283195.8743 |  | 283195.8743 | 50975.2574 | 334171.1317 | 283195.8743 | 0 | 283195.8743 | 50975.2574 | 334171.1317 | 0 |  | A
2.3 | Cable trench crossing:Design,engineering,construction including supply of labour,materials,cement,reinforcement steel,formwork etc,and all associated works for construction of trench crossing as per technical specification and approved drawing. |  |  |  |  | 0 | [7 empty] | 0
2.3.1 | Road crossing for |  |  |  |  | 0 | [7 empty] | 0
2.3.1.1 | Section 1-1 | Lot | 1 | 1 | 0 | 1 | 0 | 1246061.8469 |  | 1246061.8469 | 224291.1324 | 1470352.9794 | 1246061.8469 | 0 | 1246061.8469 | 224291.1324 | 1470352.9794 | 0 |  | A
3 | Roads: Design, construction of roads and walkways/ shoulders within sub-station(Switch yard area,approach road, control room area, main gate to the switch yard gate etc) as per specification, layout and approved drawings complete. This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Enginer In charge. Provision of drains on both the side of the roads for easy discharge of rain water.(Refer the indicative drawing of s/s layout) |  |  |  |  | 0 | [7 empty] | 0
3.1 | 3.75 mtrs concrete road with shoulder at both the side as per technical specification indicated in the civil section & shall have drain on both side of the road. | MTRS | 200 | 240 | 40 | 240 | 0 | 14953.2485 |  | 2990649.71 | 538316.9478 | 3528966.6578 | 3588779.652 | 0 | 3588779.652 | 645980.3374 | 4234759.9893 | 705793.3316 |  | B
3.2 | 7 mtrs wide Concrete roads with shoulder as per specification indicated in the civil section. & shall have drain on both side of the road. 7 Mtrs wide road inside the switchyard to be connected to switch yard main gate. | MTRS | 70 | 70 | 0 | 70 | 0 | 24695.2618 |  | 1728668.3255 | 311160.2986 | 2039828.6241 | 1728668.3255 | 0 | 1728668.3255 | 311160.2986 | 2039828.6241 | 0 |  | A
4 | Drainage system:Collection of rainfall data, Design, construction of storm water drainage scheme, road-culverts, and drains crossing cable trenches etc. as per specification and approved drawing. This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge.All the switcyard bays , roads water drainage shall be connected to the mainsurface drain.As per approved drawing and specification. |  |  |  |  | 0 | [7 empty] | 0
4.1 | Storm water drain | Lots | 1 | 1 | 0 | 1 | 0 | 3212664.7521 |  | 3212664.7521 | 578279.6554 | 3790944.4075 | 3212664.7521 | 0 | 3212664.7521 | 578279.6554 | 3790944.4075 | 0 |  | A
4.2 | Road-culverts, drain crossings | Lots | 1 | 1 | 0 | 1 | 0 | 481900.3062 |  | 481900.3062 | 86742.0551 | 568642.3614 | 481900.3062 | 0 | 481900.3062 | 86742.0551 | 568642.3614 | 0 |  | A
4.3 | Cable trench crossing | Lots | 1 | 1 | 0 | 1 | 0 | 160633.4354 |  | 160633.4354 | 28914.0184 | 189547.4538 | 160633.4354 | 0 | 160633.4354 | 28914.0184 | 189547.4538 | 0 |  | A
5 | Foundations for transformers :Design, engineering, supply of labour, material, equipments and construction of Auto-transformer/Transformer foundation including piling if any, all associated works, rail tracks, jacking pads,anchor block RCC and PCC, miscellaneous structural steel including oil collection pits, MS grating(if required), gravel filling, and other items etc. not mentioned herein, but specifically required for the completion of the work as per technical specification and approved drawing. (Rate shall be inclusive of cement, reinforcement steel, angles,flats and form work etc.)(all cement concrete shall have RCC ratio 1:1.5:3). The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used . Transformer RCC foundation and Rail Track should be extended upto the approaching road (However,the height of RCC foundation beyond transformer main plinth area should be same as height of concrete road as per item under 4.1). This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. 1. 400 kv 80 MVAR REACTOR (2 Nos) 2. 132 KV NGR (2 Nos.) |  |  |  |  | 0 | [7 empty] | 0
5.1 | 80 MVAR, 400 KV Reactor a) Overall dimension of transformer(appox) Length:7200 mmX Width 6000 mmX Height 7000 mm b) Total weight with oil and tank: 120 MT (appox) | Nos | 2 | 2 | 0 | 2 | 0 | 3670218.9265 |  | 7340437.8531 | 1321278.8136 | 8661716.6666 | 7340437.8531 | 0 | 7340437.8531 | 1321278.8136 | 8661716.6666 | 0 |  | A
5.2 | 132 KV NGR | Nos | 2 | 2 | 0 | 2 | 0 | 594711.8305 |  | 1189423.6611 | 214096.259 | 1403519.9201 | 1189423.6611 | 0 | 1189423.6611 | 214096.259 | 1403519.9201 | 0 |  | A
5.3 | OIL SUMP PIT(RCC) :Oil collection (from Reactor)sump pit with provision of pump(5 HP, with auto level control , including cabling, fixing of control gear )as per CIGRE. As per spec and approved drawing. The pump shall be housed suitably on top of the Oil sump pit in a RCC roof with brick walls as per the instruction of Engineer-In-Charge. RCC type oil sump pit & The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used . >Oil capacity of each Transformer in ltrs appox. a) 63 MVAR/80 MVAR, 400 KV Reactor: 50000 ltrs | Nos | 1 | 1 | 0 | 1 | 0 | 1787532.8333 |  | 1787532.8333 | 321755.91 | 2109288.7433 | 1787532.8333 | 0 | 1787532.8333 | 321755.91 | 2109288.7433 | 0 |  | A
6 | PCC before site surfacing :Providing and supplying all labour, material, equipments etc. required for proper leveling of earth after erection of structures and equipments and proper compaction by using roller of adequate capacity(minimum 3 Ton capacity) with water sprinkling of switch yard area. After proper leveling of the switch yard area (after anti-weed treatment), spreading of plain cement concrete with mixing ratio 1:4:8 (M10) and maintaining proper sloping for easy discharge of storm water having concrete thickness of 75 mm. including rolling , dressing, compacting,the area. As per technical specification and approved drawing, and as per the instruction of the Engg-in-Charge. This also includes excavation in all types of soil or rocks,back-filling,and disposal of excess earth as per the direction of Engineer in charge and approved drawing. (Switch yard area) | Cum | 105 | 1350 | 1245 | 131.25 | 1218.75 | 5154.8602 | 5145.91 | 541260.3215 | 97426.8579 | 638687.1794 | 676575.4019 | 6271577.8125 | 6948153.2144 | 1250667.5786 | 8198820.793 | 7560133.6136 | RC 2023 rate Sl no. 3.3(i) lower than BoQ rate. Hence, RC rate considered. | B
7 | Metal Spreading: Providing supplying and laying two layers of machine crushed metals (gravel) fill, the first layer after compaction shall make minimum 50 mm thickness coarse/ layer of 20 mm nominal size consolidated/ compacted and (by using roller as specified in the specification).A final layer of 50 mm thickness of machine crushed 20 mm nominal size of metals(gravel) above the first layer of 50 mm thickness and as per the technical specification and instruction of Engineer in charge above the PCC(1:3:6). The total compacted thickness of the metals(20 mm Nominal) 100mm above the PCC. | Cum | 140 | 1800 | 1660 | 175 | 1625 | 1642.7903 | 1642.7903 | 229990.6355 | 41398.3144 | 271388.9499 | 287488.2943 | 2669534.1618 | 2957022.4562 | 532264.0421 | 3489286.4983 | 3217897.5484 | BoQ rate lower than RC rate | B
8 | LEVELLING OF S/S AREA:Providing, neatly dressing up and leveling of substation area including switch yard area to a required level as decided by the Engineer in Charge, the work includes removal, clearing of the entire area from vegetation, trees, bushes, uprooting of plants and disposal of surplus earth and unusable material from the site by means of any mechanical transport, if required as per direction of the Project In charge, with all labours, tools, tackles and plants complete as per approved drawing and specification. This also includes excavation in all type of soils or rocks, back filling and disposal of excess earth or rocks to make the area to a level for construction as per scope and as per approved drawing and specification. |  |  |  |  | 0 | [7 empty] | 0
8.1 | Contour survey of the entire sub-station area including Supply of all labour & T&P by contractor. | SQM | 1500 | 18000 | 16500 | 1875 | 16125 | 487.5952 | 4.57 | 731392.7709 | 131650.6988 | 863043.4696 | 914240.9636 | 73691.25 | 987932.2136 | 177827.7984 | 1165760.012 | 302716.5424 | RC 2023 rate Sl no. 1.1lower than BoQ rate. Hence, RC rate considered. | B
8.2 | Cutting of sub-station area of the as per the direction of Engineer in Charge. | Cum | 1000 | 1000 | 0 | 1000 | 0 | 362.9765 | 224.01 | 362976.534 | 65335.7761 | 428312.3101 | 362976.534 | 0 | 362976.534 | 65335.7761 | 428312.3101 | 0 |  | A
8.3 | Filling with borrowed earth beyond 100 mtrs lead as per the direction of Engineer in Charge. | Cum | 3000 | 4500 | 1500 | 3750 | 750 | 396.6038 | 396.6038 | 1189811.3636 | 214166.0454 | 1403977.409 | 1487264.2044 | 297452.8409 | 1784717.0453 | 321249.0682 | 2105966.1135 | 701988.7045 | BoQ rate lower than RC rate | B
9 | PROVISION OF PLANTATIONS: Provision of plantation of 100 nos fruit bearing plants and 100 nos decorative plants at different locations, a garden in front of the control room including supply of plants,soil treatment and its plantation including materials, labour and T&P. The plantation shall have drip water irrigation system. As per the instruction of Engineer in Charge and specification. | Lot | 1 | 1 | 0 | 1 | 0 | 283195.8743 |  | 283195.8743 | 50975.2574 | 334171.1317 | 283195.8743 | 0 | 283195.8743 | 50975.2574 | 334171.1317 | 0 |  | A
10 | STONE PITCHING & TOE WALL:Stone pitching including making of toe walls both at top and bottom, including surface drain both at top and bottom and partition wall in every 10 mtrs by using boulders and RR masonry walls respectively. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth and supply of materials and labour as per the direction of Engineer In charge and as per approved drawing and specification. | Cum | 500 | 500 | 0 | 500 | 0 | 5437.7248 |  | 2718862.3761 | 489395.2277 | 3208257.6038 | 2718862.3761 | 0 | 2718862.3761 | 489395.2277 | 3208257.6038 | 0 |  | A
11 | Switch yard fencing: Providing and fixing of G.I Goat mesh (2.5 mm dia) fencing( the posts and links shall be of HD Galvanized ) in switch yard and other areas of the substation with a total fence height complete as per specification and approved drawings, and as required under the safety regulation of local, State and Central Government bodies and as per instruction of the Engineer-in-Charge.(The PCC work for grouting the post shall be 1:2:4 and a continuous Brick Masonry work with ratio mortar (cement and sand)1:5 and cement pointing of the joints, for the fencing upto a height of 350 mm from the finished ground level) .This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. The earthing of the fencing as per specification. | MTRS | 200 | 200 | 0 | 200 | 0 | 5664.2142 |  | 1132842.8394 | 203911.7111 | 1336754.5505 | 1132842.8394 | 0 | 1132842.8394 | 203911.7111 | 1336754.5505 | 0 |  | A
12 | Fire wall: Design, engineering, procurement of labour, material including all associated works for construction of fire-walls as per technical specification and approved drawings(column shall be RCC ratio1:1.5:3 and the walls are of fire resistant bricks).This also includes excavation in all types of soil or rocks,backfilling,and disposal of excess earth as per the direction of Enginer In charge. As per approved drawing and specification. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used .Painting of the walls as per direction of the Engineer in charge. | Nos | 1 | 0 | -1 | 0 | 0 | 1684449.4757 |  | 1684449.4757 | 303200.9056 | 1987650.3814 | 0 | 0 | 0 | 0 | 0 | -1987650.3814 |  | B
13 | Any other civil work to be included in the schedule by the Bidder if required essential for successful completion of project, including supply of labour, material, cement reinforcement steel, form work etc. Bidder shall also quote the unit rate for the following items of works.(Rate shall be inclusive of supply of labour, material, cement, reinforcement steel, form work etc. ) |  |  |  |  | 0 | [7 empty] | 0
13.1 | Excavation This also includes excavation in all types of soil or rocks, back filling,and disposal of excess earth as per the direction of Engineer In charge. | Cu.m. | 1 | 1 | 0 | 1 | 0 | 566.7181 |  | 566.7181 | 102.0093 | 668.7274 | 566.7181 | 0 | 566.7181 | 102.0093 | 668.7274 | 0 |  | A
13.2 | PCC: M10(1: 3 : 6) | Cu.m. | 1 | 1 | 0 | 1 | 0 | 5437.7248 |  | 5437.7248 | 978.7905 | 6416.5152 | 5437.7248 | 0 | 5437.7248 | 978.7905 | 6416.5152 | 0 |  | A
13.3 | RCC M 15(1:2:4) | Cu.m. | 1 | 1 | 0 | 1 | 0 | 6004.4429 |  | 6004.4429 | 1080.7997 | 7085.2426 | 6004.4429 | 0 | 6004.4429 | 1080.7997 | 7085.2426 | 0 |  | A
13.4 | RCC: M 20(1:1.5:3) without supply of reinforcement | Cu.m. | 1 | 1 | 0 | 1 | 0 | 8496.8158 |  | 8496.8158 | 1529.4268 | 10026.2427 | 8496.8158 | 0 | 8496.8158 | 1529.4268 | 10026.2427 | 0 |  | A
13.5 | Brick masonry work in cement sand mortar 1: 6 with bricks of class designation 75. | Cu.m. | 1 | 1 | 0 | 1 | 0 | 5664.2142 |  | 5664.2142 | 1019.5586 | 6683.7728 | 5664.2142 | 0 | 5664.2142 | 1019.5586 | 6683.7728 | 0 |  | A
13.6 | 12 mm thick plaster in cement sand mortar ( 1: 6 ). | Sq.m. | 1 | 1 | 0 | 1 | 0 | 170.1143 |  | 170.1143 | 30.6206 | 200.7349 | 170.1143 | 0 | 170.1143 | 30.6206 | 200.7349 | 0 |  | A
13.7 | Cutting,bending,binding(supply of binding wires) and fixing of reinforcement(including supply of reinforcement FE-500 as per BIS-1786 of TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786. | M.T. | 1 | 1 | 0 | 1 | 0 | 62303.3891 |  | 62303.3891 | 11214.61 | 73517.9991 | 62303.3891 | 0 | 62303.3891 | 11214.61 | 73517.9991 | 0 |  | A
14 | SWITCH YARD GATES:Design, engineering, procurement of labour, material including all associated works for construction and fixing.of following gate as per specification and approved drawing. This also includes excavation in all types of soil or rocks,back filling,and disposal of excess earth as per the direction of Engineer In charge. Provision of gate lights (Post top lantern type only switch yard) on each pillar of the gate. it includes supply & fixing of light fixtures including LED Gate lamp & switchgear etc required to complete works as per specification and approved drawings |  |  |  |  | 0 | [7 empty] | 0
14.1 | Gate | Nos | 2 | 2 | 0 | 2 | 0 | 339835.0492 |  | 679670.0983 | 122340.6177 | 802010.716 | 679670.0983 | 0 | 679670.0983 | 122340.6177 | 802010.716 | 0 |  | A
15 | COLOUR CODING, BAY MARKING Etc:Design, engineerimg, procurement of labour, material including all associated works for the followings.This should be as per direction of site In charge. a)Colur coding (red,Yellow & Blue) for equipments,Bus gantry &column of entire switch yard. Good quality weather proof (fluorescent type) stickering may be used for identification. b)Each bay should be identified with the help of bay marker sign board, suitably grouted. Stainless Steel sign board with stand to be installed.Proper painting and lettering to be done of the entire switch yard area. | Lot | 1 | 1 | 0 | 1 | 0 | 1132783.4972 |  | 1132783.4972 | 203901.0295 | 1336684.5267 | 1132783.4972 | 0 | 1132783.4972 | 203901.0295 | 1336684.5267 | 0 |  | A
16 | Switch yard buildings: Design, engineering and construction of Extension of existing switch yard control room buildings(refer the existing control room buildingdrawing uploaded) on the first floor including the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3).This also includes dismantling if any of the existing building to suitably accomodate the proposed extension work & disposal of debris as per the direction of Engineer In charge. The extension shall be made in such a manner that roof jointing with existing building & other jointing shall not make any damage to the existing part of the building. Care also to be taken for water proofing along the joints. As per approved drawings and tender specification.The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. Size of the extension of Building: 14 Mtrs x 11 Mtrs in Ground Foor and 23 Mtrs X 11 Mtrs approximately in First Floor. Existing Rest room will be merged with Control Room extension in First Floor. The size of rooms shall be decided during detailed Engg. |  |  |  |  | 0 | [7 empty] | 0
16.1 | RCC volume including MS rods FE-500 as per BIS-1786 (including column ,Beams and roofs etc) as per technical spec & approved drawings. | Lot | 1 | 0 | -1 | 0 | 0 | 8827782.1695 |  | 8827782.1695 | 1589000.7905 | 10416782.96 | 0 | 0 | 0 | 0 | 0 | -10416782.96 |  | B
16.2 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 6 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 1 | 0 | -1 | 0 | 0 | 1079543.6421 |  | 1079543.6421 | 194317.8556 | 1273861.4977 | 0 | 0 | 0 | 0 | 0 | -1273861.4977 |  | B
16.3 | Flooring with vitrified tiles with dado in all the rooms,Bath and toilets shall be provided with anti skid ceramic tiles(wall of the same also to be provided with ceramic tiles),Acid proof industrial tiles to be provided on the floor and wall of the battery room as per technical spec & approved drawings. | Lot | 1 | 0 | -1 | 0 | 0 | 817870.1993 |  | 817870.1993 | 147216.6359 | 965086.8351 | 0 | 0 | 0 | 0 | 0 | -965086.8351 |  | B
16.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) and Building internal & external & ceiling paintings as per technical spec mentioned in the civil section. The left over portion of walls and ceiling of Battery room shall be acid proof paints as per specification & approved drawings. | Lot | 1 | 0 | -1 | 0 | 0 | 374951.7925 |  | 374951.7925 | 67491.3227 | 442443.1152 | 0 | 0 | 0 | 0 | 0 | -442443.1152 |  | B
16.5 | Provision of ceiling as per specification mentioned in the civil section & approved drawings. | Lot | 1 | 0 | -1 | 0 | 0 | 882438.4828 |  | 882438.4828 | 158838.9269 | 1041277.4097 | 0 | 0 | 0 | 0 | 0 | -1041277.4097 |  | B
16.6 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC TYPE with double layer glaze of 6mm & windows shall have aluminium grills & jally etc. as per technical spec & approved drawing.Main door is to be provided with automatic close & open system with automatic sensor . | Lot | 1 | 0 | -1 | 0 | 0 | 1522461.0598 |  | 1522461.0598 | 274042.9908 | 1796504.0506 | 0 | 0 | 0 | 0 | 0 | -1796504.0506 |  | B
16.7 | Internal concealed wiring,fixing of lighting fixtures ,fans and regulators,exhaust fan including supply,D.C emergency lighting etc including supply of all materials & fixtures, as per approved drawing and direction of Engineer In charge. | Lot | 1 | 0 | -1 | 0 | 0 | 418892.7229 |  | 418892.7229 | 75400.6901 | 494293.413 | 0 | 0 | 0 | 0 | 0 | -494293.413 |  | B
16.8 | Provision of smoke and fire detection system of the building. | Lot | 1 | 0 | -1 | 0 | 0 | 207896.5407 |  | 207896.5407 | 37421.3773 | 245317.918 | 0 | 0 | 0 | 0 | 0 | -245317.918 |  | B
16.9 | Provision of PHD and other fittings(in Toilets,wash room,overhead water tank of adequate capacity etc) of reputed make,provision of rain water discharge pipes at different locations and etc as per requirement and approved drawing. There shall be septic tank and soak pit of required capacity including complete sewage system as per approved drawing & technical specification & as per instruction of Engg- in-Charge. It includes supply of all types of materials of reputed make, labour etc to complete the work. Toilets for Gents & Ladies to be provided including all good quality reputed fittings as per technoical specification. The toilets & wash room shall have antiskid floor tiles & wall tiles of seramic upto height of 8 feet.and all fittings & fixtures are of jaguar make | Lot | 1 | 0 | -1 | 0 | 0 | 1132783.4972 |  | 1132783.4972 | 203901.0295 | 1336684.5267 | 0 | 0 | 0 | 0 | 0 | -1336684.5267 |  | B
17 | RCC Security watch tower at the corner of the s/y. These watch tower shall be RCC type standard practice in this effect shall be followed.The height of the Tower shall be 6 mtrs. Size of the tower platform shall be 2.5 x2.5 X2.5 mtrs with RCC roof. The shed shall have stair case,door,windows,internal electrification,fan etc and having all protection as per standard practice and as per specification. The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used . | nos | 1 | 1 | 0 | 1 | 0 | 1755814.4207 |  | 1755814.4207 | 316046.5957 | 2071861.0164 | 1755814.4207 | 0 | 1755814.4207 | 316046.5957 | 2071861.0164 | 0 |  | A
NEW ITEMS | [5 empty] | 0 | [7 empty] | 0
18 | Switch yard panel room buildings: Design, engineering and construction of switch yard panel room buildings including the cost of material, supply of labour, cement, reinforcement- steel, form work and excavation as per the approved drawing and technical specification ( The RCC structure frame should be in the ratio 1:1.5:3). As per approved drawings and tender specification.The MS Rod (FE-500-TATA/ RINL/ Sail/JINDAL or any approved vendor of OPTCL) as per BIS-1786 to be used in the building. Size of the of Building: 10 Mtrs x 4.5 Mtrs .The size of rooms shall be decided during detailed Engg. |  |  |  |  | 0 | [7 empty] | 0 |  |  |  |  | Unit rate considered as 11% of item number 16 . Unit rate considered on prorata basis of area. Area of proposed panel room is around 45sqm
18.1 | RCC volume including MS rods FE-500 as per BIS-1786 (including column ,Beams and roofs etc) as per technical spec & approved drawings. | Lot | 0 | 1 | 1 | 0 | 1 |  | 971056.0386 | 0 | 0 | 0 | 0 | 971056.0386 | 971056.0386 | 174790.087 | 1145846.1256 | 1145846.1256 | Unit rate considered as 11% of item number 16.1 | B
18.2 | Fly ash Brick masonry by using fly ash Fly ash Brick work in cement sand mortar 1: 6 with Fly ash Bricks of class designation 75 as per technical spec & approved drawings. | Lot | 0 | 1 | 1 | 0 | 1 |  | 118749.8006 | 0 | 0 | 0 | 0 | 118749.8006 | 118749.8006 | 21374.9641 | 140124.7647 | 140124.7647 | Unit rate considered as 11% of item number 16.2 | B
18.3 | Flooring with vitrified tiles with dado in all the rooms,Bath and toilets shall be provided with anti skid ceramic tiles(wall of the same also to be provided with ceramic tiles),Acid proof industrial tiles to be provided on the floor and wall of the battery room as per technical spec & approved drawings. | Lot | 0 | 1 | 1 | 0 | 1 |  | 89965.7219 | 0 | 0 | 0 | 0 | 89965.7219 | 89965.7219 | 16193.8299 | 106159.5519 | 106159.5519 | Unit rate considered as 11% of item number 16.3 | B
18.4 | External and internal wall (External (18mm thk ) and internal (12 mm thk) wall and ceiling plastering as per technical spec mentioned in the civil section) and Building internal & external & ceiling paintings as per technical spec mentioned in the civil section. The left over portion of walls and ceiling of Battery room shall be acid proof paints as per specification & approved drawings. | Lot | 0 | 1 | 1 | 0 | 1 |  | 41244.6972 | 0 | 0 | 0 | 0 | 41244.6972 | 41244.6972 | 7424.0455 | 48668.7427 | 48668.7427 | Unit rate considered as 11% of item number 16.4 | B
18.5 | Provision of ceiling as per specification mentioned in the civil section & approved drawings. | Lot | 0 | 1 | 1 | 0 | 1 |  | 97068.2331 | 0 | 0 | 0 | 0 | 97068.2331 | 97068.2331 | 17472.282 | 114540.5151 | 114540.5151 | Unit rate considered as 11% of item number 16.5 | B
18.6 | Doors and windows shall be of sliding type with locking facility and shall be of UPVC TYPE with double layer glaze of 6mm & windows shall have aluminium grills & jally etc. as per technical spec & approved drawing.Main door is to be provided with automatic close & open system with automatic sensor . | Lot | 0 | 1 | 1 | 0 | 1 |  | 167470.7166 | 0 | 0 | 0 | 0 | 167470.7166 | 167470.7166 | 30144.729 | 197615.4456 | 197615.4456 | Unit rate considered as 11% of item number 16.6 | B
18.7 | Internal concealed wiring,fixing of lighting fixtures ,fans and regulators,exhaust fan including supply,D.C emergency lighting etc including supply of all materials & fixtures, as per approved drawing and direction of Engineer In charge. | Lot | 0 | 1 | 1 | 0 | 1 |  | 46078.1995 | 0 | 0 | 0 | 0 | 46078.1995 | 46078.1995 | 8294.0759 | 54372.2754 | 54372.2754 | Unit rate considered as 11% of item number 16.7 | B
18.8 | Provision of smoke and fire detection system of the building. | Lot | 0 | 1 | 1 | 0 | 1 |  | 22868.6195 | 0 | 0 | 0 | 0 | 22868.6195 | 22868.6195 | 4116.3515 | 26984.971 | 26984.971 | Unit rate considered as 11% of item number 16.8 | B
19 | Soil investigation : Supply of labour,T&Pand other necessary arrangements for Soil investigation/testing of the Switchyard,control Room, Quarters area etc.as per the site requirement,Technical specification & instruction of Engineer-in-Charge. | PER POINT | 0 | 3 | 7 | 0 | 3 |  | 30029.82 | 0 | 0 | 0 | 0 | 90089.46 | 90089.46 | 16216.1028 | 106305.5628 | 106305.5628 | Rate Contract Rate considered | B
[10 empty] | 315768140.2982 | 56838265.2537 | 372606405.5518 | 349322195.472 | 280648873.1174 | 629971068.5894 | 113394792.3461 | 743365860.9355 | 370759455.3837

## Price Ref of New Items
Supply
Sl. No. | DESCRIPTION OF ITEMS | UNIT | QUANTITY | Unit Ex-works Price | Total Ex-works Price | Remarks | Price Ref | Quoted Unit Price in BOQ with BHEL OH (15%) & Profit (10%) | Total Ex-Works Price of New Items | S&S Power BO dtd 8.05.23 | BPI (Avg. of Budgetary Offer) | Connector (Neemuch PO) |  | Calculation for BPIs (based on Budgetary Offers)
A1 | SUPPLY OF ADDITIONAL ITEMS FOR SUBSTATION | [6 empty] | 1.25 |  | Isolator | BPI | Connector | Total Isolator | ABI 24.02.23 | MIL 27.02.23 | IEC 24.02.23 | Average
57 | 420 KV, 3150 A, 63 KA, ISOLATORS
57.1 | WITH ONE EARTH SWITCH | Nos | 2 | 1281001.12 | 2562002.24 | HDB type, Without Springless contact , fault rate 63kA/3 Sec | Budgetary Offer | 1601251.4 | 3202502.8 | 811000 | 439500 | 30501.12 | 1250500 | 48500 | 52000 | 46000 | 48833.3333
58 | 245 KV, 2000 A, 50 KA, ISOLATORS
58.1 | WITH ONE EARTH SWITCH | Nos | 4 | 638464.28 | 2553857.12 | HDB type. Without Springless contact , fault rate 50kA/3 Sec | Budgetary Offer | 798080.35 | 3192321.4 | 398000 | 217920 | 22544.28 | 615920 | 23500 | 24640 | 24500 | 24213.3333
59 | 66kV XLPE CABLE & ACCESSORIES
59.1 | 66kV XLPE CABLE | Mtrs | 1500 | 5816 | 8724000 | PGCIL Spec, Lead Sheath, Cu Conductor, Fault 31.5KA/1 Sec | KEI BO dtd 14.07.2023 | 7270 | 10905000
59.2 | 66kV XLPE CABLE Termination Kit suitable for ICT tertiary | Nos | 6 | 63641 | 381846 |  | HPCL Visakh PO | 79551.25 | 477307.5
59.3 | 66kV XLPE CABLE Termination Kit suitable for ST | Nos | 6 | 63641 | 381846 |  | HPCL Visakh PO | 79551.25 | 477307.5
59.4 | 66kV CABLE Link Box (with SVL) with bonding cable | Nos | 2 | 162708 | 325416 |  | HPCL Visakh PO for SVL+ Bonding Cable estimated | 203385 | 406770
59.5 | 66kV CABLE Link Box (without SVL) with bonding cable | Nos | 2 | 157599 | 315198 |  | HPCL Visakh PO for SVL+ Bonding Cable estimated | 196998.75 | 393997.5
60 | 72.5kV, 31.5 kA for 1 sec Voltage Tranformer | Nos | 6 | 115525 | 693150 |  | PO Neemuch 30P2300189 dtd 24.01.23 | 144406.25 | 866437.5
61 | 72.5KV, 1250A, 31.5 KA for 1 sec, isolator (single isolator with earth switch) including post insulators as per technical specification | Nos | 2 | 247800 | 495600 |  | PGCIL Pugalur PO 22P2100719 dtd. 09.02.21 & 25000 Service charge considered from Neemuch PO ref 22P2300183 dtd 21.02.23 | 309750 | 619500
62 | 72.5KV, 1250 A, 31.5 KA 3 Sec, Circuit Breaker with supporting GI structures as per technical specification. | Nos | 2 | 541420.2 | 1082840.4 | Escalation of 10% due to higher fault rating of 31.5KA/3sec (neemuch - 25kA/1 Sec) | PO Neemuch 06P2300177 dtd 21.01.23 with | 676775.25 | 1353550.5
63 | 72.5KV, 31.5 KA for 1 sec,1200-600/1-1-1-1 A, Current Transformer as per technical specification | Nos | 6 | 120180 | 721080 |  | PO Neemuch 12P2300159 dtd 30.12.22 | 150225 | 901350
64 | 72.5KV, 31.5 KA for 1 sec, 50-25/1-1 A, Current Transformer as per technical specification | Nos | 6 | 120180 | 721080 |  | PO Neemuch 12P2300159 dtd 30.12.22 | 150225 | 901350
65 | 72.5KV Bus Post Insulator as per technical specification | Nos | 12 | 4500 | 54000 |  | BO ABI dtd 24.02.23 | 5625 | 67500
66 | 160 KN LR Antifog Porcelain INSULATOR STRINGS (TENSION) 400 KV | SET | 18 | 78500 | 1413000 |  | BO of MIL dated 06.06.2023 | 98125 | 1766250
67 | Controlled Switching Device (CSD) for 400kV Line Bays in GIS | Nos. | 2 | 623000 | 1246000 |  | Neemuch PO | 778750 | 1557500
68 | 7/9 SWG Earth Wire | Mtrs | 500 | 102 | 51000 |  | Udangudi PO | 127.5 | 63750
[5 empty] | 21721915.76 |  |  |  | 27152394.7
ETC
Sl. No. | DESCRIPTION OF ITEMS | UNIT | QUANTITY | Unit ETC Price | Total ETC Price | Price Ref
A1 | SUPPLY OF ADDITIONAL ITEMS FOR SUBSTATION | [6 empty] | Quoted Unit Price in BOQ with BHEL OH (15%) & Profit (10%) | Total Price for ETC of New Items
51 | 420 KV, 3150 A, 63 KA, ISOLATORS
51.1 | WITH ONE EARTH SWITCH | Nos | 2 | Contract Price |  |  |  | 0 | 0
52 | 245 KV, 2000 A, 50 KA, ISOLATORS
52.1 | WITH ONE EARTH SWITCH | Nos | 4 | 20208.96 | 80835.84 | Vellavidhuthi ETC dtd 14.08.2019 | Item ref 26 | 25261.2 | 101044.8
53 | 66kV XLPE CABLE & ACCESSORIES
53.1 | 66kV XLPE CABLE | Mtrs | 1500 | 573.58 | 860370 | HPCL Visag CABLE ETC dtd 27.12.2021 | Item Sl no. 2 | 716.975 | 1075462.5
53.2 | 66kV XLPE CABLE Termination Kit suitable for ICT tertiary | Nos | 6 | 8604.89 | 51629.34 | HPCL Visag CABLE ETC dtd 27.12.2021 | Item Sl no. 4 | 10756.1125 | 64536.675
53.3 | 66kV XLPE CABLE Termination Kit suitable for ST | Nos | 6 | 8604.89 | 51629.34 | HPCL Visag CABLE ETC dtd 27.12.2021 | Item Sl no. 4 | 10756.1125 | 64536.675
53.4 | 66kV CABLE Link Box (with SVL) with bonding cable | Nos | 2 | 5019.42 | 10038.84 | HPCL Visag CABLE ETC dtd 27.12.2021 | Item Sl no. 8 | 6274.275 | 12548.55
53.5 | 66kV CABLE Link Box (without SVL) with bonding cable | Nos | 2 | 5019.42 | 10038.84 | HPCL Visag CABLE ETC dtd 27.12.2021 | Item Sl no. 8 | 6274.275 | 12548.55
54 | 36 kV, 31.5 kA for 1 sec Voltage Tranformer (with higher BIL) | Nos | 6 | 2000 | 12000 | Self Estimation |  | 2500 | 15000
55 | 160 KN LR Antifog Porcelain INSULATOR STRINGS (TENSION) 400 KV | SET | 18 | 5000 | 90000 | Self Estimation |  | 6250 | 112500
56 | Controlled Switching Device (CSD) for 400kV Line Bays in GIS | Nos. | 2 | 5000 | 10000 | Self Estimation |  | 6250 | 12500
57 | 7/9 SWG Earth Wire | Mtrs | 500 | 45.36 | 22680 | Vellavidhuthi ETC dtd 14.08.2019 | Item Sl no. 62 | 56.7 | 28350
1499027.75
Sr. Manager/BHEL
|  |  | Ersama | New Duburi | Total
| Civil New Items |  | 0 | 1644591.4871 | 1644591.4871

## Simplified Summary
Summary for the a. Items for which Qty has been changed from Original BOQ/Contract Qty
|  |  | Original Order Value |  |  | Total Order Value after Amendment
New Amendment Price Schedule | Sl. No. | Item Description | Ex-Works Price with freight in INR | Total GST in INR (18%) | Total in INR | Total Revised Price | Total GST in INR (18%) | Total in INR | Diffential Value inclusive of GST (between original BOQ and Amended BOQ) | 2565134.01
| 1 | Supply Schedules | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 1784732.91
| 2 | Erection | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 12867900
| 3 | CIVIL | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 563222.85
|  | Total |  |  | #REF! |  |  | #REF! | #REF! | 563222.85
479988.6
464917.05
Summary for the b. Inclusion of New Items (Not presently covered in Original Contract) as per attached sheet "Price Ref of New Items" | [9 empty] | 1022396
|  |  | Original Order Value |  |  | Total Order Value after Amendment |  |  |  | 731010
New Amendment Price Schedule | Sl. No. | Item Description | Ex-Works Price with freight in INR | Total GST in INR (18%) | Total in INR | Total Revised Price | Total GST in INR (18%) | Total in INR | Diffential Value inclusive of GST (between original BOQ and Amended BOQ) | 1597190
| 1 | Supply Schedules |  | 0 | 0 | 27152394.7 | 4887431.046 | 32039825.746 | 32039825.746 | 1063593
| 2 | Erection |  | 0 | 0 | 1499027.75 | 269824.995 | 1768852.745 | 1768852.745 | 1063593
| 3 | CIVIL |  | 0 | 0 | 1644591.4871 | 296026.4677 | 1940617.9547 | 1940617.9547 | 79650
|  | Total |  |  | 0 | 30296013.9371 | 5453282.5087 | 35749296.4457 | 35749296.4457 | 1837850
26684400.27
Grand Summary of Above (a + b)
|  |  | Original Order Value |  |  | Total Order Value after Amendment
New Amendment Price Schedule | Sl. No. | Item Description | Ex-Works Price with freight in INR | Total GST in INR (18%) | Total in INR | Total Revised Price | Total GST in INR (18%) | Total in INR | Diffential Value inclusive of GST (between original BOQ and Amended BOQ)
| 1 | Supply Schedules | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2 | Erection | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 3 | CIVIL | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
|  | Total |  |  | #REF! |  |  | #REF! | #REF!